## Properties
Refrigerant |  | R32
Data source |  | tlk-energy.de pressure-enthalpy
Compressor Efficiency |  | 80%
Superheating | K | 6
Subcooling | K | 5
T0 | K | 273
Tcond, h | ºC | 30 | 303
h1 | kJ/kg | 525.4
h2,act | kJ/kg | 552.2
h3 | kJ/kg | 245.5
h4 | kJ/kg | 245.5
s1 | J/kg.K | 2146
s2,act | J/kg.K | 2162.9
s3 | J/kg.K | 1155.4
s4 | J/kg.K | 1160.8

## Winter
Winter
| Hot Sink |  |  | Cold Sink
| Condenser Duty | Refrig mass flow rate | Exdest.cond | Condenser Duty | Refrig mass flow rate | Exdest.cond | Exdest.cond
| Qcond,h | ṁ ref | Condenser | Qcond,c | ṁ ref | Condenser | Total
Total | 2286226.9586 |  | 9587.4188 | 339293.6997 |  | 1422.8468 | 11010.2657
Hours | kW | kg/s | kW | kW | kg/s | kW
1 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
2 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
3 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
4 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
5 | 3044.25 | 9.9258 | 12.7662 | 0 | 0 | 0
6 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
7 | 3489.75 | 11.3784 | 14.6345 | 0 | 0 | 0
8 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
9 | 3732.6611 | 12.1704 | 15.6531 | 202.5889 | 0.66054 | 0.84957
10 | 3726.13 | 12.1491 | 15.6257 | 431.87 | 1.4081 | 1.8111
11 | 3719.6339 | 12.1279 | 15.5985 | 661.1161 | 2.1556 | 2.7724
12 | 3713.1725 | 12.1069 | 15.5714 | 890.3275 | 2.9029 | 3.7336
13 | 3706.7458 | 12.0859 | 15.5444 | 1119.5042 | 3.6502 | 4.6947
14 | 3700.3537 | 12.0651 | 15.5176 | 1348.6463 | 4.3973 | 5.6556
15 | 3693.9961 | 12.0443 | 15.491 | 1206.5039 | 3.9338 | 5.0595
16 | 3693.5554 | 12.0429 | 15.4891 | 1404.9446 | 4.5808 | 5.8917
17 | 3701.1356 | 12.0676 | 15.5209 | 2090.3644 | 6.8157 | 8.7661
18 | 3708.6838 | 12.0922 | 15.5526 | 1934.3162 | 6.3069 | 8.1117
19 | 3716.1999 | 12.1167 | 15.5841 | 2223.8001 | 7.2507 | 9.3256
20 | 3723.6835 | 12.1411 | 15.6155 | 1919.3165 | 6.258 | 8.0488
21 | 3731.135 | 12.1654 | 15.6467 | 2357.365 | 7.6862 | 9.8857
22 | 3738.5542 | 12.1896 | 15.6778 | 1607.4458 | 5.2411 | 6.7409
23 | 3737.9181 | 12.1875 | 15.6752 | 865.5819 | 2.8222 | 3.6299
24 | 3731.4337 | 12.1664 | 15.648 | 129.5663 | 0.42245 | 0.54334
25 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
26 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
27 | 2554.2 | 8.328 | 10.7112 | 0 | 0 | 0
28 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
29 | 2948.7857 | 9.6146 | 12.3659 | 0 | 0 | 0
30 | 3139.7143 | 10.2371 | 13.1666 | 0 | 0 | 0
31 | 3330.6429 | 10.8596 | 13.9672 | 0 | 0 | 0
32 | 3521.5714 | 11.4821 | 14.7679 | 0 | 0 | 0
33 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
34 | 3708.2572 | 12.0908 | 15.5508 | 195.1714 | 0.63636 | 0.81846
35 | 3701.9642 | 12.0703 | 15.5244 | 392.3929 | 1.2794 | 1.6455
36 | 3695.7053 | 12.0499 | 15.4981 | 589.5804 | 1.9223 | 2.4724
37 | 3689.4802 | 12.0296 | 15.472 | 786.7341 | 2.5652 | 3.2992
38 | 3682.936 | 12.0083 | 15.4446 | 984.2068 | 3.209 | 4.1273
39 | 3675.8975 | 11.9853 | 15.4151 | 1182.1739 | 3.8545 | 4.9575
40 | 3674.7605 | 11.9816 | 15.4103 | 1374.2395 | 4.4807 | 5.7629
41 | 3681.6431 | 12.0041 | 15.4392 | 1218.8569 | 3.9741 | 5.1113
42 | 3688.4966 | 12.0264 | 15.4679 | 1509.0034 | 4.9201 | 6.3281
43 | 3695.3205 | 12.0486 | 15.4965 | 1799.1795 | 5.8663 | 7.545
44 | 3702.114 | 12.0708 | 15.525 | 1940.886 | 6.3283 | 8.1392
45 | 3708.8766 | 12.0928 | 15.5534 | 2379.6234 | 7.7588 | 9.9791
46 | 3715.6078 | 12.1148 | 15.5816 | 1630.3922 | 5.3159 | 6.8371
47 | 3714.2866 | 12.1105 | 15.5761 | 889.2134 | 2.8993 | 3.729
48 | 3707.1295 | 12.0872 | 15.5461 | 153.8705 | 0.5017 | 0.64526
49 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
50 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
51 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
52 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
53 | 2992.8462 | 9.7582 | 12.5507 | 0 | 0 | 0
54 | 3198.4615 | 10.4286 | 13.4129 | 0 | 0 | 0
55 | 3404.0769 | 11.099 | 14.2752 | 0 | 0 | 0
56 | 3609.6923 | 11.7695 | 15.1374 | 0 | 0 | 0
57 | 3683.1396 | 12.0089 | 15.4454 | 132.1681 | 0.43094 | 0.55425
58 | 3676.1537 | 11.9862 | 15.4162 | 344.7693 | 1.1241 | 1.4458
59 | 3669.2028 | 11.9635 | 15.387 | 557.3357 | 1.8172 | 2.3372
60 | 3662.2867 | 11.9409 | 15.358 | 769.8672 | 2.5102 | 3.2285
61 | 3655.4053 | 11.9185 | 15.3291 | 982.3639 | 3.203 | 4.1196
62 | 3648.5585 | 11.8962 | 15.3004 | 1194.8261 | 3.8957 | 5.0106
63 | 3641.7462 | 11.874 | 15.2719 | 1407.2538 | 4.5884 | 5.9014
64 | 3640.8211 | 11.871 | 15.268 | 1259.6789 | 4.1072 | 5.2825
65 | 3647.9123 | 11.8941 | 15.2977 | 1519.8877 | 4.9556 | 6.3737
66 | 3654.9732 | 11.9171 | 15.3273 | 1780.1268 | 5.8041 | 7.4651
67 | 3662.0028 | 11.94 | 15.3568 | 2277.9972 | 7.4274 | 9.5529
68 | 3669.0002 | 11.9628 | 15.3862 | 2270.9998 | 7.4046 | 9.5236
69 | 3675.9651 | 11.9855 | 15.4154 | 2561.0349 | 8.3503 | 10.7398
70 | 3682.8976 | 12.0081 | 15.4444 | 1781.9024 | 5.8099 | 7.4725
71 | 3681.7798 | 12.0045 | 15.4397 | 1010.8202 | 3.2958 | 4.2389
72 | 3674.8423 | 11.9819 | 15.4107 | 245.5577 | 0.80064 | 1.0298
73 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
74 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
75 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
76 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
77 | 2970 | 9.6837 | 12.4549 | 0 | 0 | 0
78 | 3168 | 10.3293 | 13.2852 | 0 | 0 | 0
79 | 3366 | 10.9749 | 14.1155 | 0 | 0 | 0
80 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
81 | 3660.4576 | 11.935 | 15.3503 | 101.5424 | 0.33108 | 0.42582
82 | 3667.5166 | 11.958 | 15.3799 | 292.4834 | 0.95365 | 1.2265
83 | 3674.5505 | 11.9809 | 15.4094 | 483.4495 | 1.5763 | 2.0274
84 | 3681.5587 | 12.0038 | 15.4388 | 674.4413 | 2.199 | 2.8283
85 | 3688.8938 | 12.0277 | 15.4696 | 865.1062 | 2.8207 | 3.6279
86 | 3696.7305 | 12.0532 | 15.5024 | 1055.2695 | 3.4407 | 4.4253
87 | 3704.5388 | 12.0787 | 15.5352 | 898.9612 | 2.9311 | 3.7698
88 | 3712.3191 | 12.1041 | 15.5678 | 1237.6809 | 4.0355 | 5.1903
89 | 3720.0706 | 12.1293 | 15.6003 | 1576.4294 | 5.14 | 6.6108
90 | 3727.7926 | 12.1545 | 15.6327 | 1915.2074 | 6.2446 | 8.0315
91 | 3735.4846 | 12.1796 | 15.665 | 1499.1404 | 4.888 | 6.2867
92 | 3743.1476 | 12.2046 | 15.6971 | 1083.1024 | 3.5315 | 4.542
93 | 3750.7831 | 12.2295 | 15.7291 | 667.0919 | 2.1751 | 2.7975
94 | 3758.3924 | 12.2543 | 15.761 | 251.1076 | 0.81874 | 1.053
95 | 3601.125 | 11.7415 | 15.1015 | 0 | 0 | 0
96 | 2970 | 9.6837 | 12.4549 | 0 | 0 | 0
97 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
98 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
99 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
100 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
101 | 2943 | 9.5957 | 12.3416 | 0 | 0 | 0
102 | 3132 | 10.2119 | 13.1342 | 0 | 0 | 0
103 | 3321 | 10.8282 | 13.9268 | 0 | 0 | 0
104 | 3510 | 11.4444 | 14.7194 | 0 | 0 | 0
105 | 3699 | 12.0606 | 15.512 | 0 | 0 | 0
106 | 3754.8469 | 12.2427 | 15.7462 | 133.1531 | 0.43415 | 0.55838
107 | 3762.5496 | 12.2678 | 15.7785 | 314.4504 | 1.0253 | 1.3187
108 | 3770.226 | 12.2929 | 15.8107 | 495.774 | 1.6165 | 2.0791
109 | 3777.8758 | 12.3178 | 15.8427 | 677.1242 | 2.2078 | 2.8396
110 | 3785.4984 | 12.3427 | 15.8747 | 584.6445 | 1.9062 | 2.4517
111 | 3793.094 | 12.3674 | 15.9065 | 492.1917 | 1.6048 | 2.064
112 | 3800.3983 | 12.3913 | 15.9372 | 400.0302 | 1.3043 | 1.6775
113 | 3805.2969 | 12.4072 | 15.9577 | 310.2745 | 1.0117 | 1.3012
114 | 3810.1744 | 12.4231 | 15.9782 | 220.5398 | 0.71907 | 0.92485
115 | 3815.0311 | 12.439 | 15.9985 | 130.826 | 0.42656 | 0.54863
116 | 3819.8673 | 12.4547 | 16.0188 | 41.1327 | 0.13411 | 0.17249
117 | 3824.6831 | 12.4704 | 16.039 | 333.3169 | 1.0868 | 1.3978
118 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
119 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
120 | 2821.5 | 9.1995 | 11.8321 | 0 | 0 | 0
121 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
122 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
123 | 2545.7143 | 8.3003 | 10.6756 | 0 | 0 | 0
124 | 2715.4286 | 8.8537 | 11.3873 | 0 | 0 | 0
125 | 2885.1429 | 9.4071 | 12.099 | 0 | 0 | 0
126 | 3054.8571 | 9.9604 | 12.8107 | 0 | 0 | 0
127 | 3224.5714 | 10.5138 | 13.5224 | 0 | 0 | 0
128 | 3394.2857 | 11.0671 | 14.2341 | 0 | 0 | 0
129 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
130 | 3733.7143 | 12.1738 | 15.6575 | 0 | 0 | 0
131 | 3764.8271 | 12.2753 | 15.788 | 138.6014 | 0.45191 | 0.58123
132 | 3755.2519 | 12.2441 | 15.7479 | 317.8909 | 1.0365 | 1.3331
133 | 3745.4524 | 12.2121 | 15.7068 | 412.5476 | 1.3451 | 1.73
134 | 3735.6931 | 12.1803 | 15.6658 | 422.3069 | 1.3769 | 1.771
135 | 3725.974 | 12.1486 | 15.6251 | 856.3117 | 2.792 | 3.591
136 | 3725.0993 | 12.1457 | 15.6214 | 1026.9007 | 3.3482 | 4.3064
137 | 3732.9701 | 12.1714 | 15.6544 | 781.4299 | 2.5479 | 3.277
138 | 3740.811 | 12.197 | 15.6873 | 535.989 | 1.7476 | 2.2477
139 | 3748.6226 | 12.2224 | 15.7201 | 409.3774 | 1.3348 | 1.7167
140 | 3756.4056 | 12.2478 | 15.7527 | 45.1944 | 0.14736 | 0.18953
141 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
142 | 3326.4 | 10.8458 | 13.9494 | 0 | 0 | 0
143 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
144 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
145 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
146 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
147 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
148 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
149 | 2821.5 | 9.1995 | 11.8321 | 0 | 0 | 0
150 | 2970 | 9.6837 | 12.4549 | 0 | 0 | 0
151 | 3118.5 | 10.1679 | 13.0776 | 0 | 0 | 0
152 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
153 | 3415.5 | 11.1363 | 14.3231 | 0 | 0 | 0
154 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
155 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
156 | 3742.1908 | 12.2015 | 15.6931 | 118.8092 | 0.38738 | 0.49823
157 | 3736.0623 | 12.1815 | 15.6674 | 273.4377 | 0.89155 | 1.1467
158 | 3729.9669 | 12.1616 | 15.6418 | 428.0331 | 1.3956 | 1.795
159 | 3723.9043 | 12.1418 | 15.6164 | 285.5957 | 0.93119 | 1.1977
160 | 3723.8709 | 12.1417 | 15.6163 | 434.1291 | 1.4155 | 1.8205
161 | 3731.8788 | 12.1678 | 15.6498 | 1020.1212 | 3.3261 | 4.2779
162 | 3739.8544 | 12.1939 | 15.6833 | 863.6456 | 2.8159 | 3.6217
163 | 3747.7975 | 12.2198 | 15.7166 | 1152.7025 | 3.7584 | 4.8339
164 | 3755.7079 | 12.2455 | 15.7498 | 818.0921 | 2.6674 | 3.4307
165 | 3763.0571 | 12.2695 | 15.7806 | 484.0429 | 1.5782 | 2.0299
166 | 3768.2611 | 12.2865 | 15.8024 | 152.1389 | 0.49605 | 0.638
167 | 3593.7 | 11.7173 | 15.0704 | 0 | 0 | 0
168 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
169 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
170 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
171 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
172 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
173 | 3044.25 | 9.9258 | 12.7662 | 0 | 0 | 0
174 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
175 | 3489.75 | 11.3784 | 14.6345 | 0 | 0 | 0
176 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
177 | 3726.0637 | 12.1489 | 15.6255 | 209.1863 | 0.68206 | 0.87723
178 | 3719.161 | 12.1264 | 15.5965 | 438.839 | 1.4308 | 1.8403
179 | 3712.2927 | 12.104 | 15.5677 | 668.4573 | 2.1795 | 2.8032
180 | 3705.4586 | 12.0817 | 15.539 | 898.0414 | 2.9281 | 3.766
181 | 3698.6585 | 12.0595 | 15.5105 | 1127.5915 | 3.6765 | 4.7286
182 | 3691.8924 | 12.0375 | 15.4822 | 1357.1076 | 4.4249 | 5.6911
183 | 3685.1601 | 12.0155 | 15.4539 | 1215.3399 | 3.9626 | 5.0966
184 | 3684.425 | 12.0131 | 15.4508 | 1414.075 | 4.6106 | 5.93
185 | 3691.7222 | 12.0369 | 15.4814 | 2099.7778 | 6.8464 | 8.8055
186 | 3698.9837 | 12.0606 | 15.5119 | 1944.0163 | 6.3385 | 8.1523
187 | 3706.2094 | 12.0842 | 15.5422 | 2233.7906 | 7.2833 | 9.3675
188 | 3713.399 | 12.1076 | 15.5723 | 1929.601 | 6.2915 | 8.0919
189 | 3720.5528 | 12.1309 | 15.6023 | 2367.9472 | 7.7207 | 9.9301
190 | 3728.1115 | 12.1556 | 15.634 | 1617.8885 | 5.2751 | 6.7847
191 | 3728.0397 | 12.1553 | 15.6337 | 875.4603 | 2.8545 | 3.6713
192 | 3722.0514 | 12.1358 | 15.6086 | 138.9486 | 0.45304 | 0.58269
193 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
194 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
195 | 2554.2 | 8.328 | 10.7112 | 0 | 0 | 0
196 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
197 | 2948.7857 | 9.6146 | 12.3659 | 0 | 0 | 0
198 | 3139.7143 | 10.2371 | 13.1666 | 0 | 0 | 0
199 | 3330.6429 | 10.8596 | 13.9672 | 0 | 0 | 0
200 | 3521.5714 | 11.4821 | 14.7679 | 0 | 0 | 0
201 | 3709.5604 | 12.0951 | 15.5562 | 2.9396 | 0.0095847 | 0.012327
202 | 3703.7076 | 12.076 | 15.5317 | 199.721 | 0.65119 | 0.83754
203 | 3697.8868 | 12.057 | 15.5073 | 396.4703 | 1.2927 | 1.6626
204 | 3692.0979 | 12.0381 | 15.483 | 593.1878 | 1.9341 | 2.4876
205 | 3686.3407 | 12.0194 | 15.4589 | 789.8736 | 2.5754 | 3.3124
206 | 3679.7336 | 11.9978 | 15.4312 | 987.4093 | 3.2195 | 4.1408
207 | 3673.1597 | 11.9764 | 15.4036 | 1184.9118 | 3.8634 | 4.969
208 | 3672.504 | 11.9743 | 15.4008 | 1376.496 | 4.4881 | 5.7724
209 | 3679.8662 | 11.9983 | 15.4317 | 1220.6338 | 3.9799 | 5.1188
210 | 3687.1939 | 12.0222 | 15.4625 | 1510.3061 | 4.9244 | 6.3336
211 | 3694.4867 | 12.0459 | 15.493 | 1800.0133 | 5.869 | 7.5485
212 | 3701.7441 | 12.0696 | 15.5235 | 1941.2559 | 6.3295 | 8.1408
213 | 3708.9655 | 12.0931 | 15.5538 | 2379.5345 | 7.7585 | 9.9787
214 | 3716.1508 | 12.1166 | 15.5839 | 1629.8492 | 5.3141 | 6.8349
215 | 3715.2787 | 12.1137 | 15.5802 | 888.2213 | 2.8961 | 3.7248
216 | 3708.5671 | 12.0918 | 15.5521 | 152.4329 | 0.49701 | 0.63924
217 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
218 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
219 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
220 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
221 | 2992.8462 | 9.7582 | 12.5507 | 0 | 0 | 0
222 | 3198.4615 | 10.4286 | 13.4129 | 0 | 0 | 0
223 | 3404.0769 | 11.099 | 14.2752 | 0 | 0 | 0
224 | 3609.6923 | 11.7695 | 15.1374 | 0 | 0 | 0
225 | 3688.507 | 12.0264 | 15.468 | 126.8007 | 0.41344 | 0.53175
226 | 3681.9463 | 12.005 | 15.4404 | 338.9768 | 1.1052 | 1.4215
227 | 3675.4185 | 11.9838 | 15.4131 | 551.1199 | 1.7969 | 2.3112
228 | 3668.9236 | 11.9626 | 15.3858 | 763.2302 | 2.4885 | 3.2006
229 | 3662.4615 | 11.9415 | 15.3587 | 975.3077 | 3.18 | 4.09
230 | 3656.032 | 11.9205 | 15.3318 | 1187.3526 | 3.8714 | 4.9792
231 | 3649.635 | 11.8997 | 15.3049 | 1399.365 | 4.5627 | 5.8683
232 | 3649.8039 | 11.9002 | 15.3057 | 1250.6961 | 4.0779 | 5.2449
233 | 3658.1569 | 11.9275 | 15.3407 | 1509.6431 | 4.9222 | 6.3308
234 | 3666.4753 | 11.9546 | 15.3756 | 1768.6247 | 5.7666 | 7.4168
235 | 3674.7582 | 11.9816 | 15.4103 | 2265.2418 | 7.3859 | 9.4994
236 | 3683.0049 | 12.0085 | 15.4449 | 2256.9951 | 7.359 | 9.4648
237 | 3691.2151 | 12.0353 | 15.4793 | 2545.7849 | 8.3006 | 10.6759
238 | 3699.3889 | 12.0619 | 15.5136 | 1765.4111 | 5.7561 | 7.4033
239 | 3699.5133 | 12.0623 | 15.5141 | 993.0867 | 3.238 | 4.1646
240 | 3693.8434 | 12.0438 | 15.4903 | 226.5566 | 0.73869 | 0.95008
241 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
242 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
243 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
244 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
245 | 2970 | 9.6837 | 12.4549 | 0 | 0 | 0
246 | 3168 | 10.3293 | 13.2852 | 0 | 0 | 0
247 | 3366 | 10.9749 | 14.1155 | 0 | 0 | 0
248 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
249 | 3691.0515 | 12.0347 | 15.4786 | 70.9485 | 0.23133 | 0.29753
250 | 3699.3004 | 12.0616 | 15.5132 | 260.6996 | 0.85001 | 1.0933
251 | 3707.5203 | 12.0884 | 15.5477 | 450.4797 | 1.4688 | 1.8891
252 | 3715.7108 | 12.1151 | 15.582 | 640.2892 | 2.0877 | 2.6851
253 | 3723.8716 | 12.1417 | 15.6163 | 830.1284 | 2.7066 | 3.4812
254 | 3732.0022 | 12.1682 | 15.6504 | 1019.9978 | 3.3257 | 4.2774
255 | 3740.1024 | 12.1947 | 15.6843 | 863.3976 | 2.8151 | 3.6207
256 | 3748.1725 | 12.221 | 15.7182 | 1201.8275 | 3.9186 | 5.0399
257 | 3756.2119 | 12.2472 | 15.7519 | 1540.2881 | 5.0221 | 6.4593
258 | 3763.6903 | 12.2716 | 15.7832 | 1879.3097 | 6.1275 | 7.881
259 | 3769.0225 | 12.289 | 15.8056 | 1465.6025 | 4.7786 | 6.1461
260 | 3774.3288 | 12.3063 | 15.8279 | 1051.9212 | 3.4298 | 4.4113
261 | 3779.6105 | 12.3235 | 15.85 | 638.2645 | 2.0811 | 2.6766
262 | 3784.8691 | 12.3406 | 15.8721 | 224.6309 | 0.73241 | 0.942
263 | 3601.125 | 11.7415 | 15.1015 | 0 | 0 | 0
264 | 2970 | 9.6837 | 12.4549 | 0 | 0 | 0
265 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
266 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
267 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
268 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
269 | 2943 | 9.5957 | 12.3416 | 0 | 0 | 0
270 | 3132 | 10.2119 | 13.1342 | 0 | 0 | 0
271 | 3321 | 10.8282 | 13.9268 | 0 | 0 | 0
272 | 3510 | 11.4444 | 14.7194 | 0 | 0 | 0
273 | 3699 | 12.0606 | 15.512 | 0 | 0 | 0
274 | 3754.0298 | 12.2401 | 15.7427 | 133.9702 | 0.43681 | 0.56181
275 | 3759.4294 | 12.2577 | 15.7654 | 317.5706 | 1.0354 | 1.3317
276 | 3764.8074 | 12.2752 | 15.7879 | 501.1926 | 1.6341 | 2.1018
277 | 3770.1632 | 12.2927 | 15.8104 | 684.8368 | 2.2329 | 2.8719
278 | 3775.4964 | 12.3101 | 15.8328 | 594.6464 | 1.9389 | 2.4937
279 | 3780.8072 | 12.3274 | 15.855 | 504.4785 | 1.6449 | 2.1156
280 | 3786.0958 | 12.3446 | 15.8772 | 414.3328 | 1.3509 | 1.7375
281 | 3791.3625 | 12.3618 | 15.8993 | 324.2089 | 1.0571 | 1.3596
282 | 3796.6077 | 12.3789 | 15.9213 | 234.1066 | 0.76331 | 0.98174
283 | 3801.8316 | 12.3959 | 15.9432 | 144.0256 | 0.4696 | 0.60398
284 | 3807.0344 | 12.4129 | 15.965 | 53.9656 | 0.17596 | 0.22631
285 | 3812.2163 | 12.4298 | 15.9867 | 345.7837 | 1.1274 | 1.4501
286 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
287 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
288 | 2821.5 | 9.1995 | 11.8321 | 0 | 0 | 0
289 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
290 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
291 | 2545.7143 | 8.3003 | 10.6756 | 0 | 0 | 0
292 | 2715.4286 | 8.8537 | 11.3873 | 0 | 0 | 0
293 | 2885.1429 | 9.4071 | 12.099 | 0 | 0 | 0
294 | 3054.8571 | 9.9604 | 12.8107 | 0 | 0 | 0
295 | 3224.5714 | 10.5138 | 13.5224 | 0 | 0 | 0
296 | 3394.2857 | 11.0671 | 14.2341 | 0 | 0 | 0
297 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
298 | 3733.7143 | 12.1738 | 15.6575 | 0 | 0 | 0
299 | 3756.8349 | 12.2492 | 15.7545 | 146.5937 | 0.47797 | 0.61475
300 | 3747.3692 | 12.2184 | 15.7148 | 325.7737 | 1.0622 | 1.3661
301 | 3737.9422 | 12.1876 | 15.6753 | 420.0578 | 1.3696 | 1.7615
302 | 3728.5538 | 12.157 | 15.6359 | 429.4462 | 1.4002 | 1.8009
303 | 3720.7913 | 12.1317 | 15.6033 | 861.4944 | 2.8089 | 3.6127
304 | 3720.0967 | 12.1294 | 15.6004 | 1031.9033 | 3.3645 | 4.3273
305 | 3727.4413 | 12.1534 | 15.6312 | 786.9587 | 2.5659 | 3.3002
306 | 3734.7572 | 12.1772 | 15.6619 | 542.0428 | 1.7673 | 2.2731
307 | 3742.045 | 12.201 | 15.6925 | 415.955 | 1.3562 | 1.7443
308 | 3749.3054 | 12.2247 | 15.7229 | 52.2946 | 0.17051 | 0.2193
309 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
310 | 3326.4 | 10.8458 | 13.9494 | 0 | 0 | 0
311 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
312 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
313 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
314 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
315 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
316 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
317 | 2821.5 | 9.1995 | 11.8321 | 0 | 0 | 0
318 | 2970 | 9.6837 | 12.4549 | 0 | 0 | 0
319 | 3118.5 | 10.1679 | 13.0776 | 0 | 0 | 0
320 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
321 | 3415.5 | 11.1363 | 14.3231 | 0 | 0 | 0
322 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
323 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
324 | 3712.857 | 12.1058 | 15.5701 | 148.143 | 0.48302 | 0.62125
325 | 3706.24 | 12.0843 | 15.5423 | 303.26 | 0.98878 | 1.2717
326 | 3699.656 | 12.0628 | 15.5147 | 458.344 | 1.4944 | 1.9221
327 | 3693.1051 | 12.0414 | 15.4872 | 316.3949 | 1.0316 | 1.3268
328 | 3692.5981 | 12.0398 | 15.4851 | 465.4019 | 1.5174 | 1.9517
329 | 3700.136 | 12.0643 | 15.5167 | 1051.864 | 3.4296 | 4.411
330 | 3707.6425 | 12.0888 | 15.5482 | 895.8575 | 2.921 | 3.7568
331 | 3715.1176 | 12.1132 | 15.5796 | 1185.3824 | 3.865 | 4.971
332 | 3722.5609 | 12.1375 | 15.6108 | 851.2391 | 2.7755 | 3.5697
333 | 3729.9732 | 12.1616 | 15.6418 | 517.1268 | 1.6861 | 2.1686
334 | 3737.3555 | 12.1857 | 15.6728 | 183.0445 | 0.59682 | 0.76761
335 | 3593.7 | 11.7173 | 15.0704 | 0 | 0 | 0
336 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
337 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
338 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
339 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
340 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
341 | 3044.25 | 9.9258 | 12.7662 | 0 | 0 | 0
342 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
343 | 3489.75 | 11.3784 | 14.6345 | 0 | 0 | 0
344 | 3712.2687 | 12.1039 | 15.5676 | 0.23128 | 0.0007541 | 0.00096989
345 | 3711.7157 | 12.1021 | 15.5653 | 223.5343 | 0.72884 | 0.9374
346 | 3705.1602 | 12.0807 | 15.5378 | 452.8398 | 1.4765 | 1.899
347 | 3698.6375 | 12.0595 | 15.5104 | 682.1125 | 2.224 | 2.8605
348 | 3692.1475 | 12.0383 | 15.4832 | 911.3525 | 2.9715 | 3.8218
349 | 3685.6901 | 12.0172 | 15.4561 | 1140.5599 | 3.7188 | 4.783
350 | 3679.2651 | 11.9963 | 15.4292 | 1369.7349 | 4.466 | 5.7441
351 | 3672.8725 | 11.9755 | 15.4024 | 1227.6275 | 4.0027 | 5.1481
352 | 3672.5112 | 11.9743 | 15.4009 | 1425.9888 | 4.6495 | 5.98
353 | 3680.188 | 11.9993 | 15.4331 | 2111.312 | 6.884 | 8.8539
354 | 3687.8284 | 12.0242 | 15.4651 | 1955.1716 | 6.3749 | 8.1991
355 | 3695.4321 | 12.049 | 15.497 | 2244.5679 | 7.3184 | 9.4127
356 | 3702.9991 | 12.0737 | 15.5287 | 1940.0009 | 6.3254 | 8.1355
357 | 3710.5295 | 12.0982 | 15.5603 | 2377.9705 | 7.7534 | 9.9722
358 | 3718.0231 | 12.1227 | 15.5917 | 1627.9769 | 5.308 | 6.827
359 | 3717.4387 | 12.1208 | 15.5893 | 886.0613 | 2.889 | 3.7157
360 | 3710.8963 | 12.0994 | 15.5618 | 150.1037 | 0.48942 | 0.62947
361 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
362 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
363 | 2554.2 | 8.328 | 10.7112 | 0 | 0 | 0
364 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
365 | 2948.7857 | 9.6146 | 12.3659 | 0 | 0 | 0
366 | 3139.7143 | 10.2371 | 13.1666 | 0 | 0 | 0
367 | 3330.6429 | 10.8596 | 13.9672 | 0 | 0 | 0
368 | 3521.5714 | 11.4821 | 14.7679 | 0 | 0 | 0
369 | 3693.3152 | 12.0421 | 15.4881 | 19.1848 | 0.062552 | 0.080452
370 | 3686.9114 | 12.0212 | 15.4613 | 216.5172 | 0.70596 | 0.90798
371 | 3680.5397 | 12.0005 | 15.4345 | 413.8174 | 1.3493 | 1.7354
372 | 3674.2002 | 11.9798 | 15.408 | 611.0855 | 1.9925 | 2.5626
373 | 3667.8927 | 11.9592 | 15.3815 | 808.3216 | 2.6355 | 3.3897
374 | 3661.617 | 11.9388 | 15.3552 | 1005.5258 | 3.2785 | 4.2167
375 | 3655.3732 | 11.9184 | 15.329 | 1202.6983 | 3.9214 | 5.0436
376 | 3655.1005 | 11.9175 | 15.3279 | 1393.8995 | 4.5448 | 5.8454
377 | 3662.8542 | 11.9428 | 15.3604 | 1237.6458 | 4.0354 | 5.1901
378 | 3670.572 | 11.968 | 15.3927 | 1526.928 | 4.9786 | 6.4033
379 | 3678.2533 | 11.993 | 15.425 | 1816.2467 | 5.9219 | 7.6165
380 | 3685.8975 | 12.0179 | 15.457 | 1957.1025 | 6.3812 | 8.2072
381 | 3693.5038 | 12.0427 | 15.4889 | 2394.9962 | 7.8089 | 10.0435
382 | 3701.0719 | 12.0674 | 15.5206 | 1644.9281 | 5.3633 | 6.8981
383 | 3700.5712 | 12.0658 | 15.5185 | 902.9288 | 2.944 | 3.7865
384 | 3694.1749 | 12.0449 | 15.4917 | 166.8251 | 0.54394 | 0.69959
385 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
386 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
387 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
388 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
389 | 2992.8462 | 9.7582 | 12.5507 | 0 | 0 | 0
390 | 3198.4615 | 10.4286 | 13.4129 | 0 | 0 | 0
391 | 3404.0769 | 11.099 | 14.2752 | 0 | 0 | 0
392 | 3609.6923 | 11.7695 | 15.1374 | 0 | 0 | 0
393 | 3676.7973 | 11.9883 | 15.4189 | 138.5103 | 0.45162 | 0.58085
394 | 3670.5391 | 11.9678 | 15.3926 | 350.384 | 1.1424 | 1.4694
395 | 3664.3124 | 11.9475 | 15.3665 | 562.226 | 1.8331 | 2.3577
396 | 3658.1173 | 11.9273 | 15.3405 | 774.0365 | 2.5238 | 3.246
397 | 3651.9537 | 11.9073 | 15.3147 | 985.8156 | 3.2143 | 4.1341
398 | 3645.8213 | 11.8873 | 15.289 | 1197.5633 | 3.9047 | 5.022
399 | 3639.7202 | 11.8674 | 15.2634 | 1409.2798 | 4.595 | 5.9099
400 | 3639.5078 | 11.8667 | 15.2625 | 1260.9922 | 4.1115 | 5.288
401 | 3647.3058 | 11.8921 | 15.2952 | 1520.4942 | 4.9576 | 6.3763
402 | 3655.0661 | 11.9174 | 15.3277 | 1780.0339 | 5.8038 | 7.4647
403 | 3662.7881 | 11.9426 | 15.3601 | 2277.2119 | 7.4249 | 9.5496
404 | 3670.4709 | 11.9676 | 15.3923 | 2269.5291 | 7.3998 | 9.5174
405 | 3678.1144 | 11.9925 | 15.4244 | 2558.8856 | 8.3433 | 10.7308
406 | 3685.7187 | 12.0173 | 15.4563 | 1779.0813 | 5.8007 | 7.4607
407 | 3685.9745 | 12.0182 | 15.4573 | 1006.6255 | 3.2821 | 4.2213
408 | 3680.5997 | 12.0007 | 15.4348 | 239.8003 | 0.78187 | 1.0056
409 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
410 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
411 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
412 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
413 | 2970 | 9.6837 | 12.4549 | 0 | 0 | 0
414 | 3168 | 10.3293 | 13.2852 | 0 | 0 | 0
415 | 3366 | 10.9749 | 14.1155 | 0 | 0 | 0
416 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
417 | 3680.1414 | 11.9992 | 15.4329 | 81.8586 | 0.2669 | 0.34328
418 | 3688.6536 | 12.0269 | 15.4686 | 271.3464 | 0.88473 | 1.1379
419 | 3697.1326 | 12.0546 | 15.5041 | 460.8674 | 1.5027 | 1.9327
420 | 3705.5781 | 12.0821 | 15.5395 | 650.4219 | 2.1207 | 2.7276
421 | 3713.9897 | 12.1095 | 15.5748 | 840.0103 | 2.7389 | 3.5226
422 | 3722.3671 | 12.1368 | 15.61 | 1029.6329 | 3.3571 | 4.3178
423 | 3730.7099 | 12.164 | 15.6449 | 872.7901 | 2.8457 | 3.6601
424 | 3739.0186 | 12.1911 | 15.6798 | 1210.9814 | 3.9484 | 5.0783
425 | 3747.2925 | 12.2181 | 15.7145 | 1549.2075 | 5.0512 | 6.4967
426 | 3755.5308 | 12.245 | 15.749 | 1887.4692 | 6.1541 | 7.9152
427 | 3763.4684 | 12.2708 | 15.7823 | 1471.1566 | 4.7967 | 6.1694
428 | 3768.9918 | 12.2889 | 15.8055 | 1057.2582 | 3.4472 | 4.4337
429 | 3774.4867 | 12.3068 | 15.8285 | 643.3883 | 2.0978 | 2.6981
430 | 3779.9546 | 12.3246 | 15.8514 | 229.5454 | 0.74844 | 0.96261
431 | 3601.125 | 11.7415 | 15.1015 | 0 | 0 | 0
432 | 2970 | 9.6837 | 12.4549 | 0 | 0 | 0
433 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
434 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
435 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
436 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
437 | 2943 | 9.5957 | 12.3416 | 0 | 0 | 0
438 | 3132 | 10.2119 | 13.1342 | 0 | 0 | 0
439 | 3321 | 10.8282 | 13.9268 | 0 | 0 | 0
440 | 3510 | 11.4444 | 14.7194 | 0 | 0 | 0
441 | 3699 | 12.0606 | 15.512 | 0 | 0 | 0
442 | 3751.7524 | 12.2326 | 15.7332 | 136.2476 | 0.44424 | 0.57136
443 | 3757.3109 | 12.2508 | 15.7565 | 319.6891 | 1.0424 | 1.3406
444 | 3762.8446 | 12.2688 | 15.7797 | 503.1554 | 1.6405 | 2.11
445 | 3768.3532 | 12.2868 | 15.8028 | 686.6468 | 2.2388 | 2.8795
446 | 3773.8363 | 12.3047 | 15.8258 | 596.3065 | 1.9443 | 2.5006
447 | 3779.2944 | 12.3224 | 15.8487 | 505.9913 | 1.6498 | 2.1219
448 | 3784.7278 | 12.3402 | 15.8715 | 415.7008 | 1.3554 | 1.7433
449 | 3790.1371 | 12.3578 | 15.8941 | 325.4344 | 1.0611 | 1.3647
450 | 3795.5226 | 12.3754 | 15.9167 | 235.1917 | 0.76685 | 0.98629
451 | 3800.8848 | 12.3928 | 15.9392 | 144.9724 | 0.47268 | 0.60795
452 | 3806.2241 | 12.4103 | 15.9616 | 54.7759 | 0.1786 | 0.22971
453 | 3811.5409 | 12.4276 | 15.9839 | 346.4591 | 1.1296 | 1.4529
454 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
455 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
456 | 2821.5 | 9.1995 | 11.8321 | 0 | 0 | 0
457 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
458 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
459 | 2545.7143 | 8.3003 | 10.6756 | 0 | 0 | 0
460 | 2715.4286 | 8.8537 | 11.3873 | 0 | 0 | 0
461 | 2885.1429 | 9.4071 | 12.099 | 0 | 0 | 0
462 | 3054.8571 | 9.9604 | 12.8107 | 0 | 0 | 0
463 | 3224.5714 | 10.5138 | 13.5224 | 0 | 0 | 0
464 | 3394.2857 | 11.0671 | 14.2341 | 0 | 0 | 0
465 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
466 | 3733.7143 | 12.1738 | 15.6575 | 0 | 0 | 0
467 | 3759.1954 | 12.2569 | 15.7644 | 144.2331 | 0.47027 | 0.60485
468 | 3749.962 | 12.2268 | 15.7257 | 323.1808 | 1.0537 | 1.3553
469 | 3740.7663 | 12.1968 | 15.6871 | 417.2337 | 1.3604 | 1.7497
470 | 3731.6081 | 12.167 | 15.6487 | 426.3919 | 1.3903 | 1.7881
471 | 3723.2812 | 12.1398 | 15.6138 | 859.0045 | 2.8008 | 3.6023
472 | 3722.7273 | 12.138 | 15.6115 | 1029.2727 | 3.356 | 4.3163
473 | 3730.1976 | 12.1624 | 15.6428 | 784.2024 | 2.5569 | 3.2886
474 | 3737.6402 | 12.1866 | 15.674 | 539.1598 | 1.7579 | 2.261
475 | 3745.056 | 12.2108 | 15.7051 | 412.944 | 1.3464 | 1.7317
476 | 3752.4455 | 12.2349 | 15.7361 | 49.1545 | 0.16027 | 0.20613
477 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
478 | 3326.4 | 10.8458 | 13.9494 | 0 | 0 | 0
479 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
480 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
481 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
482 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
483 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
484 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
485 | 2821.5 | 9.1995 | 11.8321 | 0 | 0 | 0
486 | 2970 | 9.6837 | 12.4549 | 0 | 0 | 0
487 | 3118.5 | 10.1679 | 13.0776 | 0 | 0 | 0
488 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
489 | 3415.5 | 11.1363 | 14.3231 | 0 | 0 | 0
490 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
491 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
492 | 3722.3563 | 12.1368 | 15.6099 | 138.6437 | 0.45205 | 0.58141
493 | 3716.8262 | 12.1188 | 15.5867 | 292.6738 | 0.95427 | 1.2273
494 | 3711.3265 | 12.1008 | 15.5637 | 446.6735 | 1.4564 | 1.8732
495 | 3705.857 | 12.083 | 15.5407 | 303.643 | 0.99003 | 1.2733
496 | 3706.3757 | 12.0847 | 15.5429 | 451.6243 | 1.4725 | 1.8939
497 | 3714.9289 | 12.1126 | 15.5788 | 1037.0711 | 3.3814 | 4.349
498 | 3723.4502 | 12.1404 | 15.6145 | 880.0498 | 2.8694 | 3.6905
499 | 3731.9396 | 12.168 | 15.6501 | 1168.5604 | 3.8101 | 4.9004
500 | 3740.3968 | 12.1956 | 15.6856 | 833.4032 | 2.7173 | 3.4949
501 | 3748.8225 | 12.2231 | 15.7209 | 498.2775 | 1.6246 | 2.0896
502 | 3757.2178 | 12.2505 | 15.7561 | 163.1822 | 0.53206 | 0.68431
503 | 3593.7 | 11.7173 | 15.0704 | 0 | 0 | 0
504 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
505 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
506 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
507 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
508 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
509 | 3044.25 | 9.9258 | 12.7662 | 0 | 0 | 0
510 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
511 | 3489.75 | 11.3784 | 14.6345 | 0 | 0 | 0
512 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
513 | 3743.526 | 12.2058 | 15.6987 | 191.724 | 0.62512 | 0.80401
514 | 3738.0022 | 12.1878 | 15.6755 | 419.9978 | 1.3694 | 1.7613
515 | 3732.5087 | 12.1699 | 15.6525 | 648.2413 | 2.1136 | 2.7184
516 | 3727.0453 | 12.1521 | 15.6296 | 876.4547 | 2.8577 | 3.6755
517 | 3721.612 | 12.1344 | 15.6068 | 1104.638 | 3.6017 | 4.6324
518 | 3716.2085 | 12.1168 | 15.5841 | 1332.7915 | 4.3456 | 5.5891
519 | 3710.8349 | 12.0992 | 15.5616 | 1189.6651 | 3.8789 | 4.9889
520 | 3711.4752 | 12.1013 | 15.5643 | 1387.0248 | 4.5224 | 5.8166
521 | 3720.1502 | 12.1296 | 15.6007 | 2071.3498 | 6.7537 | 8.6863
522 | 3728.7884 | 12.1578 | 15.6369 | 1914.2116 | 6.2413 | 8.0274
523 | 3737.3895 | 12.1858 | 15.6729 | 2202.6105 | 7.1816 | 9.2368
524 | 3745.9533 | 12.2137 | 15.7089 | 1897.0467 | 6.1853 | 7.9554
525 | 3754.4801 | 12.2415 | 15.7446 | 2334.0199 | 7.6101 | 9.7878
526 | 3762.9697 | 12.2692 | 15.7802 | 1583.0303 | 5.1615 | 6.6385
527 | 3760.7366 | 12.2619 | 15.7709 | 842.7634 | 2.7478 | 3.5342
528 | 3752.5513 | 12.2353 | 15.7365 | 108.4487 | 0.3536 | 0.45479
529 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
530 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
531 | 2554.2 | 8.328 | 10.7112 | 0 | 0 | 0
532 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
533 | 2948.7857 | 9.6146 | 12.3659 | 0 | 0 | 0
534 | 3139.7143 | 10.2371 | 13.1666 | 0 | 0 | 0
535 | 3330.6429 | 10.8596 | 13.9672 | 0 | 0 | 0
536 | 3521.5714 | 11.4821 | 14.7679 | 0 | 0 | 0
537 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
538 | 3722.1511 | 12.1361 | 15.609 | 181.2775 | 0.59106 | 0.7602
539 | 3715.9065 | 12.1158 | 15.5829 | 378.4507 | 1.2339 | 1.5871
540 | 3709.6932 | 12.0955 | 15.5568 | 575.5925 | 1.8767 | 2.4138
541 | 3703.5111 | 12.0754 | 15.5309 | 772.7032 | 2.5194 | 3.2404
542 | 3697.3601 | 12.0553 | 15.5051 | 969.7828 | 3.162 | 4.0668
543 | 3691.2401 | 12.0353 | 15.4794 | 1166.8313 | 3.8045 | 4.8932
544 | 3691.1147 | 12.0349 | 15.4789 | 1357.8853 | 4.4274 | 5.6944
545 | 3699.0209 | 12.0607 | 15.512 | 1201.4791 | 3.9174 | 5.0385
546 | 3706.8921 | 12.0864 | 15.5451 | 1490.6079 | 4.8601 | 6.2509
547 | 3714.7278 | 12.1119 | 15.5779 | 1779.7722 | 5.803 | 7.4636
548 | 3722.5273 | 12.1374 | 15.6106 | 1920.4727 | 6.2617 | 8.0536
549 | 3730.2899 | 12.1627 | 15.6432 | 2358.2101 | 7.689 | 9.8893
550 | 3738.0151 | 12.1879 | 15.6756 | 1607.9849 | 5.2429 | 6.7432
551 | 3737.6664 | 12.1867 | 15.6741 | 865.8336 | 2.8231 | 3.6309
552 | 3731.3857 | 12.1662 | 15.6478 | 129.6143 | 0.42261 | 0.54354
553 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
554 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
555 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
556 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
557 | 2992.8462 | 9.7582 | 12.5507 | 0 | 0 | 0
558 | 3198.4615 | 10.4286 | 13.4129 | 0 | 0 | 0
559 | 3404.0769 | 11.099 | 14.2752 | 0 | 0 | 0
560 | 3609.6923 | 11.7695 | 15.1374 | 0 | 0 | 0
561 | 3715.8668 | 12.1156 | 15.5827 | 99.4409 | 0.32423 | 0.41701
562 | 3709.7126 | 12.0956 | 15.5569 | 311.2104 | 1.0147 | 1.3051
563 | 3703.5894 | 12.0756 | 15.5312 | 522.9491 | 1.7051 | 2.193
564 | 3697.497 | 12.0557 | 15.5057 | 734.6569 | 2.3954 | 3.0808
565 | 3691.4353 | 12.036 | 15.4802 | 946.334 | 3.0855 | 3.9685
566 | 3685.4042 | 12.0163 | 15.4549 | 1157.9805 | 3.7756 | 4.8561
567 | 3679.4036 | 11.9968 | 15.4298 | 1369.5964 | 4.4656 | 5.7435
568 | 3679.3522 | 11.9966 | 15.4296 | 1221.1478 | 3.9816 | 5.121
569 | 3687.323 | 12.0226 | 15.463 | 1480.477 | 4.8271 | 6.2085
570 | 3695.2569 | 12.0484 | 15.4963 | 1739.8431 | 5.6728 | 7.2961
571 | 3703.1529 | 12.0742 | 15.5294 | 2236.8471 | 7.2933 | 9.3803
572 | 3711.0102 | 12.0998 | 15.5623 | 2228.9898 | 7.2677 | 9.3474
573 | 3718.8283 | 12.1253 | 15.5951 | 2518.1717 | 8.2105 | 10.5601
574 | 3726.7836 | 12.1512 | 15.6285 | 1738.0164 | 5.6668 | 7.2885
575 | 3727.3777 | 12.1532 | 15.631 | 965.2223 | 3.1471 | 4.0477
576 | 3722.0938 | 12.1359 | 15.6088 | 198.3062 | 0.64658 | 0.83161
577 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
578 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
579 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
580 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
581 | 2970 | 9.6837 | 12.4549 | 0 | 0 | 0
582 | 3168 | 10.3293 | 13.2852 | 0 | 0 | 0
583 | 3366 | 10.9749 | 14.1155 | 0 | 0 | 0
584 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
585 | 3723.4546 | 12.1404 | 15.6145 | 38.5454 | 0.12568 | 0.16164
586 | 3732.1285 | 12.1687 | 15.6509 | 227.8715 | 0.74298 | 0.95559
587 | 3740.7674 | 12.1968 | 15.6871 | 417.2326 | 1.3604 | 1.7497
588 | 3749.3708 | 12.2249 | 15.7232 | 606.6292 | 1.9779 | 2.5439
589 | 3757.9382 | 12.2528 | 15.7591 | 796.0618 | 2.5956 | 3.3383
590 | 3765.4106 | 12.2772 | 15.7905 | 986.5894 | 3.2168 | 4.1373
591 | 3771.2621 | 12.2963 | 15.815 | 832.2379 | 2.7135 | 3.49
592 | 3777.0819 | 12.3152 | 15.8394 | 1172.9181 | 3.8243 | 4.9187
593 | 3782.8692 | 12.3341 | 15.8637 | 1513.6308 | 4.9352 | 6.3475
594 | 3788.6231 | 12.3529 | 15.8878 | 1854.3769 | 6.0462 | 7.7764
595 | 3794.343 | 12.3715 | 15.9118 | 1440.282 | 4.6961 | 6.0399
596 | 3800.03 | 12.3901 | 15.9356 | 1026.22 | 3.346 | 4.3035
597 | 3805.6852 | 12.4085 | 15.9594 | 612.1898 | 1.9961 | 2.5673
598 | 3811.3101 | 12.4268 | 15.9829 | 198.1899 | 0.6462 | 0.83112
599 | 3601.125 | 11.7415 | 15.1015 | 0 | 0 | 0
600 | 2970 | 9.6837 | 12.4549 | 0 | 0 | 0
601 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
602 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
603 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
604 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
605 | 2943 | 9.5957 | 12.3416 | 0 | 0 | 0
606 | 3132 | 10.2119 | 13.1342 | 0 | 0 | 0
607 | 3321 | 10.8282 | 13.9268 | 0 | 0 | 0
608 | 3510 | 11.4444 | 14.7194 | 0 | 0 | 0
609 | 3699 | 12.0606 | 15.512 | 0 | 0 | 0
610 | 3785.1332 | 12.3415 | 15.8732 | 102.8668 | 0.3354 | 0.43138
611 | 3790.8012 | 12.36 | 15.8969 | 286.1988 | 0.93316 | 1.2002
612 | 3796.4411 | 12.3784 | 15.9206 | 469.5589 | 1.531 | 1.9691
613 | 3802.0525 | 12.3966 | 15.9441 | 652.9475 | 2.1289 | 2.7382
614 | 3807.6352 | 12.4149 | 15.9675 | 562.5077 | 1.8341 | 2.3589
615 | 3813.1895 | 12.433 | 15.9908 | 472.0962 | 1.5393 | 1.9798
616 | 3818.7159 | 12.451 | 16.014 | 381.7126 | 1.2446 | 1.6007
617 | 3824.215 | 12.4689 | 16.0371 | 291.3565 | 0.94997 | 1.2218
618 | 3829.687 | 12.4868 | 16.06 | 201.0273 | 0.65545 | 0.84302
619 | 3835.1326 | 12.5045 | 16.0828 | 110.7246 | 0.36102 | 0.46433
620 | 3840.5521 | 12.5222 | 16.1056 | 20.4479 | 0.066671 | 0.08575
621 | 3845.9458 | 12.5398 | 16.1282 | 312.0542 | 1.0175 | 1.3086
622 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
623 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
624 | 2821.5 | 9.1995 | 11.8321 | 0 | 0 | 0
625 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
626 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
627 | 2545.7143 | 8.3003 | 10.6756 | 0 | 0 | 0
628 | 2715.4286 | 8.8537 | 11.3873 | 0 | 0 | 0
629 | 2885.1429 | 9.4071 | 12.099 | 0 | 0 | 0
630 | 3054.8571 | 9.9604 | 12.8107 | 0 | 0 | 0
631 | 3224.5714 | 10.5138 | 13.5224 | 0 | 0 | 0
632 | 3394.2857 | 11.0671 | 14.2341 | 0 | 0 | 0
633 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
634 | 3733.7143 | 12.1738 | 15.6575 | 0 | 0 | 0
635 | 3795.3094 | 12.3747 | 15.9158 | 108.1191 | 0.35252 | 0.4534
636 | 3786.1391 | 12.3448 | 15.8774 | 287.0038 | 0.93578 | 1.2036
637 | 3777.0059 | 12.315 | 15.8391 | 380.9941 | 1.2422 | 1.5977
638 | 3767.9097 | 12.2853 | 15.8009 | 390.0903 | 1.2719 | 1.6359
639 | 3758.8505 | 12.2558 | 15.7629 | 823.4352 | 2.6848 | 3.4531
640 | 3755.6738 | 12.2454 | 15.7496 | 996.3262 | 3.2485 | 4.1781
641 | 3760.5163 | 12.2612 | 15.7699 | 753.8837 | 2.458 | 3.1615
642 | 3765.3338 | 12.2769 | 15.7901 | 511.4662 | 1.6676 | 2.1449
643 | 3770.1271 | 12.2926 | 15.8102 | 387.8729 | 1.2647 | 1.6266
644 | 3774.897 | 12.3081 | 15.8302 | 26.703 | 0.087065 | 0.11198
645 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
646 | 3326.4 | 10.8458 | 13.9494 | 0 | 0 | 0
647 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
648 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
649 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
650 | 2376 | 7.747 | 9.9639 | 0 | 0 | 0
651 | 2524.5 | 8.2312 | 10.5866 | 0 | 0 | 0
652 | 2673 | 8.7154 | 11.2094 | 0 | 0 | 0
653 | 2821.5 | 9.1995 | 11.8321 | 0 | 0 | 0
654 | 2970 | 9.6837 | 12.4549 | 0 | 0 | 0
655 | 3118.5 | 10.1679 | 13.0776 | 0 | 0 | 0
656 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
657 | 3415.5 | 11.1363 | 14.3231 | 0 | 0 | 0
658 | 3564 | 11.6205 | 14.9458 | 0 | 0 | 0
659 | 3712.5 | 12.1047 | 15.5686 | 0 | 0 | 0
660 | 3717.5011 | 12.121 | 15.5895 | 143.4989 | 0.46788 | 0.60177
661 | 3711.2215 | 12.1005 | 15.5632 | 298.2785 | 0.97254 | 1.2508
662 | 3704.9734 | 12.0801 | 15.537 | 453.0266 | 1.4771 | 1.8998
663 | 3698.7567 | 12.0599 | 15.5109 | 310.7433 | 1.0132 | 1.3031
664 | 3698.4697 | 12.0589 | 15.5097 | 459.5303 | 1.4983 | 1.9271
665 | 3706.2076 | 12.0841 | 15.5422 | 1045.7924 | 3.4098 | 4.3856
666 | 3713.915 | 12.1093 | 15.5745 | 889.585 | 2.9005 | 3.7305
667 | 3721.5917 | 12.1343 | 15.6067 | 1178.9083 | 3.8438 | 4.9438
668 | 3729.2375 | 12.1592 | 15.6388 | 844.5625 | 2.7537 | 3.5417
669 | 3736.8531 | 12.1841 | 15.6707 | 510.2469 | 1.6637 | 2.1397
670 | 3744.4395 | 12.2088 | 15.7025 | 175.9605 | 0.57372 | 0.7379
671 | 3593.7 | 11.7173 | 15.0704 | 0 | 0 | 0
672 | 3267 | 10.6521 | 13.7003 | 0 | 0 | 0
339293.6997

## Spring Autumn
Spring/Autumn
| Hot Sink |  |  | Cold Sink
| Condenser Duty | Refrig mass flow rate |  | Condenser Duty | Refrig mass flow rate
| Qcond,h | ṁ ref | Condenser | Qcond,c | ṁ ref | Condenser | Total
Total | 2182261.1703 |  | 9151.4326 | 640290.5163 |  | 2685.0936 | 11836.5262
Hours | kW | kg/s | kW | kW | kg/s | kW
1 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
2 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
3 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
4 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
5 | 3272.7044 | 10.6707 | 13.7243 | 0 | 0 | 0
6 | 3512.1706 | 11.4515 | 14.7285 | 0 | 0 | 0
7 | 3718.4927 | 12.1242 | 15.5937 | 33.144 | 0.10807 | 0.13899
8 | 3717.5067 | 12.121 | 15.5896 | 273.5962 | 0.89206 | 1.1473
9 | 3712.4356 | 12.1045 | 15.5683 | 518.1335 | 1.6894 | 2.1728
10 | 3705.1105 | 12.0806 | 15.5376 | 764.9247 | 2.494 | 3.2078
11 | 3697.8219 | 12.0568 | 15.507 | 1011.6796 | 3.2986 | 4.2425
12 | 3690.5694 | 12.0332 | 15.4766 | 1258.3982 | 4.103 | 5.2772
13 | 3683.353 | 12.0096 | 15.4463 | 1505.0808 | 4.9073 | 6.3116
14 | 3676.1725 | 11.9862 | 15.4162 | 1751.7274 | 5.7115 | 7.346
15 | 3669.0279 | 11.9629 | 15.3863 | 1599.2279 | 5.2143 | 6.7065
16 | 3664.1878 | 11.9471 | 15.366 | 1816.9269 | 5.9241 | 7.6194
17 | 3663.4534 | 11.9447 | 15.3629 | 2562.6671 | 8.3556 | 10.7467
18 | 3662.7215 | 11.9424 | 15.3598 | 2403.7549 | 7.8375 | 10.0803
19 | 3661.9919 | 11.94 | 15.3568 | 2723.7728 | 8.8809 | 11.4223
20 | 3661.2642 | 11.9376 | 15.3537 | 2405.2123 | 7.8422 | 10.0864
21 | 3660.5386 | 11.9352 | 15.3507 | 2884.8702 | 9.4062 | 12.0979
22 | 3659.8147 | 11.9329 | 15.3476 | 2087.3735 | 6.8059 | 8.7535
23 | 3655.0143 | 11.9172 | 15.3275 | 1293.9533 | 4.219 | 5.4263
24 | 3647.9938 | 11.8943 | 15.2981 | 502.7532 | 1.6392 | 2.1083
25 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
26 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
27 | 2745.8788 | 8.953 | 11.515 | 0 | 0 | 0
28 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
29 | 3170.076 | 10.3361 | 13.2939 | 0 | 0 | 0
30 | 3375.3327 | 11.0053 | 14.1546 | 0 | 0 | 0
31 | 3580.5895 | 11.6746 | 15.0154 | 0 | 0 | 0
32 | 3610.8818 | 11.7733 | 15.1424 | 174.9644 | 0.57047 | 0.73372
33 | 3606.9574 | 11.7605 | 15.126 | 384.1455 | 1.2525 | 1.6109
34 | 3601.0728 | 11.7414 | 15.1013 | 595.2868 | 1.9409 | 2.4964
35 | 3595.221 | 11.7223 | 15.0768 | 806.3953 | 2.6293 | 3.3817
36 | 3589.4018 | 11.7033 | 15.0524 | 1017.4712 | 3.3175 | 4.2668
37 | 3583.6152 | 11.6844 | 15.0281 | 1228.5146 | 4.0056 | 5.1518
38 | 3577.8609 | 11.6657 | 15.004 | 1439.5256 | 4.6936 | 6.0367
39 | 3572.0508 | 11.6467 | 14.9796 | 1650.5925 | 5.3818 | 6.9219
40 | 3567.7202 | 11.6326 | 14.9614 | 1860.1798 | 6.0651 | 7.8008
41 | 3567.482 | 11.6318 | 14.9604 | 1700.7738 | 5.5454 | 7.1323
42 | 3567.2472 | 11.6311 | 14.9594 | 2020.2969 | 6.5872 | 8.4722
43 | 3567.0151 | 11.6303 | 14.9585 | 2339.8172 | 7.629 | 9.8122
44 | 3566.7849 | 11.6296 | 14.9575 | 2499.6915 | 8.1503 | 10.4826
45 | 3566.556 | 11.6288 | 14.9565 | 2978.8528 | 9.7126 | 12.492
46 | 3566.3279 | 11.6281 | 14.9556 | 2180.8603 | 7.1107 | 9.1456
47 | 3562.0313 | 11.6141 | 14.9376 | 1386.9363 | 4.5221 | 5.8162
48 | 3555.535 | 11.5929 | 14.9103 | 595.212 | 1.9407 | 2.4961
49 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
50 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
51 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
52 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
53 | 3217.443 | 10.4905 | 13.4925 | 0 | 0 | 0
54 | 3438.4887 | 11.2112 | 14.4195 | 0 | 0 | 0
55 | 3520.985 | 11.4802 | 14.7654 | 138.5494 | 0.45174 | 0.58101
56 | 3521.0149 | 11.4803 | 14.7656 | 359.5652 | 1.1724 | 1.5079
57 | 3516.9762 | 11.4672 | 14.7486 | 584.6496 | 1.9063 | 2.4518
58 | 3510.7247 | 11.4468 | 14.7224 | 811.9467 | 2.6474 | 3.4049
59 | 3504.5058 | 11.4265 | 14.6963 | 1039.2113 | 3.3884 | 4.358
60 | 3498.3195 | 11.4063 | 14.6704 | 1266.4434 | 4.1293 | 5.3109
61 | 3492.1655 | 11.3863 | 14.6446 | 1493.643 | 4.87 | 6.2637
62 | 3486.0439 | 11.3663 | 14.6189 | 1720.8104 | 5.6107 | 7.2163
63 | 3479.9544 | 11.3464 | 14.5934 | 1947.9455 | 6.3513 | 8.1688
64 | 3476.1335 | 11.334 | 14.5774 | 1792.1224 | 5.8432 | 7.5154
65 | 3476.4034 | 11.3349 | 14.5785 | 2079.2119 | 6.7793 | 8.7193
66 | 3476.6763 | 11.3358 | 14.5796 | 2366.2983 | 7.7154 | 9.9232
67 | 3476.9515 | 11.3367 | 14.5808 | 2908.8132 | 9.4842 | 12.1983
68 | 3477.2276 | 11.3376 | 14.5819 | 2908.537 | 9.4833 | 12.1971
69 | 3477.5044 | 11.3385 | 14.5831 | 3227.5485 | 10.5235 | 13.5349
70 | 3477.7818 | 11.3394 | 14.5843 | 2397.1217 | 7.8159 | 10.0525
71 | 3473.9893 | 11.327 | 14.5684 | 1570.7648 | 5.1215 | 6.5871
72 | 3467.9927 | 11.3074 | 14.5432 | 746.612 | 2.4343 | 3.131
73 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
74 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
75 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
76 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
77 | 3192.8823 | 10.4104 | 13.3895 | 0 | 0 | 0
78 | 3405.7411 | 11.1045 | 14.2822 | 0 | 0 | 0
79 | 3435.8879 | 11.2028 | 14.4086 | 182.7121 | 0.59574 | 0.76621
80 | 3436.4325 | 11.2045 | 14.4109 | 395.0263 | 1.288 | 1.6566
81 | 3436.9856 | 11.2063 | 14.4132 | 607.332 | 1.9802 | 2.5469
82 | 3437.5468 | 11.2082 | 14.4155 | 819.6296 | 2.6724 | 3.4372
83 | 3438.1154 | 11.21 | 14.4179 | 1031.9199 | 3.3646 | 4.3274
84 | 3438.6907 | 11.2119 | 14.4203 | 1244.2033 | 4.0567 | 5.2176
85 | 3439.2723 | 11.2138 | 14.4228 | 1456.4806 | 4.7489 | 6.1078
86 | 3439.8596 | 11.2157 | 14.4252 | 1668.7522 | 5.441 | 6.998
87 | 3440.452 | 11.2176 | 14.4277 | 1508.5156 | 4.9185 | 6.326
88 | 3441.0496 | 11.2196 | 14.4302 | 1880.4209 | 6.1311 | 7.8856
89 | 3441.6513 | 11.2216 | 14.4328 | 2252.3222 | 7.3437 | 9.4452
90 | 3442.2559 | 11.2235 | 14.4353 | 2624.2205 | 8.5563 | 11.0048
91 | 3442.8626 | 11.2255 | 14.4378 | 2184.5925 | 7.1229 | 9.1612
92 | 3443.4723 | 11.2275 | 14.4404 | 1744.9614 | 5.6895 | 7.3176
93 | 3444.0863 | 11.2295 | 14.443 | 1305.3261 | 4.256 | 5.474
94 | 3444.7058 | 11.2315 | 14.4456 | 865.6853 | 2.8226 | 3.6303
95 | 3441.2331 | 11.2202 | 14.431 | 430.1368 | 1.4025 | 1.8038
96 | 3192.8823 | 10.4104 | 13.3895 | 0 | 0 | 0
97 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
98 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
99 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
100 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
101 | 3163.8561 | 10.3158 | 13.2678 | 0 | 0 | 0
102 | 3367.0395 | 10.9783 | 14.1199 | 0 | 0 | 0
103 | 3405.718 | 11.1044 | 14.2821 | 164.505 | 0.53637 | 0.68986
104 | 3406.6054 | 11.1073 | 14.2858 | 366.801 | 1.196 | 1.5382
105 | 3407.4995 | 11.1102 | 14.2895 | 569.0903 | 1.8555 | 2.3865
106 | 3408.3996 | 11.1131 | 14.2933 | 771.3736 | 2.5151 | 3.2348
107 | 3409.305 | 11.1161 | 14.2971 | 973.6516 | 3.1746 | 4.0831
108 | 3410.215 | 11.1191 | 14.3009 | 1175.925 | 3.8341 | 4.9313
109 | 3411.1289 | 11.122 | 14.3048 | 1378.1946 | 4.4936 | 5.7795
110 | 3412.0462 | 11.125 | 14.3086 | 1286.0521 | 4.1932 | 5.3931
111 | 3412.9668 | 11.128 | 14.3125 | 1193.9062 | 3.8927 | 5.0067
112 | 3413.8911 | 11.131 | 14.3163 | 1101.7568 | 3.5923 | 4.6203
113 | 3414.8191 | 11.1341 | 14.3202 | 1009.6035 | 3.2918 | 4.2338
114 | 3415.7511 | 11.1371 | 14.3241 | 917.4463 | 2.9913 | 3.8474
115 | 3416.6873 | 11.1402 | 14.3281 | 825.2849 | 2.6909 | 3.4609
116 | 3417.6279 | 11.1432 | 14.332 | 733.1191 | 2.3903 | 3.0744
117 | 3418.5728 | 11.1463 | 14.336 | 1051.4624 | 3.4283 | 4.4094
118 | 3419.5217 | 11.1494 | 14.34 | 571.5812 | 1.8636 | 2.397
119 | 3416.3466 | 11.139 | 14.3266 | 95.824 | 0.31244 | 0.40184
120 | 3033.2382 | 9.8899 | 12.7201 | 0 | 0 | 0
121 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
122 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
123 | 2736.7563 | 8.9232 | 11.4767 | 0 | 0 | 0
124 | 2919.2067 | 9.5181 | 12.2419 | 0 | 0 | 0
125 | 3101.6571 | 10.113 | 13.007 | 0 | 0 | 0
126 | 3284.1075 | 10.7079 | 13.7721 | 0 | 0 | 0
127 | 3383.5081 | 11.032 | 14.1889 | 83.0498 | 0.27079 | 0.34827
128 | 3385.5819 | 11.0387 | 14.1976 | 263.4265 | 0.85891 | 1.1047
129 | 3383.5204 | 11.032 | 14.189 | 447.9384 | 1.4605 | 1.8785
130 | 3379.0875 | 11.0176 | 14.1704 | 634.8218 | 2.0698 | 2.6622
131 | 3374.682 | 11.0032 | 14.1519 | 821.6776 | 2.6791 | 3.4458
132 | 3370.304 | 10.9889 | 14.1336 | 1008.5061 | 3.2882 | 4.2292
133 | 3365.9532 | 10.9747 | 14.1153 | 1104.082 | 3.5999 | 4.63
134 | 3361.6297 | 10.9606 | 14.0972 | 1108.4056 | 3.614 | 4.6482
135 | 3357.3333 | 10.9466 | 14.0792 | 1568.828 | 5.1152 | 6.579
136 | 3355.4579 | 10.9405 | 14.0713 | 1753.1538 | 5.7162 | 7.3519
137 | 3357.7288 | 10.9479 | 14.0808 | 1495.4523 | 4.8759 | 6.2713
138 | 3359.9973 | 10.9553 | 14.0903 | 1237.7532 | 4.0357 | 5.1906
139 | 3362.2641 | 10.9627 | 14.0998 | 1107.7712 | 3.6119 | 4.6455
140 | 3364.5295 | 10.9701 | 14.1093 | 722.3598 | 2.3553 | 3.0293
141 | 3366.7947 | 10.9775 | 14.1188 | 464.6641 | 1.515 | 1.9486
142 | 3369.0603 | 10.9849 | 14.1283 | 206.9679 | 0.67482 | 0.86793
143 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
144 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
145 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
146 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
147 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
148 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
149 | 3033.2382 | 9.8899 | 12.7201 | 0 | 0 | 0
150 | 3192.8823 | 10.4104 | 13.3895 | 0 | 0 | 0
151 | 3345.6978 | 10.9087 | 14.0304 | 6.8287 | 0.022265 | 0.028636
152 | 3348.1555 | 10.9167 | 14.0407 | 164.0151 | 0.53477 | 0.68781
153 | 3346.4667 | 10.9112 | 14.0336 | 325.348 | 1.0608 | 1.3644
154 | 3342.3787 | 10.8979 | 14.0164 | 489.0801 | 1.5947 | 2.051
155 | 3338.3169 | 10.8846 | 13.9994 | 652.7861 | 2.1284 | 2.7375
156 | 3334.2811 | 10.8715 | 13.9825 | 816.466 | 2.6621 | 3.4239
157 | 3330.2712 | 10.8584 | 13.9657 | 980.1199 | 3.1957 | 4.1102
158 | 3326.2873 | 10.8454 | 13.949 | 1143.748 | 3.7292 | 4.7964
159 | 3322.3291 | 10.8325 | 13.9324 | 988.062 | 3.2216 | 4.1435
160 | 3320.8117 | 10.8276 | 13.926 | 1149.2235 | 3.7471 | 4.8193
161 | 3323.4461 | 10.8361 | 13.9371 | 1785.1656 | 5.8206 | 7.4862
162 | 3326.0746 | 10.8447 | 13.9481 | 1622.893 | 5.2915 | 6.8057
163 | 3328.6969 | 10.8533 | 13.9591 | 1939.5589 | 6.324 | 8.1336
164 | 3331.3128 | 10.8618 | 13.97 | 1585.726 | 5.1703 | 6.6498
165 | 3333.9229 | 10.8703 | 13.981 | 1231.8989 | 4.0166 | 5.166
166 | 3336.5281 | 10.8788 | 13.9919 | 878.0766 | 2.863 | 3.6823
167 | 3334.9869 | 10.8738 | 13.9855 | 528.4007 | 1.7229 | 2.2159
168 | 3331.0563 | 10.861 | 13.969 | 181.1143 | 0.59053 | 0.75951
169 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
170 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
171 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
172 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
173 | 3272.7044 | 10.6707 | 13.7243 | 0 | 0 | 0
174 | 3313.3102 | 10.8031 | 13.8945 | 198.8603 | 0.64839 | 0.83393
175 | 3311.9417 | 10.7986 | 13.8888 | 439.695 | 1.4336 | 1.8439
176 | 3314.7239 | 10.8077 | 13.9005 | 676.379 | 2.2053 | 2.8364
177 | 3313.3589 | 10.8033 | 13.8948 | 917.2102 | 2.9906 | 3.8464
178 | 3309.6029 | 10.791 | 13.879 | 1160.4323 | 3.7836 | 4.8663
179 | 3305.4308 | 10.7774 | 13.8615 | 1404.0706 | 4.578 | 5.888
180 | 3300.8438 | 10.7625 | 13.8423 | 1648.1238 | 5.3737 | 6.9115
181 | 3296.2831 | 10.7476 | 13.8231 | 1892.1507 | 6.1694 | 7.9348
182 | 3291.7486 | 10.7328 | 13.8041 | 2136.1514 | 6.965 | 8.9581
183 | 3287.2402 | 10.7181 | 13.7852 | 1981.0156 | 6.4591 | 8.3075
184 | 3285.142 | 10.7113 | 13.7764 | 2195.9727 | 7.16 | 9.2089
185 | 3287.1813 | 10.7179 | 13.785 | 2938.9392 | 9.5825 | 12.3246
186 | 3289.2105 | 10.7245 | 13.7935 | 2777.2659 | 9.0553 | 11.6466
187 | 3291.2294 | 10.7311 | 13.802 | 3094.5353 | 10.0898 | 12.9771
188 | 3293.2374 | 10.7377 | 13.8104 | 2773.2391 | 9.0422 | 11.6297
189 | 3295.2348 | 10.7442 | 13.8187 | 3250.174 | 10.5972 | 13.6298
190 | 3297.2213 | 10.7506 | 13.8271 | 2449.9669 | 7.9882 | 10.2741
191 | 3295.0772 | 10.7436 | 13.8181 | 1653.8904 | 5.3925 | 6.9357
192 | 3290.6017 | 10.7291 | 13.7993 | 860.1453 | 2.8045 | 3.6071
193 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
194 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
195 | 2745.8788 | 8.953 | 11.515 | 0 | 0 | 0
196 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
197 | 3170.076 | 10.3361 | 13.2939 | 0 | 0 | 0
198 | 3269.0402 | 10.6588 | 13.7089 | 106.2926 | 0.34657 | 0.44574
199 | 3267.0611 | 10.6523 | 13.7006 | 313.5284 | 1.0223 | 1.3148
200 | 3269.2085 | 10.6593 | 13.7096 | 516.6377 | 1.6845 | 2.1665
201 | 3267.2347 | 10.6529 | 13.7013 | 723.8682 | 2.3602 | 3.0356
202 | 3262.9414 | 10.6389 | 13.6833 | 933.4183 | 3.0434 | 3.9143
203 | 3258.6733 | 10.625 | 13.6654 | 1142.9431 | 3.7266 | 4.793
204 | 3254.4303 | 10.6111 | 13.6476 | 1352.4428 | 4.4097 | 5.6715
205 | 3250.2124 | 10.5974 | 13.6299 | 1561.9174 | 5.0927 | 6.55
206 | 3246.0194 | 10.5837 | 13.6124 | 1771.3671 | 5.7756 | 7.4283
207 | 3241.8513 | 10.5701 | 13.5949 | 1980.7919 | 6.4584 | 8.3066
208 | 3240.0166 | 10.5641 | 13.5872 | 2187.8834 | 7.1336 | 9.175
209 | 3242.2925 | 10.5715 | 13.5967 | 2025.9634 | 6.6057 | 8.496
210 | 3244.5583 | 10.5789 | 13.6062 | 2342.9858 | 7.6393 | 9.8254
211 | 3246.8133 | 10.5863 | 13.6157 | 2660.019 | 8.673 | 11.1549
212 | 3249.0566 | 10.5936 | 13.6251 | 2817.4198 | 9.1862 | 11.815
213 | 3251.2876 | 10.6009 | 13.6345 | 3294.1212 | 10.7405 | 13.8141
214 | 3253.5056 | 10.6081 | 13.6438 | 2493.6826 | 8.1307 | 10.4574
215 | 3251.6213 | 10.602 | 13.6359 | 1697.3463 | 5.5342 | 7.1179
216 | 3247.4782 | 10.5885 | 13.6185 | 903.2688 | 2.9451 | 3.7879
217 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
218 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
219 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
220 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
221 | 3217.443 | 10.4905 | 13.4925 | 0 | 0 | 0
222 | 3227.434 | 10.5231 | 13.5344 | 211.0547 | 0.68815 | 0.88507
223 | 3225.7001 | 10.5174 | 13.5272 | 433.8342 | 1.4145 | 1.8193
224 | 3228.0571 | 10.5251 | 13.537 | 652.523 | 2.1276 | 2.7364
225 | 3226.3249 | 10.5195 | 13.5298 | 875.3008 | 2.8539 | 3.6706
226 | 3222.355 | 10.5065 | 13.5131 | 1100.3165 | 3.5876 | 4.6142
227 | 3218.409 | 10.4937 | 13.4966 | 1325.3082 | 4.3212 | 5.5578
228 | 3214.4869 | 10.4809 | 13.4801 | 1550.276 | 5.0547 | 6.5012
229 | 3210.5886 | 10.4682 | 13.4638 | 1775.2199 | 5.7881 | 7.4445
230 | 3206.7141 | 10.4555 | 13.4475 | 2000.1402 | 6.5215 | 8.3877
231 | 3202.8632 | 10.443 | 13.4314 | 2225.0367 | 7.2548 | 9.3308
232 | 3201.2569 | 10.4377 | 13.4246 | 2066.9989 | 6.7395 | 8.6681
233 | 3203.7218 | 10.4458 | 13.435 | 2351.8935 | 7.6684 | 9.8628
234 | 3206.1753 | 10.4538 | 13.4453 | 2636.7993 | 8.5973 | 11.0576
235 | 3208.6168 | 10.4617 | 13.4555 | 3177.1479 | 10.3591 | 13.3235
236 | 3211.045 | 10.4697 | 13.4657 | 3174.7196 | 10.3512 | 13.3134
237 | 3213.4598 | 10.4775 | 13.4758 | 3491.5931 | 11.3844 | 14.6422
238 | 3215.861 | 10.4854 | 13.4859 | 2659.0424 | 8.6698 | 11.1508
239 | 3214.1972 | 10.4799 | 13.4789 | 1830.5568 | 5.9686 | 7.6765
240 | 3210.3649 | 10.4674 | 13.4628 | 1004.2397 | 3.2743 | 4.2113
241 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
242 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
243 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
244 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
245 | 3192.8823 | 10.4104 | 13.3895 | 0 | 0 | 0
246 | 3191.8276 | 10.407 | 13.3851 | 213.9136 | 0.69747 | 0.89706
247 | 3190.3144 | 10.4021 | 13.3788 | 428.2856 | 1.3964 | 1.796
248 | 3192.859 | 10.4104 | 13.3894 | 638.5998 | 2.0822 | 2.678
249 | 3195.3989 | 10.4186 | 13.4001 | 848.9187 | 2.7679 | 3.56
250 | 3197.9335 | 10.4269 | 13.4107 | 1059.2429 | 3.4537 | 4.442
251 | 3200.4624 | 10.4352 | 13.4213 | 1269.5729 | 4.1395 | 5.324
252 | 3202.9849 | 10.4434 | 13.4319 | 1479.9091 | 4.8253 | 6.2061
253 | 3205.5007 | 10.4516 | 13.4424 | 1690.2522 | 5.5111 | 7.0882
254 | 3208.0091 | 10.4598 | 13.453 | 1900.6026 | 6.1969 | 7.9703
255 | 3210.5099 | 10.4679 | 13.4635 | 1738.4577 | 5.6683 | 7.2903
256 | 3213.0032 | 10.476 | 13.4739 | 2108.4673 | 6.8747 | 8.842
257 | 3215.4883 | 10.4841 | 13.4843 | 2478.4852 | 8.0811 | 10.3937
258 | 3217.9642 | 10.4922 | 13.4947 | 2848.5122 | 9.2876 | 11.9454
259 | 3220.4304 | 10.5003 | 13.5051 | 2407.0247 | 7.8481 | 10.094
260 | 3222.8878 | 10.5083 | 13.5154 | 1965.546 | 6.4087 | 8.2426
261 | 3225.3381 | 10.5163 | 13.5256 | 1524.0744 | 4.9693 | 6.3913
262 | 3227.7825 | 10.5242 | 13.5359 | 1082.6086 | 3.5299 | 4.54
263 | 3226.1797 | 10.519 | 13.5292 | 645.1902 | 2.1037 | 2.7056
264 | 3192.8823 | 10.4104 | 13.3895 | 0 | 0 | 0
265 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
266 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
267 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
268 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
269 | 3163.8561 | 10.3158 | 13.2678 | 0 | 0 | 0
270 | 3204.971 | 10.4499 | 13.4402 | 162.0685 | 0.52843 | 0.67964
271 | 3203.5322 | 10.4452 | 13.4342 | 366.6907 | 1.1956 | 1.5377
272 | 3206.1505 | 10.4537 | 13.4452 | 567.2559 | 1.8495 | 2.3788
273 | 3208.7664 | 10.4622 | 13.4561 | 767.8234 | 2.5035 | 3.2199
274 | 3211.3795 | 10.4708 | 13.4671 | 968.3937 | 3.1575 | 4.061
275 | 3213.9892 | 10.4793 | 13.478 | 1168.9675 | 3.8114 | 4.9021
276 | 3216.595 | 10.4878 | 13.489 | 1369.545 | 4.4654 | 5.7433
277 | 3219.1965 | 10.4962 | 13.4999 | 1570.127 | 5.1194 | 6.5844
278 | 3221.7932 | 10.5047 | 13.5108 | 1476.3051 | 4.8135 | 6.191
279 | 3224.3855 | 10.5132 | 13.5216 | 1382.4876 | 4.5076 | 5.7975
280 | 3226.9736 | 10.5216 | 13.5325 | 1288.6742 | 4.2017 | 5.4041
281 | 3229.5581 | 10.53 | 13.5433 | 1194.8646 | 3.8959 | 5.0107
282 | 3232.1392 | 10.5384 | 13.5542 | 1101.0582 | 3.59 | 4.6173
283 | 3235.599 | 10.5497 | 13.5687 | 1006.3733 | 3.2813 | 4.2203
284 | 3239.0545 | 10.561 | 13.5832 | 911.6926 | 2.9726 | 3.8232
285 | 3242.5059 | 10.5722 | 13.5976 | 1227.5293 | 4.0024 | 5.1477
286 | 3245.9531 | 10.5835 | 13.6121 | 745.1498 | 2.4296 | 3.1248
287 | 3245.3364 | 10.5815 | 13.6095 | 266.8342 | 0.87002 | 1.119
288 | 3033.2382 | 9.8899 | 12.7201 | 0 | 0 | 0
289 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
290 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
291 | 2736.7563 | 8.9232 | 11.4767 | 0 | 0 | 0
292 | 2919.2067 | 9.5181 | 12.2419 | 0 | 0 | 0
293 | 3101.6571 | 10.113 | 13.007 | 0 | 0 | 0
294 | 3231.59 | 10.5366 | 13.5519 | 52.5175 | 0.17123 | 0.22024
295 | 3231.1331 | 10.5352 | 13.5499 | 235.4248 | 0.76761 | 0.98727
296 | 3234.7565 | 10.547 | 13.5651 | 414.2518 | 1.3507 | 1.7372
297 | 3234.304 | 10.5455 | 13.5632 | 597.1548 | 1.947 | 2.5042
298 | 3231.6338 | 10.5368 | 13.552 | 782.2754 | 2.5506 | 3.2805
299 | 3228.9841 | 10.5282 | 13.5409 | 967.3756 | 3.1541 | 4.0567
300 | 3226.3545 | 10.5196 | 13.5299 | 1152.4555 | 3.7576 | 4.8329
301 | 3223.7452 | 10.5111 | 13.519 | 1246.29 | 4.0635 | 5.2264
302 | 3221.1561 | 10.5026 | 13.5081 | 1248.8792 | 4.072 | 5.2372
303 | 3218.5869 | 10.4943 | 13.4973 | 1707.5744 | 5.5676 | 7.1608
304 | 3218.2809 | 10.4933 | 13.496 | 1890.3308 | 6.1635 | 7.9272
305 | 3222.0584 | 10.5056 | 13.5119 | 1631.1227 | 5.3183 | 6.8402
306 | 3225.8306 | 10.5179 | 13.5277 | 1371.92 | 4.4732 | 5.7532
307 | 3229.5982 | 10.5302 | 13.5435 | 1240.4371 | 4.0445 | 5.2018
308 | 3233.3618 | 10.5424 | 13.5593 | 853.5275 | 2.7829 | 3.5793
309 | 3237.1227 | 10.5547 | 13.5751 | 594.3361 | 1.9378 | 2.4924
310 | 3240.8816 | 10.5669 | 13.5908 | 335.1466 | 1.0928 | 1.4055
311 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
312 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
313 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
314 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
315 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
316 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
317 | 3033.2382 | 9.8899 | 12.7201 | 0 | 0 | 0
318 | 3192.8823 | 10.4104 | 13.3895 | 0 | 0 | 0
319 | 3229.9261 | 10.5312 | 13.5449 | 122.6003 | 0.39974 | 0.51413
320 | 3233.8679 | 10.5441 | 13.5614 | 278.3026 | 0.90741 | 1.1671
321 | 3233.6993 | 10.5435 | 13.5607 | 438.1153 | 1.4285 | 1.8373
322 | 3231.2267 | 10.5355 | 13.5503 | 600.2321 | 1.9571 | 2.5171
323 | 3228.7734 | 10.5275 | 13.54 | 762.3295 | 2.4856 | 3.1969
324 | 3226.3396 | 10.5195 | 13.5298 | 924.4074 | 3.014 | 3.8766
325 | 3223.9251 | 10.5117 | 13.5197 | 1086.4661 | 3.5424 | 4.5562
326 | 3221.5297 | 10.5038 | 13.5097 | 1248.5055 | 4.0708 | 5.2357
327 | 3219.1536 | 10.4961 | 13.4997 | 1091.2376 | 3.558 | 4.5762
328 | 3219.135 | 10.496 | 13.4996 | 1250.9002 | 4.0786 | 5.2457
329 | 3223.2405 | 10.5094 | 13.5168 | 1885.3712 | 6.1473 | 7.9064
330 | 3227.3392 | 10.5228 | 13.534 | 1721.6284 | 5.6134 | 7.2197
331 | 3231.431 | 10.5361 | 13.5512 | 2036.8249 | 6.6411 | 8.5415
332 | 3235.5152 | 10.5494 | 13.5683 | 1681.5235 | 5.4826 | 7.0516
333 | 3239.5928 | 10.5627 | 13.5854 | 1326.229 | 4.3242 | 5.5616
334 | 3243.6646 | 10.576 | 13.6025 | 970.9401 | 3.1658 | 4.0717
335 | 3243.6058 | 10.5758 | 13.6022 | 619.7818 | 2.0208 | 2.5991
336 | 3241.2014 | 10.568 | 13.5922 | 270.9692 | 0.8835 | 1.1363
337 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
338 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
339 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
340 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
341 | 3233.8835 | 10.5441 | 13.5615 | 38.8209 | 0.12658 | 0.1628
342 | 3231.5721 | 10.5366 | 13.5518 | 280.5984 | 0.9149 | 1.1767
343 | 3231.6719 | 10.5369 | 13.5522 | 519.9648 | 1.6954 | 2.1805
344 | 3235.9147 | 10.5507 | 13.57 | 755.1882 | 2.4623 | 3.1669
345 | 3236.0123 | 10.5511 | 13.5704 | 994.5568 | 3.2428 | 4.1707
346 | 3233.7235 | 10.5436 | 13.5608 | 1236.3118 | 4.031 | 5.1845
347 | 3231.4533 | 10.5362 | 13.5513 | 1478.0482 | 4.8192 | 6.1983
348 | 3229.2016 | 10.5289 | 13.5418 | 1719.766 | 5.6073 | 7.2119
349 | 3226.9684 | 10.5216 | 13.5325 | 1961.4654 | 6.3954 | 8.2255
350 | 3224.7535 | 10.5144 | 13.5232 | 2203.1465 | 7.1834 | 9.239
351 | 3222.5569 | 10.5072 | 13.514 | 2045.6989 | 6.67 | 8.5788
352 | 3222.7802 | 10.5079 | 13.5149 | 2258.3344 | 7.3633 | 9.4705
353 | 3227.1438 | 10.5222 | 13.5332 | 2998.9768 | 9.7782 | 12.5764
354 | 3231.4944 | 10.5363 | 13.5515 | 2834.982 | 9.2435 | 11.8887
355 | 3235.832 | 10.5505 | 13.5696 | 3149.9326 | 10.2704 | 13.2094
356 | 3240.1561 | 10.5646 | 13.5878 | 2826.3203 | 9.2153 | 11.8523
357 | 3244.4669 | 10.5786 | 13.6059 | 3300.9419 | 10.7628 | 13.8427
358 | 3248.764 | 10.5926 | 13.6239 | 2498.4242 | 8.1461 | 10.4773
359 | 3248.9114 | 10.5931 | 13.6245 | 1700.0562 | 5.5431 | 7.1293
360 | 3246.6768 | 10.5858 | 13.6151 | 904.0702 | 2.9477 | 3.7913
361 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
362 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
363 | 2745.8788 | 8.953 | 11.515 | 0 | 0 | 0
364 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
365 | 3170.076 | 10.3361 | 13.2939 | 0 | 0 | 0
366 | 3238.0019 | 10.5576 | 13.5787 | 137.3308 | 0.44777 | 0.5759
367 | 3238.289 | 10.5585 | 13.5799 | 342.3004 | 1.1161 | 1.4355
368 | 3242.7252 | 10.573 | 13.5985 | 543.121 | 1.7709 | 2.2776
369 | 3243.0072 | 10.5739 | 13.5997 | 748.0957 | 2.4392 | 3.1372
370 | 3240.8801 | 10.5669 | 13.5908 | 955.4795 | 3.1154 | 4.0069
371 | 3238.7708 | 10.5601 | 13.582 | 1162.8455 | 3.7915 | 4.8765
372 | 3236.6793 | 10.5532 | 13.5732 | 1370.1938 | 4.4675 | 5.746
373 | 3234.6054 | 10.5465 | 13.5645 | 1577.5244 | 5.1435 | 6.6154
374 | 3232.5491 | 10.5398 | 13.5559 | 1784.8375 | 5.8195 | 7.4848
375 | 3230.5103 | 10.5331 | 13.5473 | 1992.133 | 6.4954 | 8.3541
376 | 3230.9088 | 10.5344 | 13.549 | 2196.9911 | 7.1633 | 9.2132
377 | 3235.4523 | 10.5492 | 13.568 | 2032.8036 | 6.628 | 8.5247
378 | 3239.9826 | 10.564 | 13.587 | 2347.5614 | 7.6543 | 9.8446
379 | 3244.4992 | 10.5787 | 13.606 | 2662.3331 | 8.6806 | 11.1646
380 | 3249.0011 | 10.5934 | 13.6249 | 2817.4753 | 9.1864 | 11.8152
381 | 3253.4875 | 10.608 | 13.6437 | 3291.9212 | 10.7334 | 13.8049
382 | 3257.9579 | 10.6226 | 13.6624 | 2489.2303 | 8.1162 | 10.4387
383 | 3258.2714 | 10.6236 | 13.6637 | 1690.6962 | 5.5125 | 7.09
384 | 3256.1869 | 10.6168 | 13.655 | 894.5601 | 2.9167 | 3.7514
385 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
386 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
387 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
388 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
389 | 3217.443 | 10.4905 | 13.4925 | 0 | 0 | 0
390 | 3248.4914 | 10.5918 | 13.6227 | 189.9973 | 0.61949 | 0.79676
391 | 3248.9285 | 10.5932 | 13.6246 | 410.6059 | 1.3388 | 1.7219
392 | 3253.5143 | 10.6081 | 13.6438 | 627.0658 | 2.0446 | 2.6296
393 | 3253.9425 | 10.6095 | 13.6456 | 847.6833 | 2.7639 | 3.5548
394 | 3251.9576 | 10.6031 | 13.6373 | 1070.7139 | 3.4911 | 4.4901
395 | 3249.9898 | 10.5966 | 13.629 | 1293.7273 | 4.2182 | 5.4253
396 | 3248.0391 | 10.5903 | 13.6208 | 1516.7238 | 4.9453 | 6.3605
397 | 3246.1052 | 10.584 | 13.6127 | 1739.7033 | 5.6723 | 7.2955
398 | 3244.1883 | 10.5777 | 13.6047 | 1962.6659 | 6.3993 | 8.2305
399 | 3242.2882 | 10.5715 | 13.5967 | 2185.6118 | 7.1262 | 9.1655
400 | 3242.8174 | 10.5733 | 13.5989 | 2025.4385 | 6.604 | 8.4938
401 | 3247.4871 | 10.5885 | 13.6185 | 2308.1281 | 7.5257 | 9.6793
402 | 3252.141 | 10.6037 | 13.638 | 2590.8336 | 8.4475 | 10.8648
403 | 3256.7781 | 10.6188 | 13.6575 | 3128.9865 | 10.2021 | 13.1216
404 | 3261.3972 | 10.6338 | 13.6768 | 3124.3675 | 10.187 | 13.1022
405 | 3265.9978 | 10.6488 | 13.6961 | 3439.0551 | 11.2131 | 14.4219
406 | 3270.5797 | 10.6638 | 13.7154 | 2604.3238 | 8.4914 | 10.9214
407 | 3271.0084 | 10.6652 | 13.7172 | 1773.7456 | 5.7833 | 7.4383
408 | 3269.0569 | 10.6588 | 13.709 | 945.5478 | 3.083 | 3.9652
409 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
410 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
411 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
412 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
413 | 3192.8823 | 10.4104 | 13.3895 | 0 | 0 | 0
414 | 3262.3117 | 10.6368 | 13.6807 | 143.4294 | 0.46765 | 0.60148
415 | 3262.8487 | 10.6386 | 13.6829 | 355.7512 | 1.1599 | 1.4919
416 | 3267.5234 | 10.6538 | 13.7025 | 563.9354 | 1.8387 | 2.3649
417 | 3272.1865 | 10.669 | 13.7221 | 772.1311 | 2.5175 | 3.238
418 | 3276.8374 | 10.6842 | 13.7416 | 980.339 | 3.1964 | 4.1111
419 | 3281.4754 | 10.6993 | 13.761 | 1188.5599 | 3.8753 | 4.9843
420 | 3286.0998 | 10.7144 | 13.7804 | 1396.7943 | 4.5543 | 5.8575
421 | 3290.71 | 10.7294 | 13.7998 | 1605.0429 | 5.2333 | 6.7308
422 | 3295.3053 | 10.7444 | 13.819 | 1813.3064 | 5.9123 | 7.6042
423 | 3299.8853 | 10.7593 | 13.8383 | 1649.0823 | 5.3769 | 6.9155
424 | 3304.45 | 10.7742 | 13.8574 | 2017.0205 | 6.5765 | 8.4585
425 | 3308.9985 | 10.789 | 13.8765 | 2384.975 | 7.7762 | 10.0015
426 | 3313.5297 | 10.8038 | 13.8955 | 2752.9467 | 8.976 | 11.5446
427 | 3318.0429 | 10.8185 | 13.9144 | 2309.4122 | 7.5299 | 9.6846
428 | 3322.539 | 10.8332 | 13.9333 | 1865.8948 | 6.0838 | 7.8247
429 | 3327.0194 | 10.8478 | 13.952 | 1422.3931 | 4.6377 | 5.9649
430 | 3331.4853 | 10.8624 | 13.9708 | 978.9058 | 3.1917 | 4.1051
431 | 3331.8063 | 10.8634 | 13.9721 | 539.5635 | 1.7593 | 2.2627
432 | 3192.8823 | 10.4104 | 13.3895 | 0 | 0 | 0
433 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
434 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
435 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
436 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
437 | 3163.8561 | 10.3158 | 13.2678 | 0 | 0 | 0
438 | 3323.7844 | 10.8372 | 13.9385 | 43.2551 | 0.14103 | 0.18139
439 | 3324.2047 | 10.8386 | 13.9402 | 246.0183 | 0.80215 | 1.0317
440 | 3328.7557 | 10.8535 | 13.9593 | 444.6507 | 1.4498 | 1.8647
441 | 3333.2943 | 10.8683 | 13.9784 | 643.2955 | 2.0975 | 2.6977
442 | 3337.8198 | 10.883 | 13.9973 | 841.9534 | 2.7452 | 3.5308
443 | 3342.3317 | 10.8977 | 14.0163 | 1040.6249 | 3.393 | 4.3639
444 | 3346.8293 | 10.9124 | 14.0351 | 1239.3108 | 4.0408 | 5.1971
445 | 3351.3119 | 10.927 | 14.0539 | 1438.0116 | 4.6887 | 6.0304
446 | 3355.7792 | 10.9416 | 14.0726 | 1342.3191 | 4.3767 | 5.6291
447 | 3360.2312 | 10.9561 | 14.0913 | 1246.6419 | 4.0647 | 5.2279
448 | 3364.6682 | 10.9706 | 14.1099 | 1150.9797 | 3.7528 | 4.8267
449 | 3369.0905 | 10.985 | 14.1285 | 1055.3322 | 3.4409 | 4.4256
450 | 3373.4983 | 10.9993 | 14.147 | 959.6991 | 3.1291 | 4.0246
451 | 3377.892 | 11.0137 | 14.1654 | 864.0803 | 2.8173 | 3.6236
452 | 3382.2718 | 11.0279 | 14.1837 | 768.4753 | 2.5056 | 3.2226
453 | 3386.6377 | 11.0422 | 14.2021 | 1083.3975 | 3.5324 | 4.5433
454 | 3390.9895 | 11.0564 | 14.2203 | 600.1134 | 1.9567 | 2.5166
455 | 3391.2013 | 11.0571 | 14.2212 | 120.9693 | 0.39442 | 0.50729
456 | 3033.2382 | 9.8899 | 12.7201 | 0 | 0 | 0
457 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
458 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
459 | 2736.7563 | 8.9232 | 11.4767 | 0 | 0 | 0
460 | 2919.2067 | 9.5181 | 12.2419 | 0 | 0 | 0
461 | 3101.6571 | 10.113 | 13.007 | 0 | 0 | 0
462 | 3284.1075 | 10.7079 | 13.7721 | 0 | 0 | 0
463 | 3384.5242 | 11.0353 | 14.1932 | 82.0337 | 0.26747 | 0.34401
464 | 3388.9432 | 11.0497 | 14.2117 | 260.0651 | 0.84795 | 1.0906
465 | 3389.2264 | 11.0506 | 14.2129 | 442.2324 | 1.4419 | 1.8545
466 | 3387.1664 | 11.0439 | 14.2043 | 626.7428 | 2.0435 | 2.6283
467 | 3385.123 | 11.0372 | 14.1957 | 811.2366 | 2.645 | 3.402
468 | 3383.0962 | 11.0306 | 14.1872 | 995.7139 | 3.2465 | 4.1756
469 | 3381.0857 | 11.0241 | 14.1788 | 1088.9495 | 3.5505 | 4.5666
470 | 3379.0917 | 11.0176 | 14.1704 | 1090.9436 | 3.557 | 4.5749
471 | 3377.1139 | 11.0111 | 14.1621 | 1549.0474 | 5.0507 | 6.496
472 | 3377.4806 | 11.0123 | 14.1637 | 1731.1311 | 5.6444 | 7.2596
473 | 3381.9567 | 11.0269 | 14.1824 | 1471.2244 | 4.7969 | 6.1697
474 | 3386.4156 | 11.0415 | 14.2011 | 1211.335 | 3.9496 | 5.0798
475 | 3390.8579 | 11.0559 | 14.2197 | 1079.1774 | 3.5187 | 4.5256
476 | 3395.2842 | 11.0704 | 14.2383 | 691.6052 | 2.255 | 2.9003
477 | 3399.6956 | 11.0848 | 14.2568 | 431.7632 | 1.4078 | 1.8106
478 | 3404.0928 | 11.0991 | 14.2753 | 171.9354 | 0.5606 | 0.72102
479 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
480 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
481 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
482 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
483 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
484 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
485 | 3033.2382 | 9.8899 | 12.7201 | 0 | 0 | 0
486 | 3192.8823 | 10.4104 | 13.3895 | 0 | 0 | 0
487 | 3352.5264 | 10.931 | 14.059 | 0 | 0 | 0
488 | 3405.6189 | 11.1041 | 14.2817 | 106.5516 | 0.34741 | 0.44683
489 | 3405.9413 | 11.1051 | 14.283 | 265.8734 | 0.86688 | 1.115
490 | 3403.9746 | 11.0987 | 14.2748 | 427.4842 | 1.3938 | 1.7927
491 | 3402.0239 | 11.0924 | 14.2666 | 589.079 | 1.9207 | 2.4703
492 | 3400.0892 | 11.086 | 14.2585 | 750.6578 | 2.4475 | 3.1479
493 | 3398.1704 | 11.0798 | 14.2504 | 912.2207 | 2.9743 | 3.8254
494 | 3396.2675 | 11.0736 | 14.2424 | 1073.7678 | 3.501 | 4.5029
495 | 3394.3804 | 11.0674 | 14.2345 | 916.0108 | 2.9867 | 3.8413
496 | 3394.7812 | 11.0687 | 14.2362 | 1075.254 | 3.5059 | 4.5091
497 | 3399.2687 | 11.0834 | 14.255 | 1709.3431 | 5.5733 | 7.1682
498 | 3403.7379 | 11.0979 | 14.2738 | 1545.2297 | 5.0382 | 6.48
499 | 3408.1891 | 11.1125 | 14.2924 | 1860.0668 | 6.0648 | 7.8003
500 | 3412.6219 | 11.1269 | 14.311 | 1504.4169 | 4.9052 | 6.3089
501 | 3417.0373 | 11.1413 | 14.3295 | 1148.7845 | 3.7456 | 4.8175
502 | 3421.4364 | 11.1556 | 14.348 | 793.1682 | 2.5861 | 3.3262
503 | 3421.7389 | 11.1566 | 14.3493 | 441.6487 | 1.44 | 1.8521
504 | 3419.7979 | 11.1503 | 14.3411 | 92.3726 | 0.30118 | 0.38737
505 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
506 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
507 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
508 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
509 | 3272.7044 | 10.6707 | 13.7243 | 0 | 0 | 0
510 | 3414.884 | 11.1343 | 14.3205 | 97.2866 | 0.3172 | 0.40798
511 | 3415.2647 | 11.1355 | 14.3221 | 336.3721 | 1.0967 | 1.4106
512 | 3419.7217 | 11.1501 | 14.3408 | 571.3812 | 1.863 | 2.3961
513 | 3420.0886 | 11.1513 | 14.3423 | 810.4805 | 2.6426 | 3.3988
514 | 3418.2245 | 11.1452 | 14.3345 | 1051.8108 | 3.4294 | 4.4108
515 | 3416.3759 | 11.1391 | 14.3268 | 1293.1256 | 4.2163 | 5.4228
516 | 3414.5426 | 11.1332 | 14.3191 | 1534.425 | 5.003 | 6.4347
517 | 3412.7247 | 11.1272 | 14.3114 | 1775.709 | 5.7897 | 7.4465
518 | 3410.9222 | 11.1214 | 14.3039 | 2016.9778 | 6.5764 | 8.4583
519 | 3409.1348 | 11.1155 | 14.2964 | 1859.121 | 6.0617 | 7.7963
520 | 3409.5766 | 11.117 | 14.2982 | 2071.538 | 6.7543 | 8.6871
521 | 3414.0795 | 11.1317 | 14.3171 | 2812.041 | 9.1687 | 11.7924
522 | 3418.5632 | 11.1463 | 14.3359 | 2647.9132 | 8.6336 | 11.1042
523 | 3423.0278 | 11.1608 | 14.3547 | 2962.7368 | 9.66 | 12.4244
524 | 3427.4731 | 11.1753 | 14.3733 | 2639.0034 | 8.6045 | 11.0668
525 | 3431.8994 | 11.1898 | 14.3919 | 3113.5094 | 10.1516 | 13.0567
526 | 3436.3065 | 11.2041 | 14.4103 | 2310.8817 | 7.5347 | 9.6908
527 | 3436.6418 | 11.2052 | 14.4117 | 1512.3258 | 4.931 | 6.342
528 | 3434.7986 | 11.1992 | 14.404 | 715.9484 | 2.3344 | 3.0024
529 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
530 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
531 | 2745.8788 | 8.953 | 11.515 | 0 | 0 | 0
532 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
533 | 3170.076 | 10.3361 | 13.2939 | 0 | 0 | 0
534 | 3375.3327 | 11.0053 | 14.1546 | 0 | 0 | 0
535 | 3431.0453 | 11.187 | 14.3883 | 149.5441 | 0.48759 | 0.62712
536 | 3435.5212 | 11.2016 | 14.407 | 350.325 | 1.1422 | 1.4691
537 | 3435.9303 | 11.2029 | 14.4088 | 555.1726 | 1.8101 | 2.3281
538 | 3434.1587 | 11.1971 | 14.4013 | 762.2009 | 2.4852 | 3.1963
539 | 3432.4021 | 11.1914 | 14.394 | 969.2143 | 3.1601 | 4.0645
540 | 3430.6603 | 11.1857 | 14.3867 | 1176.2127 | 3.8351 | 4.9325
541 | 3428.9334 | 11.1801 | 14.3794 | 1383.1964 | 4.5099 | 5.8005
542 | 3427.2213 | 11.1745 | 14.3722 | 1590.1652 | 5.1848 | 6.6684
543 | 3425.5239 | 11.169 | 14.3651 | 1797.1193 | 5.8595 | 7.5363
544 | 3426.0219 | 11.1706 | 14.3672 | 2001.8781 | 6.5272 | 8.395
545 | 3430.57 | 11.1854 | 14.3863 | 1837.6859 | 5.9918 | 7.7064
546 | 3435.1034 | 11.2002 | 14.4053 | 2152.4406 | 7.0181 | 9.0264
547 | 3439.6218 | 11.2149 | 14.4242 | 2467.2105 | 8.0444 | 10.3464
548 | 3444.1242 | 11.2296 | 14.4431 | 2622.3522 | 8.5502 | 10.997
549 | 3448.6102 | 11.2442 | 14.4619 | 3096.7986 | 10.0972 | 12.9866
550 | 3453.0793 | 11.2588 | 14.4807 | 2294.1089 | 7.48 | 9.6205
551 | 3453.4854 | 11.2601 | 14.4824 | 1495.4822 | 4.876 | 6.2714
552 | 3451.7287 | 11.2544 | 14.475 | 699.0183 | 2.2792 | 2.9314
553 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
554 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
555 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
556 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
557 | 3217.443 | 10.4905 | 13.4925 | 0 | 0 | 0
558 | 3438.4887 | 11.2112 | 14.4195 | 0 | 0 | 0
559 | 3448.6547 | 11.2444 | 14.4621 | 210.8796 | 0.68758 | 0.88434
560 | 3453.2126 | 11.2593 | 14.4812 | 427.3674 | 1.3934 | 1.7922
561 | 3453.7047 | 11.2609 | 14.4833 | 647.9211 | 2.1126 | 2.7171
562 | 3452.0142 | 11.2553 | 14.4762 | 870.6572 | 2.8388 | 3.6511
563 | 3450.3383 | 11.2499 | 14.4692 | 1093.3789 | 3.565 | 4.5851
564 | 3448.6767 | 11.2445 | 14.4622 | 1316.0862 | 4.2911 | 5.5191
565 | 3447.0295 | 11.2391 | 14.4553 | 1538.7791 | 5.0172 | 6.453
566 | 3445.3965 | 11.2338 | 14.4485 | 1761.4577 | 5.7433 | 7.3868
567 | 3443.7778 | 11.2285 | 14.4417 | 1984.1221 | 6.4693 | 8.3205
568 | 3444.3665 | 11.2304 | 14.4441 | 1823.8893 | 5.9468 | 7.6486
569 | 3449.0121 | 11.2456 | 14.4636 | 2106.6031 | 6.8686 | 8.8342
570 | 3453.6445 | 11.2607 | 14.483 | 2389.3302 | 7.7904 | 10.0198
571 | 3458.2628 | 11.2757 | 14.5024 | 2927.5019 | 9.5452 | 12.2766
572 | 3462.8659 | 11.2907 | 14.5217 | 2922.8988 | 9.5302 | 12.2573
573 | 3467.4535 | 11.3057 | 14.541 | 3237.5994 | 10.5562 | 13.5771
574 | 3472.0257 | 11.3206 | 14.5601 | 2402.8778 | 7.8346 | 10.0766
575 | 3472.527 | 11.3222 | 14.5622 | 1572.227 | 5.1263 | 6.5932
576 | 3470.844 | 11.3167 | 14.5552 | 743.7606 | 2.425 | 3.119
577 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
578 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
579 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
580 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
581 | 3192.8823 | 10.4104 | 13.3895 | 0 | 0 | 0
582 | 3405.7411 | 11.1045 | 14.2822 | 0 | 0 | 0
583 | 3468.6394 | 11.3096 | 14.5459 | 149.9606 | 0.48895 | 0.62887
584 | 3473.3183 | 11.3248 | 14.5656 | 358.1405 | 1.1677 | 1.5019
585 | 3477.9904 | 11.34 | 14.5851 | 566.3272 | 1.8465 | 2.3749
586 | 3482.6551 | 11.3552 | 14.6047 | 774.5213 | 2.5253 | 3.248
587 | 3487.3121 | 11.3704 | 14.6242 | 982.7232 | 3.2042 | 4.1211
588 | 3491.9606 | 11.3856 | 14.6437 | 1190.9335 | 3.8831 | 4.9942
589 | 3496.6003 | 11.4007 | 14.6632 | 1399.1526 | 4.562 | 5.8674
590 | 3501.2304 | 11.4158 | 14.6826 | 1607.3813 | 5.2409 | 6.7406
591 | 3505.8508 | 11.4309 | 14.702 | 1443.1168 | 4.7053 | 6.0518
592 | 3510.4615 | 11.4459 | 14.7213 | 1811.009 | 5.9048 | 7.5946
593 | 3515.0619 | 11.4609 | 14.7406 | 2178.9116 | 7.1044 | 9.1374
594 | 3519.6508 | 11.4759 | 14.7598 | 2546.8256 | 8.304 | 10.6803
595 | 3524.2278 | 11.4908 | 14.779 | 2103.2273 | 6.8576 | 8.82
596 | 3528.7938 | 11.5057 | 14.7982 | 1659.64 | 5.4113 | 6.9598
597 | 3533.3503 | 11.5205 | 14.8173 | 1216.0622 | 3.965 | 5.0996
598 | 3537.8988 | 11.5354 | 14.8364 | 772.4924 | 2.5187 | 3.2395
599 | 3538.3447 | 11.5368 | 14.8382 | 333.0251 | 1.0858 | 1.3966
600 | 3192.8823 | 10.4104 | 13.3895 | 0 | 0 | 0
601 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
602 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
603 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
604 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
605 | 3163.8561 | 10.3158 | 13.2678 | 0 | 0 | 0
606 | 3367.0395 | 10.9783 | 14.1199 | 0 | 0 | 0
607 | 3535.4216 | 11.5273 | 14.826 | 34.8014 | 0.11347 | 0.14594
608 | 3540.1005 | 11.5426 | 14.8456 | 233.3059 | 0.7607 | 0.97838
609 | 3544.7738 | 11.5578 | 14.8652 | 431.816 | 1.4079 | 1.8108
610 | 3549.4409 | 11.573 | 14.8848 | 630.3323 | 2.0552 | 2.6433
611 | 3554.101 | 11.5882 | 14.9043 | 828.8556 | 2.7025 | 3.4759
612 | 3558.7536 | 11.6034 | 14.9238 | 1027.3865 | 3.3498 | 4.3084
613 | 3563.3978 | 11.6185 | 14.9433 | 1225.9257 | 3.9971 | 5.141
614 | 3568.0333 | 11.6336 | 14.9627 | 1130.065 | 3.6846 | 4.739
615 | 3572.6601 | 11.6487 | 14.9821 | 1034.213 | 3.3721 | 4.337
616 | 3577.2785 | 11.6638 | 15.0015 | 938.3694 | 3.0596 | 3.9351
617 | 3581.8886 | 11.6788 | 15.0208 | 842.5341 | 2.7471 | 3.5332
618 | 3586.4907 | 11.6938 | 15.0401 | 746.7068 | 2.4346 | 3.1314
619 | 3591.085 | 11.7088 | 15.0594 | 650.8872 | 2.1222 | 2.7295
620 | 3595.6718 | 11.7237 | 15.0786 | 555.0752 | 1.8098 | 2.3277
621 | 3600.251 | 11.7387 | 15.0979 | 869.7842 | 2.8359 | 3.6475
622 | 3604.8223 | 11.7536 | 15.117 | 386.2806 | 1.2595 | 1.6199
623 | 3512.1706 | 11.4515 | 14.7285 | 0 | 0 | 0
624 | 3033.2382 | 9.8899 | 12.7201 | 0 | 0 | 0
625 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
626 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
627 | 2736.7563 | 8.9232 | 11.4767 | 0 | 0 | 0
628 | 2919.2067 | 9.5181 | 12.2419 | 0 | 0 | 0
629 | 3101.6571 | 10.113 | 13.007 | 0 | 0 | 0
630 | 3284.1075 | 10.7079 | 13.7721 | 0 | 0 | 0
631 | 3466.558 | 11.3028 | 14.5372 | 0 | 0 | 0
632 | 3608.3644 | 11.7651 | 15.1319 | 40.644 | 0.13252 | 0.17044
633 | 3608.8739 | 11.7668 | 15.134 | 222.5849 | 0.72574 | 0.93342
634 | 3606.9224 | 11.7604 | 15.1258 | 406.9868 | 1.327 | 1.7067
635 | 3604.9856 | 11.7541 | 15.1177 | 591.374 | 1.9282 | 2.48
636 | 3603.0634 | 11.7478 | 15.1096 | 775.7466 | 2.5293 | 3.2531
637 | 3601.1558 | 11.7416 | 15.1016 | 868.8794 | 2.833 | 3.6437
638 | 3599.2627 | 11.7355 | 15.0937 | 870.7725 | 2.8392 | 3.6516
639 | 3597.3841 | 11.7293 | 15.0858 | 1328.7772 | 4.3325 | 5.5723
640 | 3598.0094 | 11.7314 | 15.0885 | 1510.6023 | 4.9253 | 6.3348
641 | 3602.8035 | 11.747 | 15.1086 | 1250.3777 | 4.0769 | 5.2435
642 | 3607.5854 | 11.7626 | 15.1286 | 990.1651 | 3.2284 | 4.1523
643 | 3612.3561 | 11.7781 | 15.1486 | 857.6792 | 2.7965 | 3.5967
644 | 3617.1158 | 11.7937 | 15.1686 | 469.7735 | 1.5317 | 1.97
645 | 3621.8657 | 11.8091 | 15.1885 | 209.5931 | 0.68338 | 0.87894
646 | 3576.0282 | 11.6597 | 14.9963 | 0 | 0 | 0
647 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
648 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
649 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
650 | 2554.3059 | 8.3284 | 10.7116 | 0 | 0 | 0
651 | 2713.95 | 8.8489 | 11.3811 | 0 | 0 | 0
652 | 2873.5941 | 9.3694 | 12.0506 | 0 | 0 | 0
653 | 3033.2382 | 9.8899 | 12.7201 | 0 | 0 | 0
654 | 3192.8823 | 10.4104 | 13.3895 | 0 | 0 | 0
655 | 3352.5264 | 10.931 | 14.059 | 0 | 0 | 0
656 | 3512.1706 | 11.4515 | 14.7285 | 0 | 0 | 0
657 | 3635.162 | 11.8525 | 15.2443 | 36.6527 | 0.11951 | 0.15371
658 | 3633.226 | 11.8462 | 15.2361 | 198.2328 | 0.64634 | 0.8313
659 | 3631.3044 | 11.8399 | 15.2281 | 359.7985 | 1.1731 | 1.5088
660 | 3629.3973 | 11.8337 | 15.2201 | 521.3498 | 1.6999 | 2.1863
661 | 3627.5044 | 11.8275 | 15.2121 | 682.8867 | 2.2266 | 2.8637
662 | 3625.6259 | 11.8214 | 15.2043 | 844.4094 | 2.7532 | 3.5411
663 | 3623.7616 | 11.8153 | 15.1964 | 686.6296 | 2.2388 | 2.8794
664 | 3624.4788 | 11.8177 | 15.1995 | 845.5564 | 2.7569 | 3.5459
665 | 3629.3901 | 11.8337 | 15.22 | 1479.2216 | 4.823 | 6.2032
666 | 3634.2864 | 11.8496 | 15.2406 | 1314.6812 | 4.2865 | 5.5132
667 | 3639.1674 | 11.8656 | 15.261 | 1629.0885 | 5.3117 | 6.8317
668 | 3644.0326 | 11.8814 | 15.2815 | 1273.0061 | 4.1507 | 5.3384
669 | 3648.8829 | 11.8972 | 15.3018 | 916.9388 | 2.9897 | 3.8452
670 | 3653.7193 | 11.913 | 15.3221 | 560.8854 | 1.8288 | 2.3521
671 | 3654.3441 | 11.915 | 15.3247 | 209.0435 | 0.68159 | 0.87664
672 | 3512.1706 | 11.4515 | 14.7285 | 0 | 0 | 0
| 2182261.1703 |  |  | 640290.5163

## Summer
Summer
| Hot Sink |  |  | Cold Sink
| Condenser Duty | Refrig mass flow rate |  | Condenser Duty | Refrig mass flow rate | Exdest.cond
| Qcond,h | ṁ ref | Condenser | Qcond,c | ṁ ref | Condenser
Total | 1999013.7215 |  | 8382.9743 | 1028260.9548 |  | 4312.069 | 12695.0433
Hours | kW | kg/s | kW | kW | kg/s | kW
1 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
2 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
3 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
4 | 3082.0192 | 10.049 | 12.9246 | 0 | 0 | 0
5 | 3510.0775 | 11.4447 | 14.7197 | 0 | 0 | 0
6 | 3720.8569 | 12.1319 | 15.6036 | 46.0556 | 0.15016 | 0.19314
7 | 3713.486 | 12.1079 | 15.5727 | 310.2613 | 1.0116 | 1.3011
8 | 3706.1516 | 12.084 | 15.542 | 574.4306 | 1.8729 | 2.4089
9 | 3698.8536 | 12.0602 | 15.5113 | 838.5636 | 2.7341 | 3.5166
10 | 3691.5919 | 12.0365 | 15.4809 | 1102.6603 | 3.5952 | 4.6241
11 | 3684.3662 | 12.0129 | 15.4506 | 1366.7209 | 4.4562 | 5.7314
12 | 3677.1765 | 11.9895 | 15.4204 | 1630.7455 | 5.3171 | 6.8386
13 | 3670.0228 | 11.9662 | 15.3904 | 1894.7342 | 6.1778 | 7.9457
14 | 3662.9047 | 11.943 | 15.3606 | 2158.6872 | 7.0384 | 9.0526
15 | 3655.8223 | 11.9199 | 15.3309 | 1994.5463 | 6.5032 | 8.3642
16 | 3648.7755 | 11.8969 | 15.3013 | 2229.8909 | 7.2706 | 9.3512
17 | 3642.5575 | 11.8766 | 15.2753 | 3035.1509 | 9.8962 | 12.7281
18 | 3636.4613 | 11.8567 | 15.2497 | 2870.0238 | 9.3578 | 12.0356
19 | 3630.3986 | 11.837 | 15.2243 | 3218.5331 | 10.4941 | 13.4971
20 | 3624.3693 | 11.8173 | 15.199 | 2882.1158 | 9.3972 | 12.0863
21 | 3618.3733 | 11.7978 | 15.1738 | 3401.7817 | 11.0916 | 14.2656
22 | 3612.4104 | 11.7783 | 15.1488 | 2551.6281 | 8.3196 | 10.7004
23 | 3605.9515 | 11.7573 | 15.1218 | 1701.9705 | 5.5493 | 7.1373
24 | 3599.1741 | 11.7352 | 15.0933 | 852.6315 | 2.78 | 3.5756
25 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
26 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
27 | 2945.0406 | 9.6023 | 12.3502 | 0 | 0 | 0
28 | 3082.0192 | 10.049 | 12.9246 | 0 | 0 | 0
29 | 3400.0054 | 11.0858 | 14.2581 | 0 | 0 | 0
30 | 3565.0445 | 11.6239 | 14.9502 | 55.1051 | 0.17967 | 0.23109
31 | 3558.4792 | 11.6025 | 14.9227 | 281.8146 | 0.91886 | 1.1818
32 | 3551.9478 | 11.5812 | 14.8953 | 508.4903 | 1.6579 | 2.1324
33 | 3545.4499 | 11.56 | 14.868 | 735.1324 | 2.3969 | 3.0828
34 | 3538.9856 | 11.5389 | 14.8409 | 961.7409 | 3.1358 | 4.0331
35 | 3532.5547 | 11.5179 | 14.814 | 1188.316 | 3.8745 | 4.9833
36 | 3526.1572 | 11.4971 | 14.7871 | 1414.8578 | 4.6132 | 5.9333
37 | 3519.7928 | 11.4763 | 14.7604 | 1641.3664 | 5.3517 | 6.8832
38 | 3513.4615 | 11.4557 | 14.7339 | 1867.8419 | 6.0901 | 7.8329
39 | 3507.1632 | 11.4352 | 14.7075 | 2094.2845 | 6.8284 | 8.7825
40 | 3500.8978 | 11.4147 | 14.6812 | 2320.6941 | 7.5667 | 9.732
41 | 3494.9297 | 11.3953 | 14.6562 | 2155.4389 | 7.0278 | 9.039
42 | 3489.6107 | 11.3779 | 14.6339 | 2503.2045 | 8.1617 | 10.4973
43 | 3484.3225 | 11.3607 | 14.6117 | 2850.9393 | 9.2955 | 11.9556
44 | 3479.0651 | 11.3435 | 14.5897 | 3027.42 | 9.8709 | 12.6957
45 | 3473.8383 | 11.3265 | 14.5677 | 3546.3166 | 11.5628 | 14.8717
46 | 3468.6421 | 11.3096 | 14.5459 | 2695.3964 | 8.7884 | 11.3033
47 | 3463.4763 | 11.2927 | 14.5243 | 1844.4457 | 6.0138 | 7.7348
48 | 3458.2526 | 11.2757 | 14.5024 | 993.5529 | 3.2395 | 4.1665
49 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
50 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
51 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
52 | 3082.0192 | 10.049 | 12.9246 | 0 | 0 | 0
53 | 3432.9858 | 11.1933 | 14.3964 | 17.8221 | 0.058109 | 0.074738
54 | 3427.137 | 11.1742 | 14.3719 | 260.7493 | 0.85018 | 1.0935
55 | 3421.3195 | 11.1553 | 14.3475 | 503.6451 | 1.6421 | 2.1121
56 | 3416.3267 | 11.139 | 14.3266 | 745.7164 | 2.4314 | 3.1272
57 | 3411.4516 | 11.1231 | 14.3061 | 987.6699 | 3.2203 | 4.1418
58 | 3406.6057 | 11.1073 | 14.2858 | 1229.5942 | 4.0091 | 5.1564
59 | 3401.7891 | 11.0916 | 14.2656 | 1471.4892 | 4.7978 | 6.1708
60 | 3397.0016 | 11.076 | 14.2455 | 1713.3551 | 5.5864 | 7.185
61 | 3392.2431 | 11.0605 | 14.2256 | 1955.192 | 6.3749 | 8.1992
62 | 3387.5136 | 11.045 | 14.2057 | 2196.9999 | 7.1634 | 9.2132
63 | 3382.8128 | 11.0297 | 14.186 | 2438.7791 | 7.9517 | 10.2272
64 | 3377.2592 | 11.0116 | 14.1627 | 2273.1094 | 7.4115 | 9.5324
65 | 3371.7359 | 10.9936 | 14.1396 | 2586.8346 | 8.4344 | 10.848
66 | 3366.2428 | 10.9757 | 14.1165 | 2900.5297 | 9.4572 | 12.1635
67 | 3360.7797 | 10.9579 | 14.0936 | 3488.1519 | 11.3732 | 14.6278
68 | 3355.3466 | 10.9402 | 14.0708 | 3493.585 | 11.3909 | 14.6505
69 | 3349.9434 | 10.9225 | 14.0482 | 3841.4349 | 12.5251 | 16.1093
70 | 3344.6581 | 10.9053 | 14.026 | 2956.359 | 9.6393 | 12.3977
71 | 3340.1956 | 10.8908 | 14.0073 | 2070.4604 | 6.7508 | 8.6826
72 | 3335.761 | 10.8763 | 13.9887 | 1184.5339 | 3.8622 | 4.9674
73 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
74 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
75 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
76 | 3082.0192 | 10.049 | 12.9246 | 0 | 0 | 0
77 | 3317.2726 | 10.816 | 13.9112 | 107.1932 | 0.34951 | 0.44952
78 | 3312.9881 | 10.802 | 13.8932 | 339.7754 | 1.1078 | 1.4249
79 | 3308.7309 | 10.7882 | 13.8753 | 572.3304 | 1.8661 | 2.4001
80 | 3304.5008 | 10.7744 | 13.8576 | 804.8582 | 2.6243 | 3.3752
81 | 3300.2977 | 10.7607 | 13.84 | 1037.359 | 3.3823 | 4.3502
82 | 3296.1216 | 10.7471 | 13.8225 | 1269.8328 | 4.1403 | 5.3251
83 | 3291.9724 | 10.7335 | 13.8051 | 1502.2798 | 4.8982 | 6.2999
84 | 3287.8499 | 10.7201 | 13.7878 | 1734.7 | 5.656 | 7.2746
85 | 3283.754 | 10.7067 | 13.7706 | 1967.0936 | 6.4137 | 8.2491
86 | 3279.6847 | 10.6935 | 13.7535 | 2199.4606 | 7.1714 | 9.2236
87 | 3275.6419 | 10.6803 | 13.7366 | 2032.2802 | 6.6263 | 8.5225
88 | 3271.6254 | 10.6672 | 13.7197 | 2435.8176 | 7.942 | 10.2147
89 | 3267.6352 | 10.6542 | 13.703 | 2839.3289 | 9.2577 | 11.9069
90 | 3263.6712 | 10.6412 | 13.6864 | 3242.8139 | 10.5732 | 13.5989
91 | 3259.7332 | 10.6284 | 13.6699 | 2775.8878 | 9.0508 | 11.6408
92 | 3255.8213 | 10.6157 | 13.6535 | 2308.9357 | 7.5283 | 9.6826
93 | 3251.9352 | 10.603 | 13.6372 | 1841.9577 | 6.0057 | 7.7244
94 | 3248.0749 | 10.5904 | 13.621 | 1374.954 | 4.4831 | 5.7659
95 | 3244.2404 | 10.5779 | 13.6049 | 907.9245 | 2.9603 | 3.8074
96 | 3240.4314 | 10.5655 | 13.5889 | 184.0344 | 0.60005 | 0.77176
97 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
98 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
99 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
100 | 3082.0192 | 10.049 | 12.9246 | 0 | 0 | 0
101 | 3222.4692 | 10.5069 | 13.5136 | 170.8651 | 0.55711 | 0.71653
102 | 3217.922 | 10.4921 | 13.4945 | 393.3329 | 1.2825 | 1.6495
103 | 3213.4014 | 10.4773 | 13.4756 | 615.7741 | 2.0077 | 2.5823
104 | 3208.9074 | 10.4627 | 13.4567 | 838.1886 | 2.7329 | 3.515
105 | 3204.4398 | 10.4481 | 13.438 | 1060.5767 | 3.458 | 4.4476
106 | 3199.9987 | 10.4336 | 13.4194 | 1282.9384 | 4.183 | 5.3801
107 | 3195.5838 | 10.4192 | 13.4009 | 1505.2738 | 4.908 | 6.3124
108 | 3191.7243 | 10.4067 | 13.3847 | 1727.0539 | 5.6311 | 7.2425
109 | 3188.2422 | 10.3953 | 13.3701 | 1948.4565 | 6.353 | 8.171
110 | 3184.7845 | 10.384 | 13.3556 | 1854.0724 | 6.0452 | 7.7752
111 | 3181.3511 | 10.3728 | 13.3412 | 1759.6639 | 5.7374 | 7.3792
112 | 3177.9418 | 10.3617 | 13.3269 | 1665.2313 | 5.4295 | 6.9832
113 | 3174.5566 | 10.3507 | 13.3127 | 1570.7746 | 5.1215 | 6.5871
114 | 3171.1954 | 10.3397 | 13.2986 | 1476.294 | 4.8135 | 6.1909
115 | 3167.8581 | 10.3288 | 13.2846 | 1381.7894 | 4.5053 | 5.7946
116 | 3164.5446 | 10.318 | 13.2707 | 1287.261 | 4.1971 | 5.3982
117 | 3161.2548 | 10.3073 | 13.2569 | 1632.9974 | 5.3244 | 6.8481
118 | 3157.9887 | 10.2967 | 13.2432 | 1122.5936 | 3.6602 | 4.7077
119 | 3154.3933 | 10.2849 | 13.2281 | 612.5191 | 1.9971 | 2.5686
120 | 3150.2933 | 10.2716 | 13.2109 | 102.9492 | 0.33567 | 0.43172
121 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
122 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
123 | 2935.2564 | 9.5704 | 12.3092 | 0 | 0 | 0
124 | 3130.9402 | 10.2085 | 13.1298 | 0 | 0 | 0
125 | 3132.3349 | 10.213 | 13.1356 | 194.2891 | 0.63348 | 0.81476
126 | 3128.3739 | 10.2001 | 13.119 | 393.9339 | 1.2844 | 1.652
127 | 3124.4374 | 10.1873 | 13.1025 | 593.5541 | 1.9353 | 2.4891
128 | 3120.5253 | 10.1745 | 13.0861 | 793.1499 | 2.5861 | 3.3261
129 | 3116.6377 | 10.1618 | 13.0698 | 992.7213 | 3.2368 | 4.163
130 | 3112.7743 | 10.1492 | 13.0536 | 1192.2685 | 3.8874 | 4.9998
131 | 3108.9351 | 10.1367 | 13.0375 | 1391.7914 | 4.538 | 5.8366
132 | 3105.12 | 10.1243 | 13.0215 | 1591.2903 | 5.1884 | 6.6732
133 | 3101.3289 | 10.1119 | 13.0056 | 1692.9232 | 5.5198 | 7.0994
134 | 3097.5618 | 10.0996 | 12.9898 | 1696.6904 | 5.5321 | 7.1152
135 | 3093.8185 | 10.0874 | 12.9741 | 2189.6431 | 7.1394 | 9.1824
136 | 3090.099 | 10.0753 | 12.9585 | 2389.0463 | 7.7895 | 10.0186
137 | 3086.4032 | 10.0633 | 12.943 | 2118.7849 | 6.9083 | 8.8852
138 | 3082.7309 | 10.0513 | 12.9276 | 1848.4999 | 6.0271 | 7.7518
139 | 3079.435 | 10.0405 | 12.9138 | 1714.8172 | 5.5912 | 7.1912
140 | 3076.6905 | 10.0316 | 12.9023 | 1306.6258 | 4.2603 | 5.4794
141 | 3073.9677 | 10.0227 | 12.8909 | 1035.3913 | 3.3759 | 4.342
142 | 3071.2665 | 10.0139 | 12.8795 | 764.1353 | 2.4915 | 3.2044
143 | 3068.5868 | 10.0052 | 12.8683 | 13.4325 | 0.043797 | 0.05633
144 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
145 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
146 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
147 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
148 | 3057.5869 | 9.9693 | 12.8222 | 24.4323 | 0.079662 | 0.10246
149 | 3055.025 | 9.961 | 12.8114 | 198.2176 | 0.64629 | 0.83124
150 | 3052.484 | 9.9527 | 12.8008 | 371.9818 | 1.2129 | 1.5599
151 | 3049.9639 | 9.9445 | 12.7902 | 545.7252 | 1.7793 | 2.2885
152 | 3047.4646 | 9.9363 | 12.7797 | 719.4478 | 2.3458 | 3.017
153 | 3044.9861 | 9.9282 | 12.7693 | 893.1496 | 2.9121 | 3.7455
154 | 3042.4399 | 9.9199 | 12.7586 | 1066.9191 | 3.4787 | 4.4742
155 | 3039.1213 | 9.9091 | 12.7447 | 1241.461 | 4.0478 | 5.2061
156 | 3035.8248 | 9.8984 | 12.7309 | 1415.9808 | 4.6168 | 5.938
157 | 3032.5503 | 9.8877 | 12.7172 | 1590.4785 | 5.1858 | 6.6698
158 | 3029.2979 | 9.8771 | 12.7035 | 1764.9543 | 5.7547 | 7.4014
159 | 3026.0674 | 9.8665 | 12.69 | 1596.9615 | 5.2069 | 6.6969
160 | 3022.8587 | 9.8561 | 12.6765 | 1771.3934 | 5.7757 | 7.4284
161 | 3019.6718 | 9.8457 | 12.6632 | 2459.4735 | 8.0192 | 10.3139
162 | 3016.5066 | 9.8354 | 12.6499 | 2291.4154 | 7.4712 | 9.6092
163 | 3013.363 | 9.8251 | 12.6367 | 2637.0056 | 8.598 | 11.0584
164 | 3010.2409 | 9.8149 | 12.6236 | 2263.4365 | 7.38 | 9.4918
165 | 3007.1403 | 9.8048 | 12.6106 | 1889.8459 | 6.1619 | 7.9252
166 | 3004.3256 | 9.7956 | 12.5988 | 1515.9693 | 4.9428 | 6.3573
167 | 3002.1486 | 9.7886 | 12.5897 | 1141.4551 | 3.7217 | 4.7868
168 | 2999.9911 | 9.7815 | 12.5806 | 766.9213 | 2.5006 | 3.2161
169 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
170 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
171 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
172 | 2992.3725 | 9.7567 | 12.5487 | 89.6468 | 0.29229 | 0.37594
173 | 2990.3078 | 9.7499 | 12.54 | 519.7696 | 1.6947 | 2.1797
174 | 2988.2623 | 9.7433 | 12.5314 | 778.6501 | 2.5388 | 3.2653
175 | 2986.2358 | 9.7367 | 12.5229 | 1037.5116 | 3.3828 | 4.3509
176 | 2984.2282 | 9.7301 | 12.5145 | 1296.3541 | 4.2268 | 5.4363
177 | 2982.2395 | 9.7236 | 12.5062 | 1555.1777 | 5.0707 | 6.5217
178 | 2980.2696 | 9.7172 | 12.4979 | 1813.9826 | 5.9145 | 7.607
179 | 2978.3184 | 9.7109 | 12.4897 | 2072.7687 | 6.7583 | 8.6923
180 | 2976.3859 | 9.7046 | 12.4816 | 2331.5362 | 7.602 | 9.7774
181 | 2974.472 | 9.6983 | 12.4736 | 2590.285 | 8.4457 | 10.8625
182 | 2972.5765 | 9.6921 | 12.4657 | 2849.0154 | 9.2893 | 11.9475
183 | 2970.6995 | 9.686 | 12.4578 | 2679.6691 | 8.7371 | 11.2373
184 | 2968.8409 | 9.68 | 12.45 | 2909.8254 | 9.4875 | 12.2025
185 | 2967.0006 | 9.674 | 12.4423 | 3710.7078 | 12.0988 | 15.5611
186 | 2965.1784 | 9.668 | 12.4346 | 3541.3066 | 11.5465 | 14.8507
187 | 2963.3745 | 9.6621 | 12.4271 | 3885.5572 | 12.6689 | 16.2943
188 | 2961.5886 | 9.6563 | 12.4196 | 3544.8965 | 11.5582 | 14.8657
189 | 2959.8207 | 9.6505 | 12.4122 | 4060.3343 | 13.2388 | 17.0272
190 | 2958.0707 | 9.6448 | 12.4048 | 3205.9678 | 10.4531 | 13.4444
191 | 2956.3386 | 9.6392 | 12.3976 | 2351.5835 | 7.6674 | 9.8615
192 | 2954.6243 | 9.6336 | 12.3904 | 1497.1813 | 4.8816 | 6.2785
193 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
194 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
195 | 2945.0406 | 9.6023 | 12.3502 | 0 | 0 | 0
196 | 2948.4698 | 9.6135 | 12.3646 | 133.5494 | 0.43544 | 0.56005
197 | 2946.8409 | 9.6082 | 12.3577 | 453.1644 | 1.4775 | 1.9004
198 | 2945.2295 | 9.603 | 12.351 | 674.9201 | 2.2006 | 2.8303
199 | 2943.6353 | 9.5978 | 12.3443 | 896.6585 | 2.9236 | 3.7602
200 | 2942.0584 | 9.5926 | 12.3377 | 1118.3797 | 3.6465 | 4.69
201 | 2940.4986 | 9.5875 | 12.3311 | 1340.0837 | 4.3694 | 5.6197
202 | 2938.9559 | 9.5825 | 12.3247 | 1561.7706 | 5.0922 | 6.5494
203 | 2937.4303 | 9.5775 | 12.3183 | 1783.4404 | 5.8149 | 7.479
204 | 2935.9216 | 9.5726 | 12.3119 | 2005.0933 | 6.5376 | 8.4085
205 | 2934.4299 | 9.5678 | 12.3057 | 2226.7294 | 7.2603 | 9.3379
206 | 2932.9549 | 9.5629 | 12.2995 | 2448.3485 | 7.9829 | 10.2673
207 | 2931.4967 | 9.5582 | 12.2934 | 2669.951 | 8.7054 | 11.1966
208 | 2930.0552 | 9.5535 | 12.2873 | 2891.5367 | 9.4279 | 12.1258
209 | 2928.6303 | 9.5488 | 12.2814 | 2721.7383 | 8.8743 | 11.4138
210 | 2927.222 | 9.5443 | 12.2755 | 3065.5932 | 9.9954 | 12.8557
211 | 2925.8302 | 9.5397 | 12.2696 | 3409.4316 | 11.1165 | 14.2976
212 | 2924.4548 | 9.5352 | 12.2639 | 3582.0303 | 11.6793 | 15.0214
213 | 2923.0957 | 9.5308 | 12.2582 | 4097.0593 | 13.3585 | 17.1812
214 | 2921.7529 | 9.5264 | 12.2525 | 3242.2856 | 10.5715 | 13.5967
215 | 2920.4264 | 9.5221 | 12.247 | 2387.4957 | 7.7845 | 10.0121
216 | 2919.116 | 9.5178 | 12.2415 | 1532.6896 | 4.9974 | 6.4274
217 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
218 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
219 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
220 | 2914.4433 | 9.5026 | 12.2219 | 167.576 | 0.54638 | 0.70274
221 | 2913.2108 | 9.4986 | 12.2167 | 537.5971 | 1.7528 | 2.2544
222 | 2911.9941 | 9.4946 | 12.2116 | 775.8922 | 2.5298 | 3.2537
223 | 2910.7931 | 9.4907 | 12.2066 | 1014.1716 | 3.3067 | 4.253
224 | 2909.6078 | 9.4868 | 12.2016 | 1252.4353 | 4.0836 | 5.2522
225 | 2908.438 | 9.483 | 12.1967 | 1490.6835 | 4.8604 | 6.2513
226 | 2907.2837 | 9.4792 | 12.1919 | 1728.9162 | 5.6372 | 7.2503
227 | 2906.1449 | 9.4755 | 12.1871 | 1967.1334 | 6.4139 | 8.2493
228 | 2905.0215 | 9.4719 | 12.1824 | 2205.3352 | 7.1905 | 9.2482
229 | 2903.9134 | 9.4683 | 12.1777 | 2443.5217 | 7.9671 | 10.247
230 | 2902.8206 | 9.4647 | 12.1731 | 2681.693 | 8.7437 | 11.2458
231 | 2901.7429 | 9.4612 | 12.1686 | 2919.849 | 9.5202 | 12.2445
232 | 2900.6804 | 9.4577 | 12.1642 | 2749.6882 | 8.9654 | 11.531
233 | 2899.633 | 9.4543 | 12.1598 | 3058.9376 | 9.9737 | 12.8278
234 | 2898.6005 | 9.4509 | 12.1554 | 3368.1719 | 10.982 | 14.1246
235 | 2897.5831 | 9.4476 | 12.1512 | 3951.3486 | 12.8834 | 16.5702
236 | 2896.5805 | 9.4443 | 12.147 | 3952.3512 | 12.8867 | 16.5744
237 | 2895.5927 | 9.4411 | 12.1428 | 4295.7856 | 14.0065 | 18.0146
238 | 2894.6197 | 9.438 | 12.1387 | 3406.3975 | 11.1066 | 14.2849
239 | 2893.6613 | 9.4348 | 12.1347 | 2516.9947 | 8.2067 | 10.5552
240 | 2892.7177 | 9.4317 | 12.1308 | 1627.5772 | 5.3067 | 6.8253
241 | 2891.7886 | 9.4287 | 12.1269 | 19.0074 | 0.061974 | 0.079709
242 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
243 | 2888.5091 | 9.418 | 12.1131 | 22.2869 | 0.072667 | 0.093461
244 | 2886.7438 | 9.4123 | 12.1057 | 195.2755 | 0.6367 | 0.8189
245 | 2884.9945 | 9.4066 | 12.0984 | 539.4713 | 1.759 | 2.2623
246 | 2883.2612 | 9.4009 | 12.0911 | 769.5024 | 2.509 | 3.227
247 | 2881.5437 | 9.3953 | 12.0839 | 999.5175 | 3.2589 | 4.1915
248 | 2879.8421 | 9.3898 | 12.0768 | 1229.5169 | 4.0089 | 5.156
249 | 2878.1562 | 9.3843 | 12.0697 | 1459.5005 | 4.7587 | 6.1205
250 | 2876.486 | 9.3788 | 12.0627 | 1689.4684 | 5.5085 | 7.0849
251 | 2874.8315 | 9.3734 | 12.0558 | 1919.4207 | 6.2583 | 8.0492
252 | 2873.1925 | 9.3681 | 12.0489 | 2149.3574 | 7.008 | 9.0134
253 | 2871.569 | 9.3628 | 12.0421 | 2379.2786 | 7.7577 | 9.9776
254 | 2869.961 | 9.3576 | 12.0353 | 2609.1843 | 8.5073 | 10.9418
255 | 2868.3684 | 9.3524 | 12.0287 | 2439.5537 | 7.9542 | 10.2304
256 | 2866.7911 | 9.3472 | 12.022 | 2840.652 | 9.262 | 11.9124
257 | 2865.229 | 9.3421 | 12.0155 | 3241.735 | 10.5697 | 13.5944
258 | 2863.6822 | 9.3371 | 12.009 | 3642.8029 | 11.8774 | 15.2763
259 | 2862.1505 | 9.3321 | 12.0026 | 3173.4705 | 10.3471 | 13.3081
260 | 2860.6339 | 9.3271 | 11.9962 | 2704.123 | 8.8168 | 11.3399
261 | 2859.1324 | 9.3222 | 11.9899 | 2234.7606 | 7.2865 | 9.3716
262 | 2857.6458 | 9.3174 | 11.9837 | 1765.3831 | 5.7561 | 7.4032
263 | 2856.1741 | 9.3126 | 11.9775 | 1295.9907 | 4.2256 | 5.4348
264 | 2854.7172 | 9.3078 | 11.9714 | 569.7486 | 1.8577 | 2.3893
265 | 2853.2752 | 9.3031 | 11.9654 | 57.5208 | 0.18755 | 0.24122
266 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
267 | 2850.6004 | 9.2944 | 11.9542 | 60.1955 | 0.19627 | 0.25243
268 | 2849.2017 | 9.2899 | 11.9483 | 232.8176 | 0.75911 | 0.97633
269 | 2847.8174 | 9.2854 | 11.9425 | 545.5169 | 1.7787 | 2.2877
270 | 2846.4477 | 9.2809 | 11.9367 | 764.8072 | 2.4937 | 3.2073
271 | 2845.0924 | 9.2765 | 11.9311 | 984.083 | 3.2086 | 4.1268
272 | 2843.7516 | 9.2721 | 11.9254 | 1203.3444 | 3.9235 | 5.0463
273 | 2842.425 | 9.2678 | 11.9199 | 1422.5915 | 4.6384 | 5.9657
274 | 2841.1127 | 9.2635 | 11.9144 | 1641.8244 | 5.3532 | 6.8851
275 | 2839.8146 | 9.2593 | 11.9089 | 1861.043 | 6.068 | 7.8044
276 | 2838.5307 | 9.2551 | 11.9035 | 2080.2475 | 6.7827 | 8.7236
277 | 2837.2609 | 9.2509 | 11.8982 | 2299.4378 | 7.4974 | 9.6428
278 | 2836.0051 | 9.2468 | 11.8929 | 2202.8517 | 7.1824 | 9.2378
279 | 2834.7634 | 9.2428 | 11.8877 | 2106.2516 | 6.8675 | 8.8327
280 | 2833.5355 | 9.2388 | 11.8826 | 2009.6376 | 6.5525 | 8.4275
281 | 2832.3215 | 9.2348 | 11.8775 | 1913.0097 | 6.2374 | 8.0223
282 | 2831.1214 | 9.2309 | 11.8725 | 1816.368 | 5.9223 | 7.617
283 | 2829.935 | 9.227 | 11.8675 | 1719.7125 | 5.6071 | 7.2117
284 | 2828.7623 | 9.2232 | 11.8626 | 1623.0433 | 5.292 | 6.8063
285 | 2827.6033 | 9.2194 | 11.8577 | 1966.6489 | 6.4123 | 8.2473
286 | 2826.4579 | 9.2157 | 11.8529 | 1454.1244 | 4.7412 | 6.098
287 | 2825.326 | 9.212 | 11.8482 | 941.5864 | 3.0701 | 3.9486
288 | 2824.2076 | 9.2084 | 11.8435 | 429.035 | 1.3989 | 1.7992
289 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
290 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
291 | 2821.1725 | 9.1985 | 11.8307 | 114.084 | 0.37197 | 0.47842
292 | 2820.1064 | 9.195 | 11.8263 | 310.8338 | 1.0135 | 1.3035
293 | 2819.0535 | 9.1916 | 11.8219 | 507.5705 | 1.6549 | 2.1285
294 | 2818.0138 | 9.1882 | 11.8175 | 704.2939 | 2.2964 | 2.9535
295 | 2816.9872 | 9.1848 | 11.8132 | 901.0043 | 2.9377 | 3.7784
296 | 2816.4146 | 9.183 | 11.8108 | 1097.2606 | 3.5776 | 4.6014
297 | 2816.2947 | 9.1826 | 11.8103 | 1293.0643 | 4.2161 | 5.4225
298 | 2816.1861 | 9.1822 | 11.8098 | 1488.8566 | 4.8544 | 6.2436
299 | 2816.0888 | 9.1819 | 11.8094 | 1684.6377 | 5.4928 | 7.0646
300 | 2816.0026 | 9.1816 | 11.8091 | 1880.4077 | 6.1311 | 7.8856
301 | 2815.9276 | 9.1814 | 11.8087 | 1978.3246 | 6.4504 | 8.2962
302 | 2815.8636 | 9.1812 | 11.8085 | 1978.3886 | 6.4506 | 8.2965
303 | 2815.8107 | 9.181 | 11.8083 | 2467.6509 | 8.0458 | 10.3482
304 | 2815.7687 | 9.1809 | 11.8081 | 2663.3766 | 8.684 | 11.169
305 | 2815.7377 | 9.1808 | 11.808 | 2389.4504 | 7.7908 | 10.0203
306 | 2815.7175 | 9.1807 | 11.8079 | 2115.5133 | 6.8977 | 8.8715
307 | 2815.7082 | 9.1807 | 11.8078 | 1978.5439 | 6.4511 | 8.2971
308 | 2815.7097 | 9.1807 | 11.8078 | 1567.6066 | 5.1112 | 6.5738
309 | 2815.7219 | 9.1807 | 11.8079 | 1293.6371 | 4.2179 | 5.4249
310 | 2815.7447 | 9.1808 | 11.808 | 1019.657 | 3.3246 | 4.276
311 | 2815.7782 | 9.1809 | 11.8081 | 266.241 | 0.86808 | 1.1165
312 | 2815.8223 | 9.181 | 11.8083 | 94.9736 | 0.30966 | 0.39828
313 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
314 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
315 | 2816.2648 | 9.1825 | 11.8102 | 94.5311 | 0.30822 | 0.39642
316 | 2816.3496 | 9.1828 | 11.8105 | 265.6696 | 0.86622 | 1.1141
317 | 2816.4447 | 9.1831 | 11.8109 | 436.7978 | 1.4242 | 1.8317
318 | 2816.5502 | 9.1834 | 11.8114 | 607.9157 | 1.9821 | 2.5493
319 | 2816.6658 | 9.1838 | 11.8118 | 779.0233 | 2.54 | 3.2669
320 | 2816.7917 | 9.1842 | 11.8124 | 950.1207 | 3.0979 | 3.9844
321 | 2816.9278 | 9.1846 | 11.8129 | 1121.208 | 3.6557 | 4.7018
322 | 2817.0739 | 9.1851 | 11.8136 | 1292.2851 | 4.2135 | 5.4193
323 | 2817.2301 | 9.1856 | 11.8142 | 1463.3522 | 4.7713 | 6.1366
324 | 2817.3963 | 9.1862 | 11.8149 | 1634.4093 | 5.329 | 6.854
325 | 2817.5725 | 9.1867 | 11.8156 | 1805.4564 | 5.8867 | 7.5713
326 | 2817.7585 | 9.1873 | 11.8164 | 1976.4936 | 6.4444 | 8.2885
327 | 2817.9545 | 9.188 | 11.8172 | 1805.0744 | 5.8855 | 7.5697
328 | 2818.1603 | 9.1887 | 11.8181 | 1976.0919 | 6.4431 | 8.2869
329 | 2818.3758 | 9.1894 | 11.819 | 2660.7695 | 8.6755 | 11.1581
330 | 2818.6011 | 9.1901 | 11.82 | 2489.3209 | 8.1165 | 10.4391
331 | 2818.8361 | 9.1909 | 11.8209 | 2831.5325 | 9.2323 | 11.8742
332 | 2819.0807 | 9.1917 | 11.822 | 2454.5967 | 8.0032 | 10.2935
333 | 2819.3349 | 9.1925 | 11.823 | 2077.6512 | 6.7742 | 8.7127
334 | 2819.5987 | 9.1933 | 11.8241 | 1700.6962 | 5.5451 | 7.132
335 | 2819.8719 | 9.1942 | 11.8253 | 1323.7317 | 4.316 | 5.5511
336 | 2820.1547 | 9.1952 | 11.8265 | 946.7578 | 3.0869 | 3.9703
337 | 2820.4468 | 9.1961 | 11.8277 | 90.3492 | 0.29458 | 0.37888
338 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
339 | 2821.1453 | 9.1984 | 11.8306 | 89.6507 | 0.29231 | 0.37596
340 | 2821.465 | 9.1994 | 11.832 | 260.5543 | 0.84954 | 1.0926
341 | 2821.7939 | 9.2005 | 11.8333 | 688.2836 | 2.2442 | 2.8864
342 | 2822.1321 | 9.2016 | 11.8348 | 944.7804 | 3.0805 | 3.962
343 | 2822.4793 | 9.2027 | 11.8362 | 1201.268 | 3.9168 | 5.0376
344 | 2822.8357 | 9.2039 | 11.8377 | 1457.7466 | 4.753 | 6.1131
345 | 2823.2011 | 9.2051 | 11.8392 | 1714.2161 | 5.5892 | 7.1887
346 | 2823.5756 | 9.2063 | 11.8408 | 1970.6766 | 6.4254 | 8.2641
347 | 2823.959 | 9.2076 | 11.8424 | 2227.1281 | 7.2616 | 9.3396
348 | 2824.3513 | 9.2088 | 11.8441 | 2483.5707 | 8.0977 | 10.415
349 | 2824.7525 | 9.2101 | 11.8458 | 2740.0044 | 8.9338 | 11.4904
350 | 2825.1626 | 9.2115 | 11.8475 | 2996.4293 | 9.7699 | 12.5657
351 | 2825.5815 | 9.2129 | 11.8492 | 2824.7872 | 9.2103 | 11.8459
352 | 2826.0091 | 9.2142 | 11.851 | 3052.6573 | 9.9532 | 12.8015
353 | 2826.4454 | 9.2157 | 11.8529 | 3851.263 | 12.5571 | 16.1505
354 | 2826.8904 | 9.2171 | 11.8547 | 3679.5947 | 11.9974 | 15.4306
355 | 2827.344 | 9.2186 | 11.8566 | 4021.5877 | 13.1124 | 16.8647
356 | 2827.8062 | 9.2201 | 11.8586 | 3678.6789 | 11.9944 | 15.4267
357 | 2828.2769 | 9.2216 | 11.8605 | 4191.878 | 13.6677 | 17.5789
358 | 2828.7562 | 9.2232 | 11.8625 | 3335.2823 | 10.8747 | 13.9867
359 | 2829.2439 | 9.2248 | 11.8646 | 2478.6782 | 8.0818 | 10.3945
360 | 2829.74 | 9.2264 | 11.8667 | 1622.0656 | 5.2888 | 6.8022
361 | 2830.2445 | 9.2281 | 11.8688 | 80.5515 | 0.26264 | 0.3378
362 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
363 | 2831.3782 | 9.2318 | 11.8735 | 113.6624 | 0.3706 | 0.47665
364 | 2831.9071 | 9.2335 | 11.8758 | 250.1122 | 0.81549 | 1.0489
365 | 2832.4442 | 9.2352 | 11.878 | 567.5612 | 1.8505 | 2.3801
366 | 2832.9895 | 9.237 | 11.8803 | 787.1601 | 2.5665 | 3.301
367 | 2833.5429 | 9.2388 | 11.8826 | 1006.751 | 3.2825 | 4.2219
368 | 2834.1044 | 9.2406 | 11.885 | 1226.3337 | 3.9985 | 5.1427
369 | 2834.6739 | 9.2425 | 11.8874 | 1445.9084 | 4.7144 | 6.0635
370 | 2835.2514 | 9.2444 | 11.8898 | 1665.4751 | 5.4303 | 6.9843
371 | 2835.8369 | 9.2463 | 11.8922 | 1885.0338 | 6.1462 | 7.905
372 | 2836.4304 | 9.2482 | 11.8947 | 2104.5846 | 6.862 | 8.8257
373 | 2837.0317 | 9.2502 | 11.8972 | 2324.1275 | 7.5779 | 9.7464
374 | 2837.6408 | 9.2522 | 11.8998 | 2543.6626 | 8.2937 | 10.667
375 | 2838.2578 | 9.2542 | 11.9024 | 2763.1899 | 9.0094 | 11.5876
376 | 2838.8825 | 9.2562 | 11.905 | 2982.7094 | 9.7252 | 12.5082
377 | 2839.515 | 9.2583 | 11.9077 | 2810.8536 | 9.1648 | 11.7875
378 | 2840.1551 | 9.2604 | 11.9103 | 3152.6601 | 10.2793 | 13.2209
379 | 2840.8029 | 9.2625 | 11.9131 | 3494.4589 | 11.3937 | 14.6542
380 | 2841.4583 | 9.2646 | 11.9158 | 3665.0267 | 11.9499 | 15.3695
381 | 2842.1213 | 9.2668 | 11.9186 | 4178.0337 | 13.6225 | 17.5208
382 | 2842.7918 | 9.269 | 11.9214 | 3321.2467 | 10.829 | 13.9278
383 | 2843.4698 | 9.2712 | 11.9242 | 2464.4523 | 8.0354 | 10.3348
384 | 2844.1552 | 9.2734 | 11.9271 | 1607.6504 | 5.2418 | 6.7418
385 | 2844.8481 | 9.2757 | 11.93 | 65.9479 | 0.21502 | 0.27656
386 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
387 | 2846.4029 | 9.2807 | 11.9365 | 64.393 | 0.20995 | 0.27004
388 | 2847.1171 | 9.2831 | 11.9395 | 234.9021 | 0.7659 | 0.98507
389 | 2847.8386 | 9.2854 | 11.9426 | 602.9693 | 1.966 | 2.5286
390 | 2848.5673 | 9.2878 | 11.9456 | 839.319 | 2.7366 | 3.5197
391 | 2849.3031 | 9.2902 | 11.9487 | 1075.6615 | 3.5072 | 4.5108
392 | 2850.0462 | 9.2926 | 11.9518 | 1311.9969 | 4.2778 | 5.5019
393 | 2850.7963 | 9.2951 | 11.955 | 1548.3252 | 5.0483 | 6.493
394 | 2851.5535 | 9.2975 | 11.9581 | 1784.6464 | 5.8189 | 7.484
395 | 2852.3178 | 9.3 | 11.9614 | 2020.9605 | 6.5894 | 8.475
396 | 2853.089 | 9.3025 | 11.9646 | 2257.2677 | 7.3599 | 9.466
397 | 2853.8672 | 9.3051 | 11.9678 | 2493.5679 | 8.1303 | 10.4569
398 | 2854.0351 | 9.3056 | 11.9686 | 2730.4784 | 8.9028 | 11.4504
399 | 2853.9468 | 9.3053 | 11.9682 | 2967.6451 | 9.6761 | 12.445
400 | 2853.867 | 9.3051 | 11.9678 | 2796.5016 | 9.118 | 11.7273
401 | 2853.7957 | 9.3048 | 11.9675 | 3104.7748 | 10.1232 | 13.02
402 | 2853.7329 | 9.3046 | 11.9673 | 3413.0396 | 11.1283 | 14.3128
403 | 2853.6784 | 9.3045 | 11.9671 | 3995.2533 | 13.0266 | 16.7543
404 | 2853.6323 | 9.3043 | 11.9669 | 3995.2993 | 13.0267 | 16.7545
405 | 2853.5946 | 9.3042 | 11.9667 | 4337.7837 | 14.1434 | 18.1907
406 | 2853.5651 | 9.3041 | 11.9666 | 3447.452 | 11.2405 | 14.4571
407 | 2853.5439 | 9.304 | 11.9665 | 2557.1121 | 8.3375 | 10.7234
408 | 2853.5309 | 9.304 | 11.9664 | 1666.764 | 5.4345 | 6.9897
409 | 2853.5261 | 9.304 | 11.9664 | 57.2698 | 0.18673 | 0.24016
410 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
411 | 2853.711 | 9.3046 | 11.9672 | 57.085 | 0.18613 | 0.23939
412 | 2853.7297 | 9.3046 | 11.9673 | 228.2895 | 0.74434 | 0.95734
413 | 2853.7565 | 9.3047 | 11.9674 | 570.7094 | 1.8608 | 2.3933
414 | 2853.7912 | 9.3048 | 11.9675 | 798.9723 | 2.6051 | 3.3505
415 | 2853.8339 | 9.305 | 11.9677 | 1027.2274 | 3.3493 | 4.3077
416 | 2853.8846 | 9.3051 | 11.9679 | 1255.4744 | 4.0935 | 5.2649
417 | 2853.9431 | 9.3053 | 11.9682 | 1483.7137 | 4.8377 | 6.222
418 | 2854.0094 | 9.3055 | 11.9684 | 1711.945 | 5.5818 | 7.1791
419 | 2854.0836 | 9.3058 | 11.9688 | 1940.1686 | 6.3259 | 8.1362
420 | 2854.1656 | 9.3061 | 11.9691 | 2168.3843 | 7.07 | 9.0932
421 | 2854.2553 | 9.3063 | 11.9695 | 2396.5924 | 7.8141 | 10.0502
422 | 2854.3527 | 9.3067 | 11.9699 | 2624.7927 | 8.5582 | 11.0072
423 | 2854.4577 | 9.307 | 11.9703 | 2453.4643 | 7.9996 | 10.2887
424 | 2854.5704 | 9.3074 | 11.9708 | 2852.8726 | 9.3018 | 11.9637
425 | 2854.6907 | 9.3078 | 11.9713 | 3252.2734 | 10.6041 | 13.6386
426 | 2854.8186 | 9.3082 | 11.9718 | 3651.6665 | 11.9063 | 15.3135
427 | 2854.954 | 9.3086 | 11.9724 | 3180.6671 | 10.3706 | 13.3383
428 | 2855.0968 | 9.3091 | 11.973 | 2709.6602 | 8.8349 | 11.3631
429 | 2855.2472 | 9.3096 | 11.9736 | 2238.6458 | 7.2991 | 9.3879
430 | 2855.4049 | 9.3101 | 11.9743 | 1767.624 | 5.7634 | 7.4126
431 | 2855.57 | 9.3106 | 11.975 | 1296.5948 | 4.2276 | 5.4373
432 | 2855.7425 | 9.3112 | 11.9757 | 568.7233 | 1.8543 | 2.385
433 | 2855.9223 | 9.3118 | 11.9765 | 54.8737 | 0.17892 | 0.23012
434 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
435 | 2856.4816 | 9.3136 | 11.9788 | 54.3144 | 0.17709 | 0.22777
436 | 2856.6823 | 9.3143 | 11.9797 | 225.337 | 0.73471 | 0.94496
437 | 2856.8902 | 9.3149 | 11.9805 | 536.4442 | 1.7491 | 2.2496
438 | 2857.1052 | 9.3156 | 11.9814 | 754.1497 | 2.4589 | 3.1626
439 | 2857.3274 | 9.3164 | 11.9824 | 971.8481 | 3.1687 | 4.0755
440 | 2857.5566 | 9.3171 | 11.9833 | 1189.5394 | 3.8785 | 4.9884
441 | 2857.7929 | 9.3179 | 11.9843 | 1407.2237 | 4.5883 | 5.9013
442 | 2858.0361 | 9.3187 | 11.9853 | 1624.901 | 5.298 | 6.8141
443 | 2858.2864 | 9.3195 | 11.9864 | 1842.5712 | 6.0077 | 7.7269
444 | 2858.5436 | 9.3203 | 11.9875 | 2060.2346 | 6.7174 | 8.6397
445 | 2858.8077 | 9.3212 | 11.9886 | 2277.891 | 7.4271 | 9.5525
446 | 2859.0787 | 9.3221 | 11.9897 | 2179.7782 | 7.1072 | 9.141
447 | 2859.3565 | 9.323 | 11.9909 | 2081.6585 | 6.7873 | 8.7295
448 | 2859.6412 | 9.3239 | 11.9921 | 1983.532 | 6.4673 | 8.3181
449 | 2859.9326 | 9.3249 | 11.9933 | 1885.3987 | 6.1474 | 7.9065
450 | 2860.2307 | 9.3258 | 11.9945 | 1787.2586 | 5.8274 | 7.495
451 | 2860.5356 | 9.3268 | 11.9958 | 1689.1119 | 5.5074 | 7.0834
452 | 2860.8471 | 9.3278 | 11.9971 | 1590.9585 | 5.1873 | 6.6718
453 | 2861.1653 | 9.3289 | 11.9985 | 1933.0869 | 6.3029 | 8.1065
454 | 2861.4901 | 9.3299 | 11.9998 | 1419.0922 | 4.627 | 5.951
455 | 2861.8215 | 9.331 | 12.0012 | 905.0909 | 2.9511 | 3.7955
456 | 2862.1594 | 9.3321 | 12.0026 | 391.0831 | 1.2751 | 1.64
457 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
458 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
459 | 2863.6082 | 9.3368 | 12.0087 | 71.6482 | 0.23361 | 0.30046
460 | 2863.9702 | 9.338 | 12.0102 | 266.97 | 0.87046 | 1.1196
461 | 2864.3386 | 9.3392 | 12.0118 | 462.2854 | 1.5073 | 1.9386
462 | 2864.7133 | 9.3404 | 12.0133 | 657.5944 | 2.1441 | 2.7577
463 | 2865.0944 | 9.3417 | 12.0149 | 852.8971 | 2.7809 | 3.5767
464 | 2865.4817 | 9.3429 | 12.0166 | 1048.1935 | 3.4177 | 4.3957
465 | 2865.8754 | 9.3442 | 12.0182 | 1243.4836 | 4.0544 | 5.2146
466 | 2866.2752 | 9.3455 | 12.0199 | 1438.7675 | 4.6911 | 6.0336
467 | 2866.6813 | 9.3469 | 12.0216 | 1634.0452 | 5.3278 | 6.8525
468 | 2867.0936 | 9.3482 | 12.0233 | 1829.3167 | 5.9645 | 7.6713
469 | 2867.512 | 9.3496 | 12.0251 | 1926.7402 | 6.2822 | 8.0799
470 | 2867.9365 | 9.351 | 12.0268 | 1926.3157 | 6.2808 | 8.0781
471 | 2868.3671 | 9.3524 | 12.0287 | 2415.0945 | 7.8745 | 10.1278
472 | 2868.8037 | 9.3538 | 12.0305 | 2610.3416 | 8.5111 | 10.9466
473 | 2869.2464 | 9.3552 | 12.0323 | 2335.9417 | 7.6164 | 9.7959
474 | 2869.695 | 9.3567 | 12.0342 | 2061.5358 | 6.7217 | 8.6452
475 | 2870.1496 | 9.3582 | 12.0361 | 1924.1025 | 6.2736 | 8.0688
476 | 2870.6102 | 9.3597 | 12.0381 | 1512.7061 | 4.9322 | 6.3436
477 | 2871.0766 | 9.3612 | 12.04 | 1238.2824 | 4.0374 | 5.1928
478 | 2871.549 | 9.3627 | 12.042 | 963.8528 | 3.1427 | 4.042
479 | 2872.0271 | 9.3643 | 12.044 | 209.9921 | 0.68468 | 0.88061
480 | 2872.5111 | 9.3659 | 12.046 | 38.2849 | 0.12483 | 0.16055
481 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
482 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
483 | 2874.531 | 9.3725 | 12.0545 | 36.2649 | 0.11824 | 0.15208
484 | 2875.0355 | 9.3741 | 12.0566 | 206.9838 | 0.67487 | 0.868
485 | 2875.5456 | 9.3758 | 12.0588 | 377.6969 | 1.2315 | 1.5839
486 | 2876.0614 | 9.3774 | 12.0609 | 548.4045 | 1.7881 | 2.2998
487 | 2876.5828 | 9.3791 | 12.0631 | 719.1064 | 2.3447 | 3.0156
488 | 2877.1097 | 9.3809 | 12.0653 | 889.8027 | 2.9012 | 3.7314
489 | 2877.6423 | 9.3826 | 12.0676 | 1060.4934 | 3.4578 | 4.4472
490 | 2878.1803 | 9.3844 | 12.0698 | 1231.1787 | 4.0143 | 5.163
491 | 2878.7239 | 9.3861 | 12.0721 | 1401.8584 | 4.5708 | 5.8788
492 | 2879.2729 | 9.3879 | 12.0744 | 1572.5327 | 5.1273 | 6.5945
493 | 2879.8273 | 9.3897 | 12.0767 | 1743.2015 | 5.6837 | 7.3102
494 | 2880.3872 | 9.3915 | 12.0791 | 1913.865 | 6.2402 | 8.0259
495 | 2880.9525 | 9.3934 | 12.0814 | 1742.0764 | 5.6801 | 7.3055
496 | 2881.5231 | 9.3952 | 12.0838 | 1912.7291 | 6.2365 | 8.0211
497 | 2882.099 | 9.3971 | 12.0862 | 2597.0463 | 8.4677 | 10.8909
498 | 2882.6802 | 9.399 | 12.0887 | 2425.2418 | 7.9075 | 10.1704
499 | 2883.2667 | 9.4009 | 12.0911 | 2767.1019 | 9.0222 | 11.604
500 | 2883.8585 | 9.4029 | 12.0936 | 2389.8189 | 7.792 | 10.0218
501 | 2884.4554 | 9.4048 | 12.0961 | 2012.5307 | 6.5619 | 8.4397
502 | 2885.0576 | 9.4068 | 12.0986 | 1635.2373 | 5.3317 | 6.8575
503 | 2885.6649 | 9.4088 | 12.1012 | 1257.9388 | 4.1015 | 5.2752
504 | 2886.2773 | 9.4108 | 12.1038 | 880.6351 | 2.8713 | 3.693
505 | 2886.8949 | 9.4128 | 12.1064 | 23.9011 | 0.07793 | 0.10023
506 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
507 | 2888.432 | 9.4178 | 12.1128 | 22.3639 | 0.072918 | 0.093784
508 | 2889.0634 | 9.4198 | 12.1154 | 192.9558 | 0.62914 | 0.80917
509 | 2889.6998 | 9.4219 | 12.1181 | 620.3777 | 2.0228 | 2.6016
510 | 2890.3411 | 9.424 | 12.1208 | 876.5713 | 2.8581 | 3.676
511 | 2890.9874 | 9.4261 | 12.1235 | 1132.7599 | 3.6934 | 4.7503
512 | 2891.6386 | 9.4282 | 12.1262 | 1388.9436 | 4.5287 | 5.8246
513 | 2892.2948 | 9.4304 | 12.129 | 1645.1225 | 5.3639 | 6.8989
514 | 2892.9557 | 9.4325 | 12.1318 | 1901.2964 | 6.1992 | 7.9732
515 | 2893.6216 | 9.4347 | 12.1346 | 2157.4656 | 7.0344 | 9.0475
516 | 2894.2922 | 9.4369 | 12.1374 | 2413.6299 | 7.8697 | 10.1217
517 | 2894.9676 | 9.4391 | 12.1402 | 2669.7894 | 8.7049 | 11.1959
518 | 2895.6478 | 9.4413 | 12.1431 | 2925.9441 | 9.5401 | 12.2701
519 | 2896.3327 | 9.4435 | 12.1459 | 2754.0359 | 8.9796 | 11.5492
520 | 2897.0223 | 9.4458 | 12.1488 | 2981.644 | 9.7217 | 12.5037
521 | 2897.7166 | 9.448 | 12.1517 | 3779.9918 | 12.3247 | 15.8516
522 | 2898.4156 | 9.4503 | 12.1547 | 3608.0695 | 11.7642 | 15.1306
523 | 2899.1192 | 9.4526 | 12.1576 | 3949.8125 | 12.8784 | 16.5638
524 | 2899.8274 | 9.4549 | 12.1606 | 3606.6577 | 11.7596 | 15.1247
525 | 2900.5402 | 9.4573 | 12.1636 | 4119.6148 | 13.4321 | 17.2758
526 | 2901.2575 | 9.4596 | 12.1666 | 3262.781 | 10.6383 | 13.6827
527 | 2901.9794 | 9.4619 | 12.1696 | 2405.9427 | 7.8446 | 10.0895
528 | 2902.7057 | 9.4643 | 12.1727 | 1549.0999 | 5.0509 | 6.4962
529 | 2903.4366 | 9.4667 | 12.1757 | 7.3594 | 0.023995 | 0.030862
530 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
531 | 2905.2368 | 9.4726 | 12.1833 | 39.8038 | 0.12978 | 0.16692
532 | 2905.9795 | 9.475 | 12.1864 | 176.0398 | 0.57398 | 0.73823
533 | 2906.7265 | 9.4774 | 12.1895 | 493.2789 | 1.6083 | 2.0686
534 | 2907.4779 | 9.4799 | 12.1927 | 712.6717 | 2.3237 | 2.9886
535 | 2908.2336 | 9.4823 | 12.1958 | 932.0603 | 3.039 | 3.9086
536 | 2908.9936 | 9.4848 | 12.199 | 1151.4445 | 3.7543 | 4.8286
537 | 2909.7579 | 9.4873 | 12.2022 | 1370.8244 | 4.4696 | 5.7486
538 | 2910.5265 | 9.4898 | 12.2055 | 1590.2001 | 5.1849 | 6.6686
539 | 2911.2993 | 9.4923 | 12.2087 | 1809.5715 | 5.9001 | 7.5885
540 | 2912.0763 | 9.4949 | 12.212 | 2028.9387 | 6.6154 | 8.5085
541 | 2912.8575 | 9.4974 | 12.2152 | 2248.3017 | 7.3306 | 9.4284
542 | 2913.6429 | 9.5 | 12.2185 | 2467.6606 | 8.0458 | 10.3483
543 | 2914.4324 | 9.5026 | 12.2218 | 2687.0153 | 8.7611 | 11.2681
544 | 2915.226 | 9.5051 | 12.2252 | 2906.3659 | 9.4763 | 12.188
545 | 2916.0237 | 9.5077 | 12.2285 | 2734.3449 | 8.9154 | 11.4666
546 | 2916.8255 | 9.5104 | 12.2319 | 3075.9897 | 10.0293 | 12.8993
547 | 2917.6313 | 9.513 | 12.2352 | 3417.6305 | 11.1432 | 14.332
548 | 2918.4411 | 9.5156 | 12.2386 | 3588.044 | 11.6989 | 15.0467
549 | 2919.255 | 9.5183 | 12.2421 | 4100.9 | 13.371 | 17.1974
550 | 2920.0728 | 9.5209 | 12.2455 | 3243.9657 | 10.577 | 13.6037
551 | 2920.8945 | 9.5236 | 12.2489 | 2387.0275 | 7.7829 | 10.0101
552 | 2921.7202 | 9.5263 | 12.2524 | 1530.0854 | 4.9889 | 6.4165
553 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
554 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
555 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
556 | 2925.5021 | 9.5386 | 12.2683 | 156.5171 | 0.51033 | 0.65636
557 | 2926.3451 | 9.5414 | 12.2718 | 524.4628 | 1.71 | 2.1994
558 | 2927.1918 | 9.5442 | 12.2753 | 760.6945 | 2.4803 | 3.19
559 | 2928.0423 | 9.5469 | 12.2789 | 996.9223 | 3.2505 | 4.1806
560 | 2928.8966 | 9.5497 | 12.2825 | 1233.1465 | 4.0207 | 5.1713
561 | 2929.7546 | 9.5525 | 12.2861 | 1469.3669 | 4.7909 | 6.1619
562 | 2930.6163 | 9.5553 | 12.2897 | 1705.5836 | 5.5611 | 7.1525
563 | 2931.4817 | 9.5581 | 12.2933 | 1941.7966 | 6.3313 | 8.143
564 | 2932.3507 | 9.561 | 12.297 | 2178.006 | 7.1014 | 9.1336
565 | 2933.2234 | 9.5638 | 12.3006 | 2414.2117 | 7.8716 | 10.1241
566 | 2934.0996 | 9.5667 | 12.3043 | 2650.4139 | 8.6417 | 11.1147
567 | 2934.9795 | 9.5695 | 12.308 | 2886.6124 | 9.4118 | 12.1052
568 | 2935.863 | 9.5724 | 12.3117 | 2714.5056 | 8.8507 | 11.3834
569 | 2936.75 | 9.5753 | 12.3154 | 3021.8206 | 9.8527 | 12.6722
570 | 2937.6405 | 9.5782 | 12.3192 | 3329.132 | 10.8547 | 13.9609
571 | 2938.5345 | 9.5811 | 12.3229 | 3910.3971 | 12.7499 | 16.3985
572 | 2939.432 | 9.5841 | 12.3267 | 3909.4996 | 12.747 | 16.3947
573 | 2940.333 | 9.587 | 12.3304 | 4251.0452 | 13.8606 | 17.827
574 | 2941.2374 | 9.5899 | 12.3342 | 3359.7797 | 10.9546 | 14.0894
575 | 2942.1453 | 9.5929 | 12.338 | 2468.5107 | 8.0486 | 10.3518
576 | 2943.0565 | 9.5959 | 12.3419 | 1577.2384 | 5.1426 | 6.6142
577 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
578 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
579 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
580 | 2947.2783 | 9.6096 | 12.3596 | 134.741 | 0.43933 | 0.56504
581 | 2948.2037 | 9.6127 | 12.3635 | 476.2622 | 1.5529 | 1.9972
582 | 2949.1323 | 9.6157 | 12.3673 | 703.6312 | 2.2942 | 2.9507
583 | 2950.0643 | 9.6187 | 12.3713 | 930.997 | 3.0355 | 3.9042
584 | 2950.9995 | 9.6218 | 12.3752 | 1158.3595 | 3.7768 | 4.8576
585 | 2951.9378 | 9.6248 | 12.3791 | 1385.7189 | 4.5182 | 5.8111
586 | 2952.8794 | 9.6279 | 12.3831 | 1613.075 | 5.2595 | 6.7645
587 | 2953.8242 | 9.631 | 12.387 | 1840.428 | 6.0007 | 7.7179
588 | 2954.7721 | 9.6341 | 12.391 | 2067.7778 | 6.742 | 8.6713
589 | 2955.7232 | 9.6372 | 12.395 | 2295.1245 | 7.4833 | 9.6247
590 | 2956.6773 | 9.6403 | 12.399 | 2522.468 | 8.2245 | 10.5781
591 | 2957.6346 | 9.6434 | 12.403 | 2350.2875 | 7.6631 | 9.8561
592 | 2958.5949 | 9.6465 | 12.407 | 2748.8482 | 8.9627 | 11.5274
593 | 2959.5583 | 9.6497 | 12.4111 | 3147.4058 | 10.2622 | 13.1988
594 | 2960.5247 | 9.6528 | 12.4151 | 3545.9604 | 11.5617 | 14.8702
595 | 2961.4941 | 9.656 | 12.4192 | 3074.1269 | 10.0232 | 12.8915
596 | 2962.4665 | 9.6592 | 12.4233 | 2602.2904 | 8.4848 | 10.9128
597 | 2963.4419 | 9.6623 | 12.4274 | 2130.451 | 6.9464 | 8.9342
598 | 2964.4203 | 9.6655 | 12.4315 | 1658.6086 | 5.4079 | 6.9555
599 | 2965.4015 | 9.6687 | 12.4356 | 1186.7633 | 3.8695 | 4.9768
600 | 2966.3857 | 9.6719 | 12.4397 | 458.0801 | 1.4936 | 1.921
601 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
602 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
603 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
604 | 2971.0212 | 9.6871 | 12.4591 | 110.998 | 0.36191 | 0.46548
605 | 2972.0166 | 9.6903 | 12.4633 | 421.3177 | 1.3737 | 1.7668
606 | 2973.0148 | 9.6936 | 12.4675 | 638.2401 | 2.081 | 2.6765
607 | 2974.0158 | 9.6968 | 12.4717 | 855.1596 | 2.7883 | 3.5862
608 | 2975.0195 | 9.7001 | 12.4759 | 1072.0764 | 3.4955 | 4.4958
609 | 2976.026 | 9.7034 | 12.4801 | 1288.9905 | 4.2028 | 5.4055
610 | 2977.0353 | 9.7067 | 12.4844 | 1505.9018 | 4.91 | 6.3151
611 | 2978.0472 | 9.71 | 12.4886 | 1722.8104 | 5.6172 | 7.2247
612 | 2979.0618 | 9.7133 | 12.4929 | 1939.7163 | 6.3245 | 8.1343
613 | 2980.0792 | 9.7166 | 12.4971 | 2156.6196 | 7.0317 | 9.0439
614 | 2981.0991 | 9.7199 | 12.5014 | 2057.7577 | 6.7094 | 8.6293
615 | 2982.1217 | 9.7233 | 12.5057 | 1958.8933 | 6.387 | 8.2147
616 | 2983.1469 | 9.7266 | 12.51 | 1860.0262 | 6.0646 | 7.8001
617 | 2984.1748 | 9.7299 | 12.5143 | 1761.1565 | 5.7423 | 7.3855
618 | 2985.2052 | 9.7333 | 12.5186 | 1662.2842 | 5.4199 | 6.9709
619 | 2986.2381 | 9.7367 | 12.523 | 1563.4093 | 5.0975 | 6.5562
620 | 2987.2736 | 9.7401 | 12.5273 | 1464.5319 | 4.7751 | 6.1416
621 | 2988.3117 | 9.7434 | 12.5316 | 1805.9405 | 5.8883 | 7.5733
622 | 2989.3522 | 9.7468 | 12.536 | 1291.2301 | 4.2101 | 5.4148
623 | 2990.3953 | 9.7502 | 12.5404 | 776.5172 | 2.5318 | 3.2564
624 | 2991.4408 | 9.7536 | 12.5448 | 261.8018 | 0.85361 | 1.0979
625 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
626 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
627 | 2935.2564 | 9.5704 | 12.3092 | 0 | 0 | 0
628 | 2996.7227 | 9.7709 | 12.5669 | 134.2175 | 0.43762 | 0.56285
629 | 2997.7753 | 9.7743 | 12.5713 | 328.8486 | 1.0722 | 1.379
630 | 2998.8304 | 9.7777 | 12.5758 | 523.4774 | 1.7068 | 2.1952
631 | 2999.8878 | 9.7812 | 12.5802 | 718.1037 | 2.3414 | 3.0114
632 | 3000.9475 | 9.7846 | 12.5846 | 912.7277 | 2.976 | 3.8276
633 | 3002.0096 | 9.7881 | 12.5891 | 1107.3494 | 3.6105 | 4.6437
634 | 3003.074 | 9.7916 | 12.5936 | 1301.9688 | 4.2451 | 5.4599
635 | 3004.1406 | 9.795 | 12.598 | 1496.5859 | 4.8796 | 6.276
636 | 3005.2096 | 9.7985 | 12.6025 | 1691.2007 | 5.5142 | 7.0921
637 | 3006.2808 | 9.802 | 12.607 | 1787.9713 | 5.8297 | 7.498
638 | 3007.3543 | 9.8055 | 12.6115 | 1786.8979 | 5.8262 | 7.4935
639 | 3008.43 | 9.809 | 12.616 | 2275.0316 | 7.4178 | 9.5405
640 | 3009.5079 | 9.8125 | 12.6205 | 2469.6375 | 8.0523 | 10.3566
641 | 3010.588 | 9.8161 | 12.6251 | 2194.6001 | 7.1555 | 9.2032
642 | 3011.6702 | 9.8196 | 12.6296 | 1919.5606 | 6.2588 | 8.0498
643 | 3012.7546 | 9.8231 | 12.6342 | 1781.4975 | 5.8086 | 7.4708
644 | 3013.8412 | 9.8267 | 12.6387 | 1369.4751 | 4.4652 | 5.743
645 | 3014.9299 | 9.8302 | 12.6433 | 1094.4291 | 3.5684 | 4.5895
646 | 3016.0207 | 9.8338 | 12.6478 | 819.3811 | 2.6716 | 3.4361
647 | 3017.1136 | 9.8373 | 12.6524 | 64.9057 | 0.21163 | 0.27219
648 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
649 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
650 | 2739.5727 | 8.9324 | 11.4885 | 0 | 0 | 0
651 | 2910.796 | 9.4907 | 12.2066 | 0 | 0 | 0
652 | 3024.2608 | 9.8606 | 12.6824 | 57.7584 | 0.18832 | 0.24221
653 | 3025.3583 | 9.8642 | 12.687 | 227.8842 | 0.74302 | 0.95565
654 | 3026.4578 | 9.8678 | 12.6916 | 398.008 | 1.2977 | 1.6691
655 | 3027.5593 | 9.8714 | 12.6962 | 568.1299 | 1.8524 | 2.3825
656 | 3028.6627 | 9.875 | 12.7009 | 738.2497 | 2.4071 | 3.0959
657 | 3029.7681 | 9.8786 | 12.7055 | 908.3676 | 2.9617 | 3.8093
658 | 3030.8754 | 9.8822 | 12.7101 | 1078.4836 | 3.5164 | 4.5227
659 | 3031.9847 | 9.8858 | 12.7148 | 1248.5976 | 4.0711 | 5.2361
660 | 3033.0959 | 9.8895 | 12.7195 | 1418.7097 | 4.6257 | 5.9494
661 | 3034.2089 | 9.8931 | 12.7241 | 1588.82 | 5.1804 | 6.6628
662 | 3035.3238 | 9.8967 | 12.7288 | 1758.9283 | 5.735 | 7.3762
663 | 3036.4406 | 9.9004 | 12.7335 | 1586.5882 | 5.1731 | 6.6534
664 | 3037.5593 | 9.904 | 12.7382 | 1756.6929 | 5.7277 | 7.3668
665 | 3038.6797 | 9.9077 | 12.7429 | 2440.4656 | 7.9572 | 10.2342
666 | 3039.802 | 9.9113 | 12.7476 | 2268.12 | 7.3952 | 9.5115
667 | 3040.9261 | 9.915 | 12.7523 | 2609.4426 | 8.5081 | 10.9428
668 | 3042.0519 | 9.9187 | 12.757 | 2231.6255 | 7.2762 | 9.3584
669 | 3043.7086 | 9.9241 | 12.764 | 1853.2775 | 6.0426 | 7.7718
670 | 3045.7185 | 9.9306 | 12.7724 | 1474.5764 | 4.8079 | 6.1837
671 | 3047.7284 | 9.9372 | 12.7808 | 1095.8752 | 3.5731 | 4.5956
672 | 3049.7384 | 9.9437 | 12.7892 | 717.174 | 2.3384 | 3.0075
339293.6997