## Properties
T0 | K | 273
Tcond, h | ºC | 30 | 303
|  | Hot Sink |  | Cold Sink
|  | ºC | K | ºC | K
Tin |  | 20 | 293 | 10 | 283
Tout |  | 28 | 301 | 25 | 298
ED | kW |  | 0.018257 | Qcond,h | 0.038978 | Qcond,c
Exergy Destruction Summary
|  | Hot Sink | Cold Sink | Total
|  | ED, h | ED, c | ED
Winter |  | 41741 | 13225 | 54966
Spring/autumn |  | 39842 | 24957 | 64799
Summer |  | 36497 | 40079 | 76576
Note on D10: Peter North: This is the hot sink exergy factor used in the seasonal exergy calculations.
Note on F10: Peter North: This is the cold sink exergy factor used in the seasonal exergy calculations.

## Winter
Winter
| Hot Sink |  |  | Cold Sink
| Condenser Duty | Factor | Exergy Destruction | Condenser Duty | Factor | Exergy Destruction | Total Exergy Destruction
| Qcond, h | 0.018257 | ED, h | Qcond, c | 0.038978 | ED, c | ED
Total | 2286226.9586 |  | 41741 | 339293.6997 |  | 13225 | 54966
Hours | kWh |  | kWh | kWh |  | kW
1 | 2524.5 |  | 46.0908 | 0 |  | 0
2 | 2376 |  | 43.3796 | 0 |  | 0
3 | 2524.5 |  | 46.0908 | 0 |  | 0
4 | 2673 |  | 48.802 | 0 |  | 0
5 | 3044.25 |  | 55.5801 | 0 |  | 0
6 | 3267 |  | 59.6469 | 0 |  | 0
7 | 3489.75 |  | 63.7138 | 0 |  | 0
8 | 3712.5 |  | 67.7806 | 0 |  | 0
9 | 3732.6611 |  | 68.1487 | 202.5889 |  | 7.8965
10 | 3726.13 |  | 68.0295 | 431.87 |  | 16.8333
11 | 3719.6339 |  | 67.9109 | 661.1161 |  | 25.7689
12 | 3713.1725 |  | 67.7929 | 890.3275 |  | 34.703
13 | 3706.7458 |  | 67.6756 | 1119.5042 |  | 43.6358
14 | 3700.3537 |  | 67.5588 | 1348.6463 |  | 52.5673
15 | 3693.9961 |  | 67.4428 | 1206.5039 |  | 47.0269
16 | 3693.5554 |  | 67.4347 | 1404.9446 |  | 54.7617
17 | 3701.1356 |  | 67.5731 | 2090.3644 |  | 81.4778
18 | 3708.6838 |  | 67.7109 | 1934.3162 |  | 75.3954
19 | 3716.1999 |  | 67.8482 | 2223.8001 |  | 86.6789
20 | 3723.6835 |  | 67.9848 | 1919.3165 |  | 74.8108
21 | 3731.135 |  | 68.1208 | 2357.365 |  | 91.8849
22 | 3738.5542 |  | 68.2563 | 1607.4458 |  | 62.6547
23 | 3737.9181 |  | 68.2447 | 865.5819 |  | 33.7385
24 | 3731.4337 |  | 68.1263 | 129.5663 |  | 5.0502
25 | 2524.5 |  | 46.0908 | 0 |  | 0
26 | 2376 |  | 43.3796 | 0 |  | 0
27 | 2554.2 |  | 46.6331 | 0 |  | 0
28 | 2673 |  | 48.802 | 0 |  | 0
29 | 2948.7857 |  | 53.8372 | 0 |  | 0
30 | 3139.7143 |  | 57.323 | 0 |  | 0
31 | 3330.6429 |  | 60.8089 | 0 |  | 0
32 | 3521.5714 |  | 64.2947 | 0 |  | 0
33 | 3712.5 |  | 67.7806 | 0 |  | 0
34 | 3708.2572 |  | 67.7031 | 195.1714 |  | 7.6074
35 | 3701.9642 |  | 67.5883 | 392.3929 |  | 15.2946
36 | 3695.7053 |  | 67.474 | 589.5804 |  | 22.9806
37 | 3689.4802 |  | 67.3603 | 786.7341 |  | 30.6652
38 | 3682.936 |  | 67.2408 | 984.2068 |  | 38.3622
39 | 3675.8975 |  | 67.1123 | 1182.1739 |  | 46.0786
40 | 3674.7605 |  | 67.0916 | 1374.2395 |  | 53.5649
41 | 3681.6431 |  | 67.2172 | 1218.8569 |  | 47.5084
42 | 3688.4966 |  | 67.3424 | 1509.0034 |  | 58.8177
43 | 3695.3205 |  | 67.467 | 1799.1795 |  | 70.1281
44 | 3702.114 |  | 67.591 | 1940.886 |  | 75.6515
45 | 3708.8766 |  | 67.7145 | 2379.6234 |  | 92.7525
46 | 3715.6078 |  | 67.8373 | 1630.3922 |  | 63.5491
47 | 3714.2866 |  | 67.8132 | 889.2134 |  | 34.6596
48 | 3707.1295 |  | 67.6826 | 153.8705 |  | 5.9975
49 | 2524.5 |  | 46.0908 | 0 |  | 0
50 | 2376 |  | 43.3796 | 0 |  | 0
51 | 2524.5 |  | 46.0908 | 0 |  | 0
52 | 2673 |  | 48.802 | 0 |  | 0
53 | 2992.8462 |  | 54.6416 | 0 |  | 0
54 | 3198.4615 |  | 58.3956 | 0 |  | 0
55 | 3404.0769 |  | 62.1496 | 0 |  | 0
56 | 3609.6923 |  | 65.9036 | 0 |  | 0
57 | 3683.1396 |  | 67.2446 | 132.1681 |  | 5.1516
58 | 3676.1537 |  | 67.117 | 344.7693 |  | 13.4384
59 | 3669.2028 |  | 66.9901 | 557.3357 |  | 21.7237
60 | 3662.2867 |  | 66.8638 | 769.8672 |  | 30.0077
61 | 3655.4053 |  | 66.7382 | 982.3639 |  | 38.2904
62 | 3648.5585 |  | 66.6132 | 1194.8261 |  | 46.5717
63 | 3641.7462 |  | 66.4888 | 1407.2538 |  | 54.8517
64 | 3640.8211 |  | 66.4719 | 1259.6789 |  | 49.0995
65 | 3647.9123 |  | 66.6014 | 1519.8877 |  | 59.2419
66 | 3654.9732 |  | 66.7303 | 1780.1268 |  | 69.3855
67 | 3662.0028 |  | 66.8587 | 2277.9972 |  | 88.7914
68 | 3669.0002 |  | 66.9864 | 2270.9998 |  | 88.5186
69 | 3675.9651 |  | 67.1136 | 2561.0349 |  | 99.8236
70 | 3682.8976 |  | 67.2401 | 1781.9024 |  | 69.4547
71 | 3681.7798 |  | 67.2197 | 1010.8202 |  | 39.3996
72 | 3674.8423 |  | 67.0931 | 245.5577 |  | 9.5713
73 | 2524.5 |  | 46.0908 | 0 |  | 0
74 | 2376 |  | 43.3796 | 0 |  | 0
75 | 2524.5 |  | 46.0908 | 0 |  | 0
76 | 2673 |  | 48.802 | 0 |  | 0
77 | 2970 |  | 54.2245 | 0 |  | 0
78 | 3168 |  | 57.8395 | 0 |  | 0
79 | 3366 |  | 61.4544 | 0 |  | 0
80 | 3564 |  | 65.0694 | 0 |  | 0
81 | 3660.4576 |  | 66.8304 | 101.5424 |  | 3.9579
82 | 3667.5166 |  | 66.9593 | 292.4834 |  | 11.4004
83 | 3674.5505 |  | 67.0877 | 483.4495 |  | 18.8438
84 | 3681.5587 |  | 67.2157 | 674.4413 |  | 26.2882
85 | 3688.8938 |  | 67.3496 | 865.1062 |  | 33.72
86 | 3696.7305 |  | 67.4927 | 1055.2695 |  | 41.1321
87 | 3704.5388 |  | 67.6353 | 898.9612 |  | 35.0395
88 | 3712.3191 |  | 67.7773 | 1237.6809 |  | 48.2421
89 | 3720.0706 |  | 67.9188 | 1576.4294 |  | 61.4458
90 | 3727.7926 |  | 68.0598 | 1915.2074 |  | 74.6506
91 | 3735.4846 |  | 68.2002 | 1499.1404 |  | 58.4332
92 | 3743.1476 |  | 68.3402 | 1083.1024 |  | 42.217
93 | 3750.7831 |  | 68.4796 | 667.0919 |  | 26.0018
94 | 3758.3924 |  | 68.6185 | 251.1076 |  | 9.7876
95 | 3601.125 |  | 65.7472 | 0 |  | 0
96 | 2970 |  | 54.2245 | 0 |  | 0
97 | 2524.5 |  | 46.0908 | 0 |  | 0
98 | 2376 |  | 43.3796 | 0 |  | 0
99 | 2524.5 |  | 46.0908 | 0 |  | 0
100 | 2673 |  | 48.802 | 0 |  | 0
101 | 2943 |  | 53.7315 | 0 |  | 0
102 | 3132 |  | 57.1822 | 0 |  | 0
103 | 3321 |  | 60.6328 | 0 |  | 0
104 | 3510 |  | 64.0835 | 0 |  | 0
105 | 3699 |  | 67.5341 | 0 |  | 0
106 | 3754.8469 |  | 68.5538 | 133.1531 |  | 5.19
107 | 3762.5496 |  | 68.6944 | 314.4504 |  | 12.2566
108 | 3770.226 |  | 68.8345 | 495.774 |  | 19.3242
109 | 3777.8758 |  | 68.9742 | 677.1242 |  | 26.3928
110 | 3785.4984 |  | 69.1134 | 584.6445 |  | 22.7882
111 | 3793.094 |  | 69.252 | 492.1917 |  | 19.1846
112 | 3800.3983 |  | 69.3854 | 400.0302 |  | 15.5923
113 | 3805.2969 |  | 69.4748 | 310.2745 |  | 12.0938
114 | 3810.1744 |  | 69.5639 | 220.5398 |  | 8.5962
115 | 3815.0311 |  | 69.6526 | 130.826 |  | 5.0993
116 | 3819.8673 |  | 69.7409 | 41.1327 |  | 1.6033
117 | 3824.6831 |  | 69.8288 | 333.3169 |  | 12.992
118 | 3712.5 |  | 67.7806 | 0 |  | 0
119 | 3267 |  | 59.6469 | 0 |  | 0
120 | 2821.5 |  | 51.5133 | 0 |  | 0
121 | 2376 |  | 43.3796 | 0 |  | 0
122 | 2376 |  | 43.3796 | 0 |  | 0
123 | 2545.7143 |  | 46.4781 | 0 |  | 0
124 | 2715.4286 |  | 49.5767 | 0 |  | 0
125 | 2885.1429 |  | 52.6752 | 0 |  | 0
126 | 3054.8571 |  | 55.7738 | 0 |  | 0
127 | 3224.5714 |  | 58.8723 | 0 |  | 0
128 | 3394.2857 |  | 61.9708 | 0 |  | 0
129 | 3564 |  | 65.0694 | 0 |  | 0
130 | 3733.7143 |  | 68.1679 | 0 |  | 0
131 | 3764.8271 |  | 68.736 | 138.6014 |  | 5.4024
132 | 3755.2519 |  | 68.5611 | 317.8909 |  | 12.3907
133 | 3745.4524 |  | 68.3822 | 412.5476 |  | 16.0802
134 | 3735.6931 |  | 68.2041 | 422.3069 |  | 16.4606
135 | 3725.974 |  | 68.0266 | 856.3117 |  | 33.3772
136 | 3725.0993 |  | 68.0106 | 1026.9007 |  | 40.0263
137 | 3732.9701 |  | 68.1543 | 781.4299 |  | 30.4584
138 | 3740.811 |  | 68.2975 | 535.989 |  | 20.8917
139 | 3748.6226 |  | 68.4401 | 409.3774 |  | 15.9566
140 | 3756.4056 |  | 68.5822 | 45.1944 |  | 1.7616
141 | 3564 |  | 65.0694 | 0 |  | 0
142 | 3326.4 |  | 60.7314 | 0 |  | 0
143 | 2673 |  | 48.802 | 0 |  | 0
144 | 2524.5 |  | 46.0908 | 0 |  | 0
145 | 2376 |  | 43.3796 | 0 |  | 0
146 | 2376 |  | 43.3796 | 0 |  | 0
147 | 2524.5 |  | 46.0908 | 0 |  | 0
148 | 2673 |  | 48.802 | 0 |  | 0
149 | 2821.5 |  | 51.5133 | 0 |  | 0
150 | 2970 |  | 54.2245 | 0 |  | 0
151 | 3118.5 |  | 56.9357 | 0 |  | 0
152 | 3267 |  | 59.6469 | 0 |  | 0
153 | 3415.5 |  | 62.3582 | 0 |  | 0
154 | 3564 |  | 65.0694 | 0 |  | 0
155 | 3712.5 |  | 67.7806 | 0 |  | 0
156 | 3742.1908 |  | 68.3227 | 118.8092 |  | 4.6309
157 | 3736.0623 |  | 68.2108 | 273.4377 |  | 10.658
158 | 3729.9669 |  | 68.0995 | 428.0331 |  | 16.6838
159 | 3723.9043 |  | 67.9888 | 285.5957 |  | 11.1319
160 | 3723.8709 |  | 67.9882 | 434.1291 |  | 16.9214
161 | 3731.8788 |  | 68.1344 | 1020.1212 |  | 39.7621
162 | 3739.8544 |  | 68.28 | 863.6456 |  | 33.663
163 | 3747.7975 |  | 68.425 | 1152.7025 |  | 44.9298
164 | 3755.7079 |  | 68.5695 | 818.0921 |  | 31.8874
165 | 3763.0571 |  | 68.7036 | 484.0429 |  | 18.8669
166 | 3768.2611 |  | 68.7987 | 152.1389 |  | 5.93
167 | 3593.7 |  | 65.6116 | 0 |  | 0
168 | 3267 |  | 59.6469 | 0 |  | 0
169 | 2524.5 |  | 46.0908 | 0 |  | 0
170 | 2376 |  | 43.3796 | 0 |  | 0
171 | 2524.5 |  | 46.0908 | 0 |  | 0
172 | 2673 |  | 48.802 | 0 |  | 0
173 | 3044.25 |  | 55.5801 | 0 |  | 0
174 | 3267 |  | 59.6469 | 0 |  | 0
175 | 3489.75 |  | 63.7138 | 0 |  | 0
176 | 3712.5 |  | 67.7806 | 0 |  | 0
177 | 3726.0637 |  | 68.0282 | 209.1863 |  | 8.1536
178 | 3719.161 |  | 67.9022 | 438.839 |  | 17.105
179 | 3712.2927 |  | 67.7768 | 668.4573 |  | 26.055
180 | 3705.4586 |  | 67.6521 | 898.0414 |  | 35.0037
181 | 3698.6585 |  | 67.5279 | 1127.5915 |  | 43.9511
182 | 3691.8924 |  | 67.4044 | 1357.1076 |  | 52.8971
183 | 3685.1601 |  | 67.2815 | 1215.3399 |  | 47.3713
184 | 3684.425 |  | 67.268 | 1414.075 |  | 55.1176
185 | 3691.7222 |  | 67.4013 | 2099.7778 |  | 81.8448
186 | 3698.9837 |  | 67.5338 | 1944.0163 |  | 75.7735
187 | 3706.2094 |  | 67.6658 | 2233.7906 |  | 87.0683
188 | 3713.399 |  | 67.797 | 1929.601 |  | 75.2116
189 | 3720.5528 |  | 67.9276 | 2367.9472 |  | 92.2974
190 | 3728.1115 |  | 68.0656 | 1617.8885 |  | 63.0618
191 | 3728.0397 |  | 68.0643 | 875.4603 |  | 34.1235
192 | 3722.0514 |  | 67.955 | 138.9486 |  | 5.4159
193 | 2524.5 |  | 46.0908 | 0 |  | 0
194 | 2376 |  | 43.3796 | 0 |  | 0
195 | 2554.2 |  | 46.6331 | 0 |  | 0
196 | 2673 |  | 48.802 | 0 |  | 0
197 | 2948.7857 |  | 53.8372 | 0 |  | 0
198 | 3139.7143 |  | 57.323 | 0 |  | 0
199 | 3330.6429 |  | 60.8089 | 0 |  | 0
200 | 3521.5714 |  | 64.2947 | 0 |  | 0
201 | 3709.5604 |  | 67.7269 | 2.9396 |  | 0.11458
202 | 3703.7076 |  | 67.6201 | 199.721 |  | 7.7847
203 | 3697.8868 |  | 67.5138 | 396.4703 |  | 15.4535
204 | 3692.0979 |  | 67.4081 | 593.1878 |  | 23.1212
205 | 3686.3407 |  | 67.303 | 789.8736 |  | 30.7876
206 | 3679.7336 |  | 67.1824 | 987.4093 |  | 38.4871
207 | 3673.1597 |  | 67.0624 | 1184.9118 |  | 46.1853
208 | 3672.504 |  | 67.0504 | 1376.496 |  | 53.6528
209 | 3679.8662 |  | 67.1848 | 1220.6338 |  | 47.5776
210 | 3687.1939 |  | 67.3186 | 1510.3061 |  | 58.8684
211 | 3694.4867 |  | 67.4517 | 1800.0133 |  | 70.1606
212 | 3701.7441 |  | 67.5842 | 1941.2559 |  | 75.6659
213 | 3708.9655 |  | 67.7161 | 2379.5345 |  | 92.7491
214 | 3716.1508 |  | 67.8473 | 1629.8492 |  | 63.528
215 | 3715.2787 |  | 67.8313 | 888.2213 |  | 34.6209
216 | 3708.5671 |  | 67.7088 | 152.4329 |  | 5.9415
217 | 2524.5 |  | 46.0908 | 0 |  | 0
218 | 2376 |  | 43.3796 | 0 |  | 0
219 | 2524.5 |  | 46.0908 | 0 |  | 0
220 | 2673 |  | 48.802 | 0 |  | 0
221 | 2992.8462 |  | 54.6416 | 0 |  | 0
222 | 3198.4615 |  | 58.3956 | 0 |  | 0
223 | 3404.0769 |  | 62.1496 | 0 |  | 0
224 | 3609.6923 |  | 65.9036 | 0 |  | 0
225 | 3688.507 |  | 67.3426 | 126.8007 |  | 4.9424
226 | 3681.9463 |  | 67.2228 | 338.9768 |  | 13.2126
227 | 3675.4185 |  | 67.1036 | 551.1199 |  | 21.4815
228 | 3668.9236 |  | 66.985 | 763.2302 |  | 29.749
229 | 3662.4615 |  | 66.867 | 975.3077 |  | 38.0154
230 | 3656.032 |  | 66.7496 | 1187.3526 |  | 46.2804
231 | 3649.635 |  | 66.6329 | 1399.365 |  | 54.5442
232 | 3649.8039 |  | 66.6359 | 1250.6961 |  | 48.7494
233 | 3658.1569 |  | 66.7884 | 1509.6431 |  | 58.8426
234 | 3666.4753 |  | 66.9403 | 1768.6247 |  | 68.9371
235 | 3674.7582 |  | 67.0915 | 2265.2418 |  | 88.2942
236 | 3683.0049 |  | 67.2421 | 2256.9951 |  | 87.9727
237 | 3691.2151 |  | 67.392 | 2545.7849 |  | 99.2291
238 | 3699.3889 |  | 67.5412 | 1765.4111 |  | 68.8119
239 | 3699.5133 |  | 67.5435 | 993.0867 |  | 38.7084
240 | 3693.8434 |  | 67.44 | 226.5566 |  | 8.8307
241 | 2524.5 |  | 46.0908 | 0 |  | 0
242 | 2376 |  | 43.3796 | 0 |  | 0
243 | 2524.5 |  | 46.0908 | 0 |  | 0
244 | 2673 |  | 48.802 | 0 |  | 0
245 | 2970 |  | 54.2245 | 0 |  | 0
246 | 3168 |  | 57.8395 | 0 |  | 0
247 | 3366 |  | 61.4544 | 0 |  | 0
248 | 3564 |  | 65.0694 | 0 |  | 0
249 | 3691.0515 |  | 67.389 | 70.9485 |  | 2.7654
250 | 3699.3004 |  | 67.5396 | 260.6996 |  | 10.1615
251 | 3707.5203 |  | 67.6897 | 450.4797 |  | 17.5587
252 | 3715.7108 |  | 67.8392 | 640.2892 |  | 24.9571
253 | 3723.8716 |  | 67.9882 | 830.1284 |  | 32.3566
254 | 3732.0022 |  | 68.1367 | 1019.9978 |  | 39.7573
255 | 3740.1024 |  | 68.2846 | 863.3976 |  | 33.6534
256 | 3748.1725 |  | 68.4319 | 1201.8275 |  | 46.8446
257 | 3756.2119 |  | 68.5787 | 1540.2881 |  | 60.0371
258 | 3763.6903 |  | 68.7152 | 1879.3097 |  | 73.2514
259 | 3769.0225 |  | 68.8126 | 1465.6025 |  | 57.126
260 | 3774.3288 |  | 68.9094 | 1051.9212 |  | 41.0016
261 | 3779.6105 |  | 69.0059 | 638.2645 |  | 24.8782
262 | 3784.8691 |  | 69.1019 | 224.6309 |  | 8.7556
263 | 3601.125 |  | 65.7472 | 0 |  | 0
264 | 2970 |  | 54.2245 | 0 |  | 0
265 | 2524.5 |  | 46.0908 | 0 |  | 0
266 | 2376 |  | 43.3796 | 0 |  | 0
267 | 2524.5 |  | 46.0908 | 0 |  | 0
268 | 2673 |  | 48.802 | 0 |  | 0
269 | 2943 |  | 53.7315 | 0 |  | 0
270 | 3132 |  | 57.1822 | 0 |  | 0
271 | 3321 |  | 60.6328 | 0 |  | 0
272 | 3510 |  | 64.0835 | 0 |  | 0
273 | 3699 |  | 67.5341 | 0 |  | 0
274 | 3754.0298 |  | 68.5388 | 133.9702 |  | 5.2219
275 | 3759.4294 |  | 68.6374 | 317.5706 |  | 12.3782
276 | 3764.8074 |  | 68.7356 | 501.1926 |  | 19.5354
277 | 3770.1632 |  | 68.8334 | 684.8368 |  | 26.6934
278 | 3775.4964 |  | 68.9308 | 594.6464 |  | 23.178
279 | 3780.8072 |  | 69.0277 | 504.4785 |  | 19.6635
280 | 3786.0958 |  | 69.1243 | 414.3328 |  | 16.1498
281 | 3791.3625 |  | 69.2204 | 324.2089 |  | 12.637
282 | 3796.6077 |  | 69.3162 | 234.1066 |  | 9.125
283 | 3801.8316 |  | 69.4116 | 144.0256 |  | 5.6138
284 | 3807.0344 |  | 69.5066 | 53.9656 |  | 2.1035
285 | 3812.2163 |  | 69.6012 | 345.7837 |  | 13.4779
286 | 3712.5 |  | 67.7806 | 0 |  | 0
287 | 3267 |  | 59.6469 | 0 |  | 0
288 | 2821.5 |  | 51.5133 | 0 |  | 0
289 | 2376 |  | 43.3796 | 0 |  | 0
290 | 2376 |  | 43.3796 | 0 |  | 0
291 | 2545.7143 |  | 46.4781 | 0 |  | 0
292 | 2715.4286 |  | 49.5767 | 0 |  | 0
293 | 2885.1429 |  | 52.6752 | 0 |  | 0
294 | 3054.8571 |  | 55.7738 | 0 |  | 0
295 | 3224.5714 |  | 58.8723 | 0 |  | 0
296 | 3394.2857 |  | 61.9708 | 0 |  | 0
297 | 3564 |  | 65.0694 | 0 |  | 0
298 | 3733.7143 |  | 68.1679 | 0 |  | 0
299 | 3756.8349 |  | 68.59 | 146.5937 |  | 5.7139
300 | 3747.3692 |  | 68.4172 | 325.7737 |  | 12.6979
301 | 3737.9422 |  | 68.2451 | 420.0578 |  | 16.3729
302 | 3728.5538 |  | 68.0737 | 429.4462 |  | 16.7389
303 | 3720.7913 |  | 67.932 | 861.4944 |  | 33.5792
304 | 3720.0967 |  | 67.9193 | 1031.9033 |  | 40.2213
305 | 3727.4413 |  | 68.0534 | 786.9587 |  | 30.6739
306 | 3734.7572 |  | 68.187 | 542.0428 |  | 21.1276
307 | 3742.045 |  | 68.32 | 415.955 |  | 16.213
308 | 3749.3054 |  | 68.4526 | 52.2946 |  | 2.0383
309 | 3564 |  | 65.0694 | 0 |  | 0
310 | 3326.4 |  | 60.7314 | 0 |  | 0
311 | 2673 |  | 48.802 | 0 |  | 0
312 | 2524.5 |  | 46.0908 | 0 |  | 0
313 | 2376 |  | 43.3796 | 0 |  | 0
314 | 2376 |  | 43.3796 | 0 |  | 0
315 | 2524.5 |  | 46.0908 | 0 |  | 0
316 | 2673 |  | 48.802 | 0 |  | 0
317 | 2821.5 |  | 51.5133 | 0 |  | 0
318 | 2970 |  | 54.2245 | 0 |  | 0
319 | 3118.5 |  | 56.9357 | 0 |  | 0
320 | 3267 |  | 59.6469 | 0 |  | 0
321 | 3415.5 |  | 62.3582 | 0 |  | 0
322 | 3564 |  | 65.0694 | 0 |  | 0
323 | 3712.5 |  | 67.7806 | 0 |  | 0
324 | 3712.857 |  | 67.7871 | 148.143 |  | 5.7743
325 | 3706.24 |  | 67.6663 | 303.26 |  | 11.8204
326 | 3699.656 |  | 67.5461 | 458.344 |  | 17.8652
327 | 3693.1051 |  | 67.4265 | 316.3949 |  | 12.3324
328 | 3692.5981 |  | 67.4173 | 465.4019 |  | 18.1403
329 | 3700.136 |  | 67.5549 | 1051.864 |  | 40.9994
330 | 3707.6425 |  | 67.6919 | 895.8575 |  | 34.9186
331 | 3715.1176 |  | 67.8284 | 1185.3824 |  | 46.2036
332 | 3722.5609 |  | 67.9643 | 851.2391 |  | 33.1794
333 | 3729.9732 |  | 68.0996 | 517.1268 |  | 20.1565
334 | 3737.3555 |  | 68.2344 | 183.0445 |  | 7.1347
335 | 3593.7 |  | 65.6116 | 0 |  | 0
336 | 3267 |  | 59.6469 | 0 |  | 0
337 | 2524.5 |  | 46.0908 | 0 |  | 0
338 | 2376 |  | 43.3796 | 0 |  | 0
339 | 2524.5 |  | 46.0908 | 0 |  | 0
340 | 2673 |  | 48.802 | 0 |  | 0
341 | 3044.25 |  | 55.5801 | 0 |  | 0
342 | 3267 |  | 59.6469 | 0 |  | 0
343 | 3489.75 |  | 63.7138 | 0 |  | 0
344 | 3712.2687 |  | 67.7764 | 0.23128 |  | 0.0090148
345 | 3711.7157 |  | 67.7663 | 223.5343 |  | 8.7129
346 | 3705.1602 |  | 67.6466 | 452.8398 |  | 17.6507
347 | 3698.6375 |  | 67.5275 | 682.1125 |  | 26.5873
348 | 3692.1475 |  | 67.409 | 911.3525 |  | 35.5225
349 | 3685.6901 |  | 67.2911 | 1140.5599 |  | 44.4565
350 | 3679.2651 |  | 67.1738 | 1369.7349 |  | 53.3893
351 | 3672.8725 |  | 67.0571 | 1227.6275 |  | 47.8502
352 | 3672.5112 |  | 67.0505 | 1425.9888 |  | 55.5819
353 | 3680.188 |  | 67.1907 | 2111.312 |  | 82.2943
354 | 3687.8284 |  | 67.3302 | 1955.1716 |  | 76.2083
355 | 3695.4321 |  | 67.469 | 2244.5679 |  | 87.4884
356 | 3702.9991 |  | 67.6071 | 1940.0009 |  | 75.617
357 | 3710.5295 |  | 67.7446 | 2377.9705 |  | 92.6881
358 | 3718.0231 |  | 67.8814 | 1627.9769 |  | 63.455
359 | 3717.4387 |  | 67.8708 | 886.0613 |  | 34.5367
360 | 3710.8963 |  | 67.7513 | 150.1037 |  | 5.8507
361 | 2524.5 |  | 46.0908 | 0 |  | 0
362 | 2376 |  | 43.3796 | 0 |  | 0
363 | 2554.2 |  | 46.6331 | 0 |  | 0
364 | 2673 |  | 48.802 | 0 |  | 0
365 | 2948.7857 |  | 53.8372 | 0 |  | 0
366 | 3139.7143 |  | 57.323 | 0 |  | 0
367 | 3330.6429 |  | 60.8089 | 0 |  | 0
368 | 3521.5714 |  | 64.2947 | 0 |  | 0
369 | 3693.3152 |  | 67.4303 | 19.1848 |  | 0.74778
370 | 3686.9114 |  | 67.3134 | 216.5172 |  | 8.4394
371 | 3680.5397 |  | 67.1971 | 413.8174 |  | 16.1297
372 | 3674.2002 |  | 67.0814 | 611.0855 |  | 23.8188
373 | 3667.8927 |  | 66.9662 | 808.3216 |  | 31.5066
374 | 3661.617 |  | 66.8516 | 1005.5258 |  | 39.1932
375 | 3655.3732 |  | 66.7376 | 1202.6983 |  | 46.8786
376 | 3655.1005 |  | 66.7326 | 1393.8995 |  | 54.3312
377 | 3662.8542 |  | 66.8742 | 1237.6458 |  | 48.2407
378 | 3670.572 |  | 67.0151 | 1526.928 |  | 59.5163
379 | 3678.2533 |  | 67.1554 | 1816.2467 |  | 70.7933
380 | 3685.8975 |  | 67.2949 | 1957.1025 |  | 76.2836
381 | 3693.5038 |  | 67.4338 | 2394.9962 |  | 93.3517
382 | 3701.0719 |  | 67.572 | 1644.9281 |  | 64.1157
383 | 3700.5712 |  | 67.5628 | 902.9288 |  | 35.1942
384 | 3694.1749 |  | 67.446 | 166.8251 |  | 6.5025
385 | 2524.5 |  | 46.0908 | 0 |  | 0
386 | 2376 |  | 43.3796 | 0 |  | 0
387 | 2524.5 |  | 46.0908 | 0 |  | 0
388 | 2673 |  | 48.802 | 0 |  | 0
389 | 2992.8462 |  | 54.6416 | 0 |  | 0
390 | 3198.4615 |  | 58.3956 | 0 |  | 0
391 | 3404.0769 |  | 62.1496 | 0 |  | 0
392 | 3609.6923 |  | 65.9036 | 0 |  | 0
393 | 3676.7973 |  | 67.1288 | 138.5103 |  | 5.3988
394 | 3670.5391 |  | 67.0145 | 350.384 |  | 13.6572
395 | 3664.3124 |  | 66.9008 | 562.226 |  | 21.9143
396 | 3658.1173 |  | 66.7877 | 774.0365 |  | 30.1703
397 | 3651.9537 |  | 66.6752 | 985.8156 |  | 38.4249
398 | 3645.8213 |  | 66.5632 | 1197.5633 |  | 46.6784
399 | 3639.7202 |  | 66.4518 | 1409.2798 |  | 54.9307
400 | 3639.5078 |  | 66.448 | 1260.9922 |  | 49.1507
401 | 3647.3058 |  | 66.5903 | 1520.4942 |  | 59.2655
402 | 3655.0661 |  | 66.732 | 1780.0339 |  | 69.3818
403 | 3662.7881 |  | 66.873 | 2277.2119 |  | 88.7608
404 | 3670.4709 |  | 67.0133 | 2269.5291 |  | 88.4613
405 | 3678.1144 |  | 67.1528 | 2558.8856 |  | 99.7398
406 | 3685.7187 |  | 67.2917 | 1779.0813 |  | 69.3447
407 | 3685.9745 |  | 67.2963 | 1006.6255 |  | 39.2361
408 | 3680.5997 |  | 67.1982 | 239.8003 |  | 9.3469
409 | 2524.5 |  | 46.0908 | 0 |  | 0
410 | 2376 |  | 43.3796 | 0 |  | 0
411 | 2524.5 |  | 46.0908 | 0 |  | 0
412 | 2673 |  | 48.802 | 0 |  | 0
413 | 2970 |  | 54.2245 | 0 |  | 0
414 | 3168 |  | 57.8395 | 0 |  | 0
415 | 3366 |  | 61.4544 | 0 |  | 0
416 | 3564 |  | 65.0694 | 0 |  | 0
417 | 3680.1414 |  | 67.1898 | 81.8586 |  | 3.1907
418 | 3688.6536 |  | 67.3452 | 271.3464 |  | 10.5765
419 | 3697.1326 |  | 67.5 | 460.8674 |  | 17.9636
420 | 3705.5781 |  | 67.6542 | 650.4219 |  | 25.352
421 | 3713.9897 |  | 67.8078 | 840.0103 |  | 32.7418
422 | 3722.3671 |  | 67.9608 | 1029.6329 |  | 40.1328
423 | 3730.7099 |  | 68.1131 | 872.7901 |  | 34.0195
424 | 3739.0186 |  | 68.2648 | 1210.9814 |  | 47.2014
425 | 3747.2925 |  | 68.4158 | 1549.2075 |  | 60.3847
426 | 3755.5308 |  | 68.5662 | 1887.4692 |  | 73.5694
427 | 3763.4684 |  | 68.7112 | 1471.1566 |  | 57.3425
428 | 3768.9918 |  | 68.812 | 1057.2582 |  | 41.2096
429 | 3774.4867 |  | 68.9123 | 643.3883 |  | 25.0779
430 | 3779.9546 |  | 69.0122 | 229.5454 |  | 8.9472
431 | 3601.125 |  | 65.7472 | 0 |  | 0
432 | 2970 |  | 54.2245 | 0 |  | 0
433 | 2524.5 |  | 46.0908 | 0 |  | 0
434 | 2376 |  | 43.3796 | 0 |  | 0
435 | 2524.5 |  | 46.0908 | 0 |  | 0
436 | 2673 |  | 48.802 | 0 |  | 0
437 | 2943 |  | 53.7315 | 0 |  | 0
438 | 3132 |  | 57.1822 | 0 |  | 0
439 | 3321 |  | 60.6328 | 0 |  | 0
440 | 3510 |  | 64.0835 | 0 |  | 0
441 | 3699 |  | 67.5341 | 0 |  | 0
442 | 3751.7524 |  | 68.4973 | 136.2476 |  | 5.3106
443 | 3757.3109 |  | 68.5987 | 319.6891 |  | 12.4608
444 | 3762.8446 |  | 68.6998 | 503.1554 |  | 19.6119
445 | 3768.3532 |  | 68.8003 | 686.6468 |  | 26.764
446 | 3773.8363 |  | 68.9004 | 596.3065 |  | 23.2427
447 | 3779.2944 |  | 69.0001 | 505.9913 |  | 19.7224
448 | 3784.7278 |  | 69.0993 | 415.7008 |  | 16.2031
449 | 3790.1371 |  | 69.1981 | 325.4344 |  | 12.6847
450 | 3795.5226 |  | 69.2964 | 235.1917 |  | 9.1673
451 | 3800.8848 |  | 69.3943 | 144.9724 |  | 5.6507
452 | 3806.2241 |  | 69.4918 | 54.7759 |  | 2.135
453 | 3811.5409 |  | 69.5888 | 346.4591 |  | 13.5042
454 | 3712.5 |  | 67.7806 | 0 |  | 0
455 | 3267 |  | 59.6469 | 0 |  | 0
456 | 2821.5 |  | 51.5133 | 0 |  | 0
457 | 2376 |  | 43.3796 | 0 |  | 0
458 | 2376 |  | 43.3796 | 0 |  | 0
459 | 2545.7143 |  | 46.4781 | 0 |  | 0
460 | 2715.4286 |  | 49.5767 | 0 |  | 0
461 | 2885.1429 |  | 52.6752 | 0 |  | 0
462 | 3054.8571 |  | 55.7738 | 0 |  | 0
463 | 3224.5714 |  | 58.8723 | 0 |  | 0
464 | 3394.2857 |  | 61.9708 | 0 |  | 0
465 | 3564 |  | 65.0694 | 0 |  | 0
466 | 3733.7143 |  | 68.1679 | 0 |  | 0
467 | 3759.1954 |  | 68.6331 | 144.2331 |  | 5.6219
468 | 3749.962 |  | 68.4646 | 323.1808 |  | 12.5969
469 | 3740.7663 |  | 68.2967 | 417.2337 |  | 16.2629
470 | 3731.6081 |  | 68.1295 | 426.3919 |  | 16.6198
471 | 3723.2812 |  | 67.9774 | 859.0045 |  | 33.4821
472 | 3722.7273 |  | 67.9673 | 1029.2727 |  | 40.1188
473 | 3730.1976 |  | 68.1037 | 784.2024 |  | 30.5665
474 | 3737.6402 |  | 68.2396 | 539.1598 |  | 21.0153
475 | 3745.056 |  | 68.375 | 412.944 |  | 16.0957
476 | 3752.4455 |  | 68.5099 | 49.1545 |  | 1.9159
477 | 3564 |  | 65.0694 | 0 |  | 0
478 | 3326.4 |  | 60.7314 | 0 |  | 0
479 | 2673 |  | 48.802 | 0 |  | 0
480 | 2524.5 |  | 46.0908 | 0 |  | 0
481 | 2376 |  | 43.3796 | 0 |  | 0
482 | 2376 |  | 43.3796 | 0 |  | 0
483 | 2524.5 |  | 46.0908 | 0 |  | 0
484 | 2673 |  | 48.802 | 0 |  | 0
485 | 2821.5 |  | 51.5133 | 0 |  | 0
486 | 2970 |  | 54.2245 | 0 |  | 0
487 | 3118.5 |  | 56.9357 | 0 |  | 0
488 | 3267 |  | 59.6469 | 0 |  | 0
489 | 3415.5 |  | 62.3582 | 0 |  | 0
490 | 3564 |  | 65.0694 | 0 |  | 0
491 | 3712.5 |  | 67.7806 | 0 |  | 0
492 | 3722.3563 |  | 67.9606 | 138.6437 |  | 5.404
493 | 3716.8262 |  | 67.8596 | 292.6738 |  | 11.4078
494 | 3711.3265 |  | 67.7592 | 446.6735 |  | 17.4104
495 | 3705.857 |  | 67.6593 | 303.643 |  | 11.8353
496 | 3706.3757 |  | 67.6688 | 451.6243 |  | 17.6033
497 | 3714.9289 |  | 67.825 | 1037.0711 |  | 40.4228
498 | 3723.4502 |  | 67.9805 | 880.0498 |  | 34.3024
499 | 3731.9396 |  | 68.1355 | 1168.5604 |  | 45.5479
500 | 3740.3968 |  | 68.2899 | 833.4032 |  | 32.4842
501 | 3748.8225 |  | 68.4438 | 498.2775 |  | 19.4218
502 | 3757.2178 |  | 68.597 | 163.1822 |  | 6.3605
503 | 3593.7 |  | 65.6116 | 0 |  | 0
504 | 3267 |  | 59.6469 | 0 |  | 0
505 | 2524.5 |  | 46.0908 | 0 |  | 0
506 | 2376 |  | 43.3796 | 0 |  | 0
507 | 2524.5 |  | 46.0908 | 0 |  | 0
508 | 2673 |  | 48.802 | 0 |  | 0
509 | 3044.25 |  | 55.5801 | 0 |  | 0
510 | 3267 |  | 59.6469 | 0 |  | 0
511 | 3489.75 |  | 63.7138 | 0 |  | 0
512 | 3712.5 |  | 67.7806 | 0 |  | 0
513 | 3743.526 |  | 68.3471 | 191.724 |  | 7.473
514 | 3738.0022 |  | 68.2462 | 419.9978 |  | 16.3706
515 | 3732.5087 |  | 68.1459 | 648.2413 |  | 25.267
516 | 3727.0453 |  | 68.0462 | 876.4547 |  | 34.1623
517 | 3721.612 |  | 67.947 | 1104.638 |  | 43.0564
518 | 3716.2085 |  | 67.8483 | 1332.7915 |  | 51.9493
519 | 3710.8349 |  | 67.7502 | 1189.6651 |  | 46.3705
520 | 3711.4752 |  | 67.7619 | 1387.0248 |  | 54.0632
521 | 3720.1502 |  | 67.9203 | 2071.3498 |  | 80.7367
522 | 3728.7884 |  | 68.078 | 1914.2116 |  | 74.6118
523 | 3737.3895 |  | 68.235 | 2202.6105 |  | 85.853
524 | 3745.9533 |  | 68.3914 | 1897.0467 |  | 73.9427
525 | 3754.4801 |  | 68.5471 | 2334.0199 |  | 90.975
526 | 3762.9697 |  | 68.7021 | 1583.0303 |  | 61.7031
527 | 3760.7366 |  | 68.6613 | 842.7634 |  | 32.8491
528 | 3752.5513 |  | 68.5118 | 108.4487 |  | 4.2271
529 | 2524.5 |  | 46.0908 | 0 |  | 0
530 | 2376 |  | 43.3796 | 0 |  | 0
531 | 2554.2 |  | 46.6331 | 0 |  | 0
532 | 2673 |  | 48.802 | 0 |  | 0
533 | 2948.7857 |  | 53.8372 | 0 |  | 0
534 | 3139.7143 |  | 57.323 | 0 |  | 0
535 | 3330.6429 |  | 60.8089 | 0 |  | 0
536 | 3521.5714 |  | 64.2947 | 0 |  | 0
537 | 3712.5 |  | 67.7806 | 0 |  | 0
538 | 3722.1511 |  | 67.9568 | 181.2775 |  | 7.0658
539 | 3715.9065 |  | 67.8428 | 378.4507 |  | 14.7512
540 | 3709.6932 |  | 67.7294 | 575.5925 |  | 22.4353
541 | 3703.5111 |  | 67.6165 | 772.7032 |  | 30.1183
542 | 3697.3601 |  | 67.5042 | 969.7828 |  | 37.8
543 | 3691.2401 |  | 67.3925 | 1166.8313 |  | 45.4805
544 | 3691.1147 |  | 67.3902 | 1357.8853 |  | 52.9274
545 | 3699.0209 |  | 67.5345 | 1201.4791 |  | 46.831
546 | 3706.8921 |  | 67.6782 | 1490.6079 |  | 58.1006
547 | 3714.7278 |  | 67.8213 | 1779.7722 |  | 69.3716
548 | 3722.5273 |  | 67.9637 | 1920.4727 |  | 74.8558
549 | 3730.2899 |  | 68.1054 | 2358.2101 |  | 91.9179
550 | 3738.0151 |  | 68.2464 | 1607.9849 |  | 62.6757
551 | 3737.6664 |  | 68.2401 | 865.8336 |  | 33.7483
552 | 3731.3857 |  | 68.1254 | 129.6143 |  | 5.0521
553 | 2524.5 |  | 46.0908 | 0 |  | 0
554 | 2376 |  | 43.3796 | 0 |  | 0
555 | 2524.5 |  | 46.0908 | 0 |  | 0
556 | 2673 |  | 48.802 | 0 |  | 0
557 | 2992.8462 |  | 54.6416 | 0 |  | 0
558 | 3198.4615 |  | 58.3956 | 0 |  | 0
559 | 3404.0769 |  | 62.1496 | 0 |  | 0
560 | 3609.6923 |  | 65.9036 | 0 |  | 0
561 | 3715.8668 |  | 67.8421 | 99.4409 |  | 3.876
562 | 3709.7126 |  | 67.7297 | 311.2104 |  | 12.1303
563 | 3703.5894 |  | 67.6179 | 522.9491 |  | 20.3834
564 | 3697.497 |  | 67.5067 | 734.6569 |  | 28.6353
565 | 3691.4353 |  | 67.396 | 946.334 |  | 36.886
566 | 3685.4042 |  | 67.2859 | 1157.9805 |  | 45.1356
567 | 3679.4036 |  | 67.1764 | 1369.5964 |  | 53.3839
568 | 3679.3522 |  | 67.1754 | 1221.1478 |  | 47.5977
569 | 3687.323 |  | 67.3209 | 1480.477 |  | 57.7058
570 | 3695.2569 |  | 67.4658 | 1739.8431 |  | 67.8153
571 | 3703.1529 |  | 67.61 | 2236.8471 |  | 87.1874
572 | 3711.0102 |  | 67.7534 | 2228.9898 |  | 86.8812
573 | 3718.8283 |  | 67.8961 | 2518.1717 |  | 98.1528
574 | 3726.7836 |  | 68.0414 | 1738.0164 |  | 67.7441
575 | 3727.3777 |  | 68.0522 | 965.2223 |  | 37.6223
576 | 3722.0938 |  | 67.9558 | 198.3062 |  | 7.7295
577 | 2524.5 |  | 46.0908 | 0 |  | 0
578 | 2376 |  | 43.3796 | 0 |  | 0
579 | 2524.5 |  | 46.0908 | 0 |  | 0
580 | 2673 |  | 48.802 | 0 |  | 0
581 | 2970 |  | 54.2245 | 0 |  | 0
582 | 3168 |  | 57.8395 | 0 |  | 0
583 | 3366 |  | 61.4544 | 0 |  | 0
584 | 3564 |  | 65.0694 | 0 |  | 0
585 | 3723.4546 |  | 67.9806 | 38.5454 |  | 1.5024
586 | 3732.1285 |  | 68.139 | 227.8715 |  | 8.8819
587 | 3740.7674 |  | 68.2967 | 417.2326 |  | 16.2628
588 | 3749.3708 |  | 68.4538 | 606.6292 |  | 23.6451
589 | 3757.9382 |  | 68.6102 | 796.0618 |  | 31.0288
590 | 3765.4106 |  | 68.7466 | 986.5894 |  | 38.4551
591 | 3771.2621 |  | 68.8535 | 832.2379 |  | 32.4388
592 | 3777.0819 |  | 68.9597 | 1172.9181 |  | 45.7178
593 | 3782.8692 |  | 69.0654 | 1513.6308 |  | 58.998
594 | 3788.6231 |  | 69.1704 | 1854.3769 |  | 72.2796
595 | 3794.343 |  | 69.2748 | 1440.282 |  | 56.139
596 | 3800.03 |  | 69.3787 | 1026.22 |  | 39.9998
597 | 3805.6852 |  | 69.4819 | 612.1898 |  | 23.8618
598 | 3811.3101 |  | 69.5846 | 198.1899 |  | 7.725
599 | 3601.125 |  | 65.7472 | 0 |  | 0
600 | 2970 |  | 54.2245 | 0 |  | 0
601 | 2524.5 |  | 46.0908 | 0 |  | 0
602 | 2376 |  | 43.3796 | 0 |  | 0
603 | 2524.5 |  | 46.0908 | 0 |  | 0
604 | 2673 |  | 48.802 | 0 |  | 0
605 | 2943 |  | 53.7315 | 0 |  | 0
606 | 3132 |  | 57.1822 | 0 |  | 0
607 | 3321 |  | 60.6328 | 0 |  | 0
608 | 3510 |  | 64.0835 | 0 |  | 0
609 | 3699 |  | 67.5341 | 0 |  | 0
610 | 3785.1332 |  | 69.1067 | 102.8668 |  | 4.0095
611 | 3790.8012 |  | 69.2102 | 286.1988 |  | 11.1554
612 | 3796.4411 |  | 69.3132 | 469.5589 |  | 18.3024
613 | 3802.0525 |  | 69.4156 | 652.9475 |  | 25.4505
614 | 3807.6352 |  | 69.5175 | 562.5077 |  | 21.9253
615 | 3813.1895 |  | 69.6189 | 472.0962 |  | 18.4013
616 | 3818.7159 |  | 69.7198 | 381.7126 |  | 14.8783
617 | 3824.215 |  | 69.8202 | 291.3565 |  | 11.3564
618 | 3829.687 |  | 69.9201 | 201.0273 |  | 7.8356
619 | 3835.1326 |  | 70.0196 | 110.7246 |  | 4.3158
620 | 3840.5521 |  | 70.1185 | 20.4479 |  | 0.79702
621 | 3845.9458 |  | 70.217 | 312.0542 |  | 12.1632
622 | 3712.5 |  | 67.7806 | 0 |  | 0
623 | 3267 |  | 59.6469 | 0 |  | 0
624 | 2821.5 |  | 51.5133 | 0 |  | 0
625 | 2376 |  | 43.3796 | 0 |  | 0
626 | 2376 |  | 43.3796 | 0 |  | 0
627 | 2545.7143 |  | 46.4781 | 0 |  | 0
628 | 2715.4286 |  | 49.5767 | 0 |  | 0
629 | 2885.1429 |  | 52.6752 | 0 |  | 0
630 | 3054.8571 |  | 55.7738 | 0 |  | 0
631 | 3224.5714 |  | 58.8723 | 0 |  | 0
632 | 3394.2857 |  | 61.9708 | 0 |  | 0
633 | 3564 |  | 65.0694 | 0 |  | 0
634 | 3733.7143 |  | 68.1679 | 0 |  | 0
635 | 3795.3094 |  | 69.2925 | 108.1191 |  | 4.2142
636 | 3786.1391 |  | 69.1251 | 287.0038 |  | 11.1868
637 | 3777.0059 |  | 68.9583 | 380.9941 |  | 14.8503
638 | 3767.9097 |  | 68.7922 | 390.0903 |  | 15.2049
639 | 3758.8505 |  | 68.6268 | 823.4352 |  | 32.0957
640 | 3755.6738 |  | 68.5688 | 996.3262 |  | 38.8346
641 | 3760.5163 |  | 68.6573 | 753.8837 |  | 29.3847
642 | 3765.3338 |  | 68.7452 | 511.4662 |  | 19.9358
643 | 3770.1271 |  | 68.8327 | 387.8729 |  | 15.1184
644 | 3774.897 |  | 68.9198 | 26.703 |  | 1.0408
645 | 3564 |  | 65.0694 | 0 |  | 0
646 | 3326.4 |  | 60.7314 | 0 |  | 0
647 | 2673 |  | 48.802 | 0 |  | 0
648 | 2524.5 |  | 46.0908 | 0 |  | 0
649 | 2376 |  | 43.3796 | 0 |  | 0
650 | 2376 |  | 43.3796 | 0 |  | 0
651 | 2524.5 |  | 46.0908 | 0 |  | 0
652 | 2673 |  | 48.802 | 0 |  | 0
653 | 2821.5 |  | 51.5133 | 0 |  | 0
654 | 2970 |  | 54.2245 | 0 |  | 0
655 | 3118.5 |  | 56.9357 | 0 |  | 0
656 | 3267 |  | 59.6469 | 0 |  | 0
657 | 3415.5 |  | 62.3582 | 0 |  | 0
658 | 3564 |  | 65.0694 | 0 |  | 0
659 | 3712.5 |  | 67.7806 | 0 |  | 0
660 | 3717.5011 |  | 67.8719 | 143.4989 |  | 5.5933
661 | 3711.2215 |  | 67.7573 | 298.2785 |  | 11.6262
662 | 3704.9734 |  | 67.6432 | 453.0266 |  | 17.658
663 | 3698.7567 |  | 67.5297 | 310.7433 |  | 12.1121
664 | 3698.4697 |  | 67.5245 | 459.5303 |  | 17.9115
665 | 3706.2076 |  | 67.6657 | 1045.7924 |  | 40.7627
666 | 3713.915 |  | 67.8064 | 889.585 |  | 34.6741
667 | 3721.5917 |  | 67.9466 | 1178.9083 |  | 45.9513
668 | 3729.2375 |  | 68.0862 | 844.5625 |  | 32.9192
669 | 3736.8531 |  | 68.2252 | 510.2469 |  | 19.8883
670 | 3744.4395 |  | 68.3637 | 175.9605 |  | 6.8586
671 | 3593.7 |  | 65.6116 | 0 |  | 0
672 | 3267 |  | 59.6469 | 0 |  | 0

## Spring Autumn
Spring/Autumn
| Hot Sink |  |  | Cold Sink
| Condenser Duty | Factor | Exergy Destruction | Condenser Duty | Factor | Exergy Destruction | Total Exergy Destruction
| Qcond, h | 0.018257 | ED, h | Qcond, c | 0.038978 | ED, c | ED
Total | 2182261.1703 |  | 39842 | 640290.5163 |  | 24957 | 64799
Hours | kWh |  | kWh | kWh |  | kWh | kWh
1 | 2713.95 |  | 49.5497 | 0 |  | 0
2 | 2554.3059 |  | 46.635 | 0 |  | 0
3 | 2713.95 |  | 49.5497 | 0 |  | 0
4 | 2873.5941 |  | 52.4644 | 0 |  | 0
5 | 3272.7044 |  | 59.7511 | 0 |  | 0
6 | 3512.1706 |  | 64.1231 | 0 |  | 0
7 | 3718.4927 |  | 67.89 | 33.144 |  | 1.2919
8 | 3717.5067 |  | 67.872 | 273.5962 |  | 10.6642
9 | 3712.4356 |  | 67.7794 | 518.1335 |  | 20.1957
10 | 3705.1105 |  | 67.6457 | 764.9247 |  | 29.8151
11 | 3697.8219 |  | 67.5126 | 1011.6796 |  | 39.4331
12 | 3690.5694 |  | 67.3802 | 1258.3982 |  | 49.0496
13 | 3683.353 |  | 67.2485 | 1505.0808 |  | 58.6648
14 | 3676.1725 |  | 67.1174 | 1751.7274 |  | 68.2785
15 | 3669.0279 |  | 66.9869 | 1599.2279 |  | 62.3344
16 | 3664.1878 |  | 66.8986 | 1816.9269 |  | 70.8198
17 | 3663.4534 |  | 66.8851 | 2562.6671 |  | 99.8872
18 | 3662.7215 |  | 66.8718 | 2403.7549 |  | 93.6931
19 | 3661.9919 |  | 66.8585 | 2723.7728 |  | 106.1667
20 | 3661.2642 |  | 66.8452 | 2405.2123 |  | 93.7499
21 | 3660.5386 |  | 66.8319 | 2884.8702 |  | 112.4459
22 | 3659.8147 |  | 66.8187 | 2087.3735 |  | 81.3613
23 | 3655.0143 |  | 66.7311 | 1293.9533 |  | 50.4355
24 | 3647.9938 |  | 66.6029 | 502.7532 |  | 19.5962
25 | 2713.95 |  | 49.5497 | 0 |  | 0
26 | 2554.3059 |  | 46.635 | 0 |  | 0
27 | 2745.8788 |  | 50.1326 | 0 |  | 0
28 | 2873.5941 |  | 52.4644 | 0 |  | 0
29 | 3170.076 |  | 57.8774 | 0 |  | 0
30 | 3375.3327 |  | 61.6248 | 0 |  | 0
31 | 3580.5895 |  | 65.3723 | 0 |  | 0
32 | 3610.8818 |  | 65.9253 | 174.9644 |  | 6.8197
33 | 3606.9574 |  | 65.8537 | 384.1455 |  | 14.9732
34 | 3601.0728 |  | 65.7462 | 595.2868 |  | 23.203
35 | 3595.221 |  | 65.6394 | 806.3953 |  | 31.4315
36 | 3589.4018 |  | 65.5332 | 1017.4712 |  | 39.6588
37 | 3583.6152 |  | 65.4275 | 1228.5146 |  | 47.8848
38 | 3577.8609 |  | 65.3224 | 1439.5256 |  | 56.1096
39 | 3572.0508 |  | 65.2164 | 1650.5925 |  | 64.3365
40 | 3567.7202 |  | 65.1373 | 1860.1798 |  | 72.5057
41 | 3567.482 |  | 65.133 | 1700.7738 |  | 66.2925
42 | 3567.2472 |  | 65.1287 | 2020.2969 |  | 78.7468
43 | 3567.0151 |  | 65.1244 | 2339.8172 |  | 91.201
44 | 3566.7849 |  | 65.1202 | 2499.6915 |  | 97.4325
45 | 3566.556 |  | 65.116 | 2978.8528 |  | 116.1092
46 | 3566.3279 |  | 65.1119 | 2180.8603 |  | 85.0052
47 | 3562.0313 |  | 65.0334 | 1386.9363 |  | 54.0598
48 | 3555.535 |  | 64.9148 | 595.212 |  | 23.2001
49 | 2713.95 |  | 49.5497 | 0 |  | 0
50 | 2554.3059 |  | 46.635 | 0 |  | 0
51 | 2713.95 |  | 49.5497 | 0 |  | 0
52 | 2873.5941 |  | 52.4644 | 0 |  | 0
53 | 3217.443 |  | 58.7422 | 0 |  | 0
54 | 3438.4887 |  | 62.7779 | 0 |  | 0
55 | 3520.985 |  | 64.284 | 138.5494 |  | 5.4004
56 | 3521.0149 |  | 64.2846 | 359.5652 |  | 14.0151
57 | 3516.9762 |  | 64.2109 | 584.6496 |  | 22.7884
58 | 3510.7247 |  | 64.0967 | 811.9467 |  | 31.6479
59 | 3504.5058 |  | 63.9832 | 1039.2113 |  | 40.5062
60 | 3498.3195 |  | 63.8702 | 1266.4434 |  | 49.3632
61 | 3492.1655 |  | 63.7579 | 1493.643 |  | 58.2189
62 | 3486.0439 |  | 63.6461 | 1720.8104 |  | 67.0734
63 | 3479.9544 |  | 63.5349 | 1947.9455 |  | 75.9267
64 | 3476.1335 |  | 63.4652 | 1792.1224 |  | 69.853
65 | 3476.4034 |  | 63.4701 | 2079.2119 |  | 81.0431
66 | 3476.6763 |  | 63.4751 | 2366.2983 |  | 92.2331
67 | 3476.9515 |  | 63.4801 | 2908.8132 |  | 113.3792
68 | 3477.2276 |  | 63.4851 | 2908.537 |  | 113.3684
69 | 3477.5044 |  | 63.4902 | 3227.5485 |  | 125.8028
70 | 3477.7818 |  | 63.4953 | 2397.1217 |  | 93.4346
71 | 3473.9893 |  | 63.426 | 1570.7648 |  | 61.225
72 | 3467.9927 |  | 63.3165 | 746.612 |  | 29.1013
73 | 2713.95 |  | 49.5497 | 0 |  | 0
74 | 2554.3059 |  | 46.635 | 0 |  | 0
75 | 2713.95 |  | 49.5497 | 0 |  | 0
76 | 2873.5941 |  | 52.4644 | 0 |  | 0
77 | 3192.8823 |  | 58.2937 | 0 |  | 0
78 | 3405.7411 |  | 62.18 | 0 |  | 0
79 | 3435.8879 |  | 62.7304 | 182.7121 |  | 7.1217
80 | 3436.4325 |  | 62.7403 | 395.0263 |  | 15.3973
81 | 3436.9856 |  | 62.7504 | 607.332 |  | 23.6725
82 | 3437.5468 |  | 62.7607 | 819.6296 |  | 31.9474
83 | 3438.1154 |  | 62.7711 | 1031.9199 |  | 40.222
84 | 3438.6907 |  | 62.7816 | 1244.2033 |  | 48.4963
85 | 3439.2723 |  | 62.7922 | 1456.4806 |  | 56.7704
86 | 3439.8596 |  | 62.8029 | 1668.7522 |  | 65.0443
87 | 3440.452 |  | 62.8137 | 1508.5156 |  | 58.7986
88 | 3441.0496 |  | 62.8246 | 1880.4209 |  | 73.2947
89 | 3441.6513 |  | 62.8356 | 2252.3222 |  | 87.7906
90 | 3442.2559 |  | 62.8467 | 2624.2205 |  | 102.2864
91 | 3442.8626 |  | 62.8577 | 2184.5925 |  | 85.1506
92 | 3443.4723 |  | 62.8689 | 1744.9614 |  | 68.0148
93 | 3444.0863 |  | 62.8801 | 1305.3261 |  | 50.8788
94 | 3444.7058 |  | 62.8914 | 865.6853 |  | 33.7425
95 | 3441.2331 |  | 62.828 | 430.1368 |  | 16.7658
96 | 3192.8823 |  | 58.2937 | 0 |  | 0
97 | 2713.95 |  | 49.5497 | 0 |  | 0
98 | 2554.3059 |  | 46.635 | 0 |  | 0
99 | 2713.95 |  | 49.5497 | 0 |  | 0
100 | 2873.5941 |  | 52.4644 | 0 |  | 0
101 | 3163.8561 |  | 57.7638 | 0 |  | 0
102 | 3367.0395 |  | 61.4734 | 0 |  | 0
103 | 3405.718 |  | 62.1796 | 164.505 |  | 6.412
104 | 3406.6054 |  | 62.1958 | 366.801 |  | 14.2971
105 | 3407.4995 |  | 62.2121 | 569.0903 |  | 22.1819
106 | 3408.3996 |  | 62.2285 | 771.3736 |  | 30.0665
107 | 3409.305 |  | 62.2451 | 973.6516 |  | 37.9508
108 | 3410.215 |  | 62.2617 | 1175.925 |  | 45.835
109 | 3411.1289 |  | 62.2784 | 1378.1946 |  | 53.719
110 | 3412.0462 |  | 62.2951 | 1286.0521 |  | 50.1275
111 | 3412.9668 |  | 62.3119 | 1193.9062 |  | 46.5359
112 | 3413.8911 |  | 62.3288 | 1101.7568 |  | 42.9441
113 | 3414.8191 |  | 62.3457 | 1009.6035 |  | 39.3521
114 | 3415.7511 |  | 62.3627 | 917.4463 |  | 35.7601
115 | 3416.6873 |  | 62.3798 | 825.2849 |  | 32.1678
116 | 3417.6279 |  | 62.397 | 733.1191 |  | 28.5754
117 | 3418.5728 |  | 62.4143 | 1051.4624 |  | 40.9837
118 | 3419.5217 |  | 62.4316 | 571.5812 |  | 22.279
119 | 3416.3466 |  | 62.3736 | 95.824 |  | 3.735
120 | 3033.2382 |  | 55.3791 | 0 |  | 0
121 | 2554.3059 |  | 46.635 | 0 |  | 0
122 | 2554.3059 |  | 46.635 | 0 |  | 0
123 | 2736.7563 |  | 49.9661 | 0 |  | 0
124 | 2919.2067 |  | 53.2971 | 0 |  | 0
125 | 3101.6571 |  | 56.6282 | 0 |  | 0
126 | 3284.1075 |  | 59.9593 | 0 |  | 0
127 | 3383.5081 |  | 61.7741 | 83.0498 |  | 3.2371
128 | 3385.5819 |  | 61.8119 | 263.4265 |  | 10.2678
129 | 3383.5204 |  | 61.7743 | 447.9384 |  | 17.4597
130 | 3379.0875 |  | 61.6934 | 634.8218 |  | 24.744
131 | 3374.682 |  | 61.6129 | 821.6776 |  | 32.0272
132 | 3370.304 |  | 61.533 | 1008.5061 |  | 39.3094
133 | 3365.9532 |  | 61.4536 | 1104.082 |  | 43.0347
134 | 3361.6297 |  | 61.3746 | 1108.4056 |  | 43.2032
135 | 3357.3333 |  | 61.2962 | 1568.828 |  | 61.1495
136 | 3355.4579 |  | 61.2619 | 1753.1538 |  | 68.3341
137 | 3357.7288 |  | 61.3034 | 1495.4523 |  | 58.2895
138 | 3359.9973 |  | 61.3448 | 1237.7532 |  | 48.2449
139 | 3362.2641 |  | 61.3862 | 1107.7712 |  | 43.1785
140 | 3364.5295 |  | 61.4276 | 722.3598 |  | 28.156
141 | 3366.7947 |  | 61.4689 | 464.6641 |  | 18.1116
142 | 3369.0603 |  | 61.5103 | 206.9679 |  | 8.0672
143 | 2873.5941 |  | 52.4644 | 0 |  | 0
144 | 2713.95 |  | 49.5497 | 0 |  | 0
145 | 2554.3059 |  | 46.635 | 0 |  | 0
146 | 2554.3059 |  | 46.635 | 0 |  | 0
147 | 2713.95 |  | 49.5497 | 0 |  | 0
148 | 2873.5941 |  | 52.4644 | 0 |  | 0
149 | 3033.2382 |  | 55.3791 | 0 |  | 0
150 | 3192.8823 |  | 58.2937 | 0 |  | 0
151 | 3345.6978 |  | 61.0838 | 6.8287 |  | 0.26617
152 | 3348.1555 |  | 61.1286 | 164.0151 |  | 6.393
153 | 3346.4667 |  | 61.0978 | 325.348 |  | 12.6814
154 | 3342.3787 |  | 61.0232 | 489.0801 |  | 19.0633
155 | 3338.3169 |  | 60.949 | 652.7861 |  | 25.4442
156 | 3334.2811 |  | 60.8753 | 816.466 |  | 31.8241
157 | 3330.2712 |  | 60.8021 | 980.1199 |  | 38.2029
158 | 3326.2873 |  | 60.7294 | 1143.748 |  | 44.5808
159 | 3322.3291 |  | 60.6571 | 988.062 |  | 38.5125
160 | 3320.8117 |  | 60.6294 | 1149.2235 |  | 44.7942
161 | 3323.4461 |  | 60.6775 | 1785.1656 |  | 69.5819
162 | 3326.0746 |  | 60.7255 | 1622.893 |  | 63.2568
163 | 3328.6969 |  | 60.7734 | 1939.5589 |  | 75.5998
164 | 3331.3128 |  | 60.8211 | 1585.726 |  | 61.8081
165 | 3333.9229 |  | 60.8688 | 1231.8989 |  | 48.0167
166 | 3336.5281 |  | 60.9163 | 878.0766 |  | 34.2255
167 | 3334.9869 |  | 60.8882 | 528.4007 |  | 20.5959
168 | 3331.0563 |  | 60.8164 | 181.1143 |  | 7.0594
169 | 2713.95 |  | 49.5497 | 0 |  | 0
170 | 2554.3059 |  | 46.635 | 0 |  | 0
171 | 2713.95 |  | 49.5497 | 0 |  | 0
172 | 2873.5941 |  | 52.4644 | 0 |  | 0
173 | 3272.7044 |  | 59.7511 | 0 |  | 0
174 | 3313.3102 |  | 60.4924 | 198.8603 |  | 7.7511
175 | 3311.9417 |  | 60.4675 | 439.695 |  | 17.1384
176 | 3314.7239 |  | 60.5183 | 676.379 |  | 26.3638
177 | 3313.3589 |  | 60.4933 | 917.2102 |  | 35.7509
178 | 3309.6029 |  | 60.4248 | 1160.4323 |  | 45.2311
179 | 3305.4308 |  | 60.3486 | 1404.0706 |  | 54.7276
180 | 3300.8438 |  | 60.2648 | 1648.1238 |  | 64.2403
181 | 3296.2831 |  | 60.1816 | 1892.1507 |  | 73.7519
182 | 3291.7486 |  | 60.0988 | 2136.1514 |  | 83.2625
183 | 3287.2402 |  | 60.0165 | 1981.0156 |  | 77.2157
184 | 3285.142 |  | 59.9782 | 2195.9727 |  | 85.5942
185 | 3287.1813 |  | 60.0154 | 2938.9392 |  | 114.5534
186 | 3289.2105 |  | 60.0524 | 2777.2659 |  | 108.2518
187 | 3291.2294 |  | 60.0893 | 3094.5353 |  | 120.6182
188 | 3293.2374 |  | 60.126 | 2773.2391 |  | 108.0948
189 | 3295.2348 |  | 60.1624 | 3250.174 |  | 126.6847
190 | 3297.2213 |  | 60.1987 | 2449.9669 |  | 95.4944
191 | 3295.0772 |  | 60.1596 | 1653.8904 |  | 64.465
192 | 3290.6017 |  | 60.0778 | 860.1453 |  | 33.5266
193 | 2713.95 |  | 49.5497 | 0 |  | 0
194 | 2554.3059 |  | 46.635 | 0 |  | 0
195 | 2745.8788 |  | 50.1326 | 0 |  | 0
196 | 2873.5941 |  | 52.4644 | 0 |  | 0
197 | 3170.076 |  | 57.8774 | 0 |  | 0
198 | 3269.0402 |  | 59.6842 | 106.2926 |  | 4.1431
199 | 3267.0611 |  | 59.648 | 313.5284 |  | 12.2207
200 | 3269.2085 |  | 59.6873 | 516.6377 |  | 20.1374
201 | 3267.2347 |  | 59.6512 | 723.8682 |  | 28.2148
202 | 3262.9414 |  | 59.5728 | 933.4183 |  | 36.3826
203 | 3258.6733 |  | 59.4949 | 1142.9431 |  | 44.5494
204 | 3254.4303 |  | 59.4174 | 1352.4428 |  | 52.7153
205 | 3250.2124 |  | 59.3404 | 1561.9174 |  | 60.8801
206 | 3246.0194 |  | 59.2639 | 1771.3671 |  | 69.044
207 | 3241.8513 |  | 59.1878 | 1980.7919 |  | 77.2069
208 | 3240.0166 |  | 59.1543 | 2187.8834 |  | 85.2789
209 | 3242.2925 |  | 59.1958 | 2025.9634 |  | 78.9676
210 | 3244.5583 |  | 59.2372 | 2342.9858 |  | 91.3245
211 | 3246.8133 |  | 59.2784 | 2660.019 |  | 103.6817
212 | 3249.0566 |  | 59.3193 | 2817.4198 |  | 109.8169
213 | 3251.2876 |  | 59.3601 | 3294.1212 |  | 128.3977
214 | 3253.5056 |  | 59.4006 | 2493.6826 |  | 97.1983
215 | 3251.6213 |  | 59.3662 | 1697.3463 |  | 66.1589
216 | 3247.4782 |  | 59.2905 | 903.2688 |  | 35.2074
217 | 2713.95 |  | 49.5497 | 0 |  | 0
218 | 2554.3059 |  | 46.635 | 0 |  | 0
219 | 2713.95 |  | 49.5497 | 0 |  | 0
220 | 2873.5941 |  | 52.4644 | 0 |  | 0
221 | 3217.443 |  | 58.7422 | 0 |  | 0
222 | 3227.434 |  | 58.9246 | 211.0547 |  | 8.2265
223 | 3225.7001 |  | 58.8929 | 433.8342 |  | 16.9099
224 | 3228.0571 |  | 58.9359 | 652.523 |  | 25.4339
225 | 3226.3249 |  | 58.9043 | 875.3008 |  | 34.1173
226 | 3222.355 |  | 58.8318 | 1100.3165 |  | 42.8879
227 | 3218.409 |  | 58.7598 | 1325.3082 |  | 51.6576
228 | 3214.4869 |  | 58.6882 | 1550.276 |  | 60.4264
229 | 3210.5886 |  | 58.617 | 1775.2199 |  | 69.1942
230 | 3206.7141 |  | 58.5463 | 2000.1402 |  | 77.9611
231 | 3202.8632 |  | 58.476 | 2225.0367 |  | 86.7271
232 | 3201.2569 |  | 58.4466 | 2066.9989 |  | 80.5671
233 | 3203.7218 |  | 58.4916 | 2351.8935 |  | 91.6717
234 | 3206.1753 |  | 58.5364 | 2636.7993 |  | 102.7767
235 | 3208.6168 |  | 58.581 | 3177.1479 |  | 123.8383
236 | 3211.045 |  | 58.6253 | 3174.7196 |  | 123.7436
237 | 3213.4598 |  | 58.6694 | 3491.5931 |  | 136.0947
238 | 3215.861 |  | 58.7133 | 2659.0424 |  | 103.6437
239 | 3214.1972 |  | 58.6829 | 1830.5568 |  | 71.3511
240 | 3210.3649 |  | 58.6129 | 1004.2397 |  | 39.1431
241 | 2713.95 |  | 49.5497 | 0 |  | 0
242 | 2554.3059 |  | 46.635 | 0 |  | 0
243 | 2713.95 |  | 49.5497 | 0 |  | 0
244 | 2873.5941 |  | 52.4644 | 0 |  | 0
245 | 3192.8823 |  | 58.2937 | 0 |  | 0
246 | 3191.8276 |  | 58.2745 | 213.9136 |  | 8.3379
247 | 3190.3144 |  | 58.2469 | 428.2856 |  | 16.6936
248 | 3192.859 |  | 58.2933 | 638.5998 |  | 24.8912
249 | 3195.3989 |  | 58.3397 | 848.9187 |  | 33.089
250 | 3197.9335 |  | 58.386 | 1059.2429 |  | 41.287
251 | 3200.4624 |  | 58.4321 | 1269.5729 |  | 49.4852
252 | 3202.9849 |  | 58.4782 | 1479.9091 |  | 57.6836
253 | 3205.5007 |  | 58.5241 | 1690.2522 |  | 65.8823
254 | 3208.0091 |  | 58.5699 | 1900.6026 |  | 74.0813
255 | 3210.5099 |  | 58.6156 | 1738.4577 |  | 67.7613
256 | 3213.0032 |  | 58.6611 | 2108.4673 |  | 82.1835
257 | 3215.4883 |  | 58.7065 | 2478.4852 |  | 96.6059
258 | 3217.9642 |  | 58.7517 | 2848.5122 |  | 111.0288
259 | 3220.4304 |  | 58.7967 | 2407.0247 |  | 93.8206
260 | 3222.8878 |  | 58.8416 | 1965.546 |  | 76.6127
261 | 3225.3381 |  | 58.8863 | 1524.0744 |  | 59.4051
262 | 3227.7825 |  | 58.9309 | 1082.6086 |  | 42.1977
263 | 3226.1797 |  | 58.9017 | 645.1902 |  | 25.1481
264 | 3192.8823 |  | 58.2937 | 0 |  | 0
265 | 2713.95 |  | 49.5497 | 0 |  | 0
266 | 2554.3059 |  | 46.635 | 0 |  | 0
267 | 2713.95 |  | 49.5497 | 0 |  | 0
268 | 2873.5941 |  | 52.4644 | 0 |  | 0
269 | 3163.8561 |  | 57.7638 | 0 |  | 0
270 | 3204.971 |  | 58.5144 | 162.0685 |  | 6.3171
271 | 3203.5322 |  | 58.4882 | 366.6907 |  | 14.2928
272 | 3206.1505 |  | 58.536 | 567.2559 |  | 22.1104
273 | 3208.7664 |  | 58.5837 | 767.8234 |  | 29.9281
274 | 3211.3795 |  | 58.6314 | 968.3937 |  | 37.7459
275 | 3213.9892 |  | 58.6791 | 1168.9675 |  | 45.5638
276 | 3216.595 |  | 58.7267 | 1369.545 |  | 53.3819
277 | 3219.1965 |  | 58.7742 | 1570.127 |  | 61.2001
278 | 3221.7932 |  | 58.8216 | 1476.3051 |  | 57.5432
279 | 3224.3855 |  | 58.8689 | 1382.4876 |  | 53.8864
280 | 3226.9736 |  | 58.9162 | 1288.6742 |  | 50.2297
281 | 3229.5581 |  | 58.9633 | 1194.8646 |  | 46.5732
282 | 3232.1392 |  | 59.0105 | 1101.0582 |  | 42.9168
283 | 3235.599 |  | 59.0736 | 1006.3733 |  | 39.2262
284 | 3239.0545 |  | 59.1367 | 911.6926 |  | 35.5358
285 | 3242.5059 |  | 59.1997 | 1227.5293 |  | 47.8464
286 | 3245.9531 |  | 59.2627 | 745.1498 |  | 29.0443
287 | 3245.3364 |  | 59.2514 | 266.8342 |  | 10.4006
288 | 3033.2382 |  | 55.3791 | 0 |  | 0
289 | 2554.3059 |  | 46.635 | 0 |  | 0
290 | 2554.3059 |  | 46.635 | 0 |  | 0
291 | 2736.7563 |  | 49.9661 | 0 |  | 0
292 | 2919.2067 |  | 53.2971 | 0 |  | 0
293 | 3101.6571 |  | 56.6282 | 0 |  | 0
294 | 3231.59 |  | 59.0004 | 52.5175 |  | 2.047
295 | 3231.1331 |  | 58.9921 | 235.4248 |  | 9.1763
296 | 3234.7565 |  | 59.0583 | 414.2518 |  | 16.1466
297 | 3234.304 |  | 59.05 | 597.1548 |  | 23.2758
298 | 3231.6338 |  | 59.0012 | 782.2754 |  | 30.4914
299 | 3228.9841 |  | 58.9529 | 967.3756 |  | 37.7062
300 | 3226.3545 |  | 58.9049 | 1152.4555 |  | 44.9202
301 | 3223.7452 |  | 58.8572 | 1246.29 |  | 48.5777
302 | 3221.1561 |  | 58.8099 | 1248.8792 |  | 48.6786
303 | 3218.5869 |  | 58.763 | 1707.5744 |  | 66.5575
304 | 3218.2809 |  | 58.7575 | 1890.3308 |  | 73.681
305 | 3222.0584 |  | 58.8264 | 1631.1227 |  | 63.5776
306 | 3225.8306 |  | 58.8953 | 1371.92 |  | 53.4744
307 | 3229.5982 |  | 58.9641 | 1240.4371 |  | 48.3495
308 | 3233.3618 |  | 59.0328 | 853.5275 |  | 33.2686
309 | 3237.1227 |  | 59.1015 | 594.3361 |  | 23.1659
310 | 3240.8816 |  | 59.1701 | 335.1466 |  | 13.0633
311 | 2873.5941 |  | 52.4644 | 0 |  | 0
312 | 2713.95 |  | 49.5497 | 0 |  | 0
313 | 2554.3059 |  | 46.635 | 0 |  | 0
314 | 2554.3059 |  | 46.635 | 0 |  | 0
315 | 2713.95 |  | 49.5497 | 0 |  | 0
316 | 2873.5941 |  | 52.4644 | 0 |  | 0
317 | 3033.2382 |  | 55.3791 | 0 |  | 0
318 | 3192.8823 |  | 58.2937 | 0 |  | 0
319 | 3229.9261 |  | 58.9701 | 122.6003 |  | 4.7787
320 | 3233.8679 |  | 59.042 | 278.3026 |  | 10.8476
321 | 3233.6993 |  | 59.039 | 438.1153 |  | 17.0768
322 | 3231.2267 |  | 58.9938 | 600.2321 |  | 23.3957
323 | 3228.7734 |  | 58.949 | 762.3295 |  | 29.7139
324 | 3226.3396 |  | 58.9046 | 924.4074 |  | 36.0314
325 | 3223.9251 |  | 58.8605 | 1086.4661 |  | 42.3481
326 | 3221.5297 |  | 58.8168 | 1248.5055 |  | 48.664
327 | 3219.1536 |  | 58.7734 | 1091.2376 |  | 42.5341
328 | 3219.135 |  | 58.773 | 1250.9002 |  | 48.7574
329 | 3223.2405 |  | 58.848 | 1885.3712 |  | 73.4877
330 | 3227.3392 |  | 58.9228 | 1721.6284 |  | 67.1053
331 | 3231.431 |  | 58.9975 | 2036.8249 |  | 79.391
332 | 3235.5152 |  | 59.0721 | 1681.5235 |  | 65.5421
333 | 3239.5928 |  | 59.1466 | 1326.229 |  | 51.6935
334 | 3243.6646 |  | 59.2209 | 970.9401 |  | 37.8451
335 | 3243.6058 |  | 59.2198 | 619.7818 |  | 24.1577
336 | 3241.2014 |  | 59.1759 | 270.9692 |  | 10.5618
337 | 2713.95 |  | 49.5497 | 0 |  | 0
338 | 2554.3059 |  | 46.635 | 0 |  | 0
339 | 2713.95 |  | 49.5497 | 0 |  | 0
340 | 2873.5941 |  | 52.4644 | 0 |  | 0
341 | 3233.8835 |  | 59.0423 | 38.8209 |  | 1.5132
342 | 3231.5721 |  | 59.0001 | 280.5984 |  | 10.9371
343 | 3231.6719 |  | 59.0019 | 519.9648 |  | 20.2671
344 | 3235.9147 |  | 59.0794 | 755.1882 |  | 29.4356
345 | 3236.0123 |  | 59.0812 | 994.5568 |  | 38.7657
346 | 3233.7235 |  | 59.0394 | 1236.3118 |  | 48.1887
347 | 3231.4533 |  | 58.9979 | 1478.0482 |  | 57.6111
348 | 3229.2016 |  | 58.9568 | 1719.766 |  | 67.0327
349 | 3226.9684 |  | 58.9161 | 1961.4654 |  | 76.4536
350 | 3224.7535 |  | 58.8756 | 2203.1465 |  | 85.8738
351 | 3222.5569 |  | 58.8355 | 2045.6989 |  | 79.7369
352 | 3222.7802 |  | 58.8396 | 2258.3344 |  | 88.0249
353 | 3227.1438 |  | 58.9193 | 2998.9768 |  | 116.8936
354 | 3231.4944 |  | 58.9987 | 2834.982 |  | 110.5014
355 | 3235.832 |  | 59.0779 | 3149.9326 |  | 122.7775
356 | 3240.1561 |  | 59.1568 | 2826.3203 |  | 110.1638
357 | 3244.4669 |  | 59.2355 | 3300.9419 |  | 128.6635
358 | 3248.764 |  | 59.314 | 2498.4242 |  | 97.3831
359 | 3248.9114 |  | 59.3167 | 1700.0562 |  | 66.2645
360 | 3246.6768 |  | 59.2759 | 904.0702 |  | 35.2387
361 | 2713.95 |  | 49.5497 | 0 |  | 0
362 | 2554.3059 |  | 46.635 | 0 |  | 0
363 | 2745.8788 |  | 50.1326 | 0 |  | 0
364 | 2873.5941 |  | 52.4644 | 0 |  | 0
365 | 3170.076 |  | 57.8774 | 0 |  | 0
366 | 3238.0019 |  | 59.1175 | 137.3308 |  | 5.3529
367 | 3238.289 |  | 59.1227 | 342.3004 |  | 13.3421
368 | 3242.7252 |  | 59.2037 | 543.121 |  | 21.1697
369 | 3243.0072 |  | 59.2089 | 748.0957 |  | 29.1591
370 | 3240.8801 |  | 59.1701 | 955.4795 |  | 37.2425
371 | 3238.7708 |  | 59.1315 | 1162.8455 |  | 45.3252
372 | 3236.6793 |  | 59.0934 | 1370.1938 |  | 53.4072
373 | 3234.6054 |  | 59.0555 | 1577.5244 |  | 61.4885
374 | 3232.5491 |  | 59.018 | 1784.8375 |  | 69.5691
375 | 3230.5103 |  | 58.9807 | 1992.133 |  | 77.649
376 | 3230.9088 |  | 58.988 | 2196.9911 |  | 85.6339
377 | 3235.4523 |  | 59.071 | 2032.8036 |  | 79.2342
378 | 3239.9826 |  | 59.1537 | 2347.5614 |  | 91.5028
379 | 3244.4992 |  | 59.2361 | 2662.3331 |  | 103.7719
380 | 3249.0011 |  | 59.3183 | 2817.4753 |  | 109.819
381 | 3253.4875 |  | 59.4002 | 3291.9212 |  | 128.3119
382 | 3257.9579 |  | 59.4818 | 2489.2303 |  | 97.0248
383 | 3258.2714 |  | 59.4876 | 1690.6962 |  | 65.8997
384 | 3256.1869 |  | 59.4495 | 894.5601 |  | 34.868
385 | 2713.95 |  | 49.5497 | 0 |  | 0
386 | 2554.3059 |  | 46.635 | 0 |  | 0
387 | 2713.95 |  | 49.5497 | 0 |  | 0
388 | 2873.5941 |  | 52.4644 | 0 |  | 0
389 | 3217.443 |  | 58.7422 | 0 |  | 0
390 | 3248.4914 |  | 59.309 | 189.9973 |  | 7.4057
391 | 3248.9285 |  | 59.317 | 410.6059 |  | 16.0045
392 | 3253.5143 |  | 59.4007 | 627.0658 |  | 24.4417
393 | 3253.9425 |  | 59.4085 | 847.6833 |  | 33.0408
394 | 3251.9576 |  | 59.3723 | 1070.7139 |  | 41.7341
395 | 3249.9898 |  | 59.3364 | 1293.7273 |  | 50.4267
396 | 3248.0391 |  | 59.3008 | 1516.7238 |  | 59.1186
397 | 3246.1052 |  | 59.2655 | 1739.7033 |  | 67.8098
398 | 3244.1883 |  | 59.2305 | 1962.6659 |  | 76.5004
399 | 3242.2882 |  | 59.1958 | 2185.6118 |  | 85.1904
400 | 3242.8174 |  | 59.2054 | 2025.4385 |  | 78.9472
401 | 3247.4871 |  | 59.2907 | 2308.1281 |  | 89.9658
402 | 3252.141 |  | 59.3756 | 2590.8336 |  | 100.985
403 | 3256.7781 |  | 59.4603 | 3128.9865 |  | 121.9611
404 | 3261.3972 |  | 59.5446 | 3124.3675 |  | 121.781
405 | 3265.9978 |  | 59.6286 | 3439.0551 |  | 134.0469
406 | 3270.5797 |  | 59.7123 | 2604.3238 |  | 101.5109
407 | 3271.0084 |  | 59.7201 | 1773.7456 |  | 69.1367
408 | 3269.0569 |  | 59.6845 | 945.5478 |  | 36.8554
409 | 2713.95 |  | 49.5497 | 0 |  | 0
410 | 2554.3059 |  | 46.635 | 0 |  | 0
411 | 2713.95 |  | 49.5497 | 0 |  | 0
412 | 2873.5941 |  | 52.4644 | 0 |  | 0
413 | 3192.8823 |  | 58.2937 | 0 |  | 0
414 | 3262.3117 |  | 59.5613 | 143.4294 |  | 5.5906
415 | 3262.8487 |  | 59.5711 | 355.7512 |  | 13.8664
416 | 3267.5234 |  | 59.6565 | 563.9354 |  | 21.981
417 | 3272.1865 |  | 59.7416 | 772.1311 |  | 30.096
418 | 3276.8374 |  | 59.8265 | 980.339 |  | 38.2115
419 | 3281.4754 |  | 59.9112 | 1188.5599 |  | 46.3275
420 | 3286.0998 |  | 59.9956 | 1396.7943 |  | 54.444
421 | 3290.71 |  | 60.0798 | 1605.0429 |  | 62.5611
422 | 3295.3053 |  | 60.1637 | 1813.3064 |  | 70.6787
423 | 3299.8853 |  | 60.2473 | 1649.0823 |  | 64.2776
424 | 3304.45 |  | 60.3307 | 2017.0205 |  | 78.6191
425 | 3308.9985 |  | 60.4137 | 2384.975 |  | 92.9611
426 | 3313.5297 |  | 60.4964 | 2752.9467 |  | 107.3039
427 | 3318.0429 |  | 60.5788 | 2309.4122 |  | 90.0158
428 | 3322.539 |  | 60.6609 | 1865.8948 |  | 72.7285
429 | 3327.0194 |  | 60.7427 | 1422.3931 |  | 55.4418
430 | 3331.4853 |  | 60.8243 | 978.9058 |  | 38.1556
431 | 3331.8063 |  | 60.8301 | 539.5635 |  | 21.031
432 | 3192.8823 |  | 58.2937 | 0 |  | 0
433 | 2713.95 |  | 49.5497 | 0 |  | 0
434 | 2554.3059 |  | 46.635 | 0 |  | 0
435 | 2713.95 |  | 49.5497 | 0 |  | 0
436 | 2873.5941 |  | 52.4644 | 0 |  | 0
437 | 3163.8561 |  | 57.7638 | 0 |  | 0
438 | 3323.7844 |  | 60.6837 | 43.2551 |  | 1.686
439 | 3324.2047 |  | 60.6913 | 246.0183 |  | 9.5893
440 | 3328.7557 |  | 60.7744 | 444.6507 |  | 17.3315
441 | 3333.2943 |  | 60.8573 | 643.2955 |  | 25.0743
442 | 3337.8198 |  | 60.9399 | 841.9534 |  | 32.8175
443 | 3342.3317 |  | 61.0223 | 1040.6249 |  | 40.5613
444 | 3346.8293 |  | 61.1044 | 1239.3108 |  | 48.3056
445 | 3351.3119 |  | 61.1863 | 1438.0116 |  | 56.0506
446 | 3355.7792 |  | 61.2678 | 1342.3191 |  | 52.3207
447 | 3360.2312 |  | 61.3491 | 1246.6419 |  | 48.5914
448 | 3364.6682 |  | 61.4301 | 1150.9797 |  | 44.8627
449 | 3369.0905 |  | 61.5108 | 1055.3322 |  | 41.1345
450 | 3373.4983 |  | 61.5913 | 959.6991 |  | 37.407
451 | 3377.892 |  | 61.6715 | 864.0803 |  | 33.68
452 | 3382.2718 |  | 61.7515 | 768.4753 |  | 29.9535
453 | 3386.6377 |  | 61.8312 | 1083.3975 |  | 42.2285
454 | 3390.9895 |  | 61.9107 | 600.1134 |  | 23.3911
455 | 3391.2013 |  | 61.9145 | 120.9693 |  | 4.7151
456 | 3033.2382 |  | 55.3791 | 0 |  | 0
457 | 2554.3059 |  | 46.635 | 0 |  | 0
458 | 2554.3059 |  | 46.635 | 0 |  | 0
459 | 2736.7563 |  | 49.9661 | 0 |  | 0
460 | 2919.2067 |  | 53.2971 | 0 |  | 0
461 | 3101.6571 |  | 56.6282 | 0 |  | 0
462 | 3284.1075 |  | 59.9593 | 0 |  | 0
463 | 3384.5242 |  | 61.7926 | 82.0337 |  | 3.1975
464 | 3388.9432 |  | 61.8733 | 260.0651 |  | 10.1368
465 | 3389.2264 |  | 61.8785 | 442.2324 |  | 17.2373
466 | 3387.1664 |  | 61.8409 | 626.7428 |  | 24.4291
467 | 3385.123 |  | 61.8036 | 811.2366 |  | 31.6202
468 | 3383.0962 |  | 61.7665 | 995.7139 |  | 38.8108
469 | 3381.0857 |  | 61.7298 | 1088.9495 |  | 42.4449
470 | 3379.0917 |  | 61.6934 | 1090.9436 |  | 42.5226
471 | 3377.1139 |  | 61.6573 | 1549.0474 |  | 60.3785
472 | 3377.4806 |  | 61.664 | 1731.1311 |  | 67.4757
473 | 3381.9567 |  | 61.7457 | 1471.2244 |  | 57.3451
474 | 3386.4156 |  | 61.8272 | 1211.335 |  | 47.2152
475 | 3390.8579 |  | 61.9083 | 1079.1774 |  | 42.064
476 | 3395.2842 |  | 61.9891 | 691.6052 |  | 26.9573
477 | 3399.6956 |  | 62.0696 | 431.7632 |  | 16.8292
478 | 3404.0928 |  | 62.1499 | 171.9354 |  | 6.7017
479 | 2873.5941 |  | 52.4644 | 0 |  | 0
480 | 2713.95 |  | 49.5497 | 0 |  | 0
481 | 2554.3059 |  | 46.635 | 0 |  | 0
482 | 2554.3059 |  | 46.635 | 0 |  | 0
483 | 2713.95 |  | 49.5497 | 0 |  | 0
484 | 2873.5941 |  | 52.4644 | 0 |  | 0
485 | 3033.2382 |  | 55.3791 | 0 |  | 0
486 | 3192.8823 |  | 58.2937 | 0 |  | 0
487 | 3352.5264 |  | 61.2084 | 0 |  | 0
488 | 3405.6189 |  | 62.1778 | 106.5516 |  | 4.1531
489 | 3405.9413 |  | 62.1836 | 265.8734 |  | 10.3632
490 | 3403.9746 |  | 62.1477 | 427.4842 |  | 16.6624
491 | 3402.0239 |  | 62.1121 | 589.079 |  | 22.961
492 | 3400.0892 |  | 62.0768 | 750.6578 |  | 29.259
493 | 3398.1704 |  | 62.0418 | 912.2207 |  | 35.5564
494 | 3396.2675 |  | 62.007 | 1073.7678 |  | 41.8531
495 | 3394.3804 |  | 61.9726 | 916.0108 |  | 35.7041
496 | 3394.7812 |  | 61.9799 | 1075.254 |  | 41.9111
497 | 3399.2687 |  | 62.0618 | 1709.3431 |  | 66.6265
498 | 3403.7379 |  | 62.1434 | 1545.2297 |  | 60.2297
499 | 3408.1891 |  | 62.2247 | 1860.0668 |  | 72.5013
500 | 3412.6219 |  | 62.3056 | 1504.4169 |  | 58.6389
501 | 3417.0373 |  | 62.3862 | 1148.7845 |  | 44.7771
502 | 3421.4364 |  | 62.4665 | 793.1682 |  | 30.916
503 | 3421.7389 |  | 62.4721 | 441.6487 |  | 17.2145
504 | 3419.7979 |  | 62.4366 | 92.3726 |  | 3.6005
505 | 2713.95 |  | 49.5497 | 0 |  | 0
506 | 2554.3059 |  | 46.635 | 0 |  | 0
507 | 2713.95 |  | 49.5497 | 0 |  | 0
508 | 2873.5941 |  | 52.4644 | 0 |  | 0
509 | 3272.7044 |  | 59.7511 | 0 |  | 0
510 | 3414.884 |  | 62.3469 | 97.2866 |  | 3.792
511 | 3415.2647 |  | 62.3539 | 336.3721 |  | 13.111
512 | 3419.7217 |  | 62.4352 | 571.3812 |  | 22.2712
513 | 3420.0886 |  | 62.4419 | 810.4805 |  | 31.5908
514 | 3418.2245 |  | 62.4079 | 1051.8108 |  | 40.9973
515 | 3416.3759 |  | 62.3742 | 1293.1256 |  | 50.4032
516 | 3414.5426 |  | 62.3407 | 1534.425 |  | 59.8085
517 | 3412.7247 |  | 62.3075 | 1775.709 |  | 69.2133
518 | 3410.9222 |  | 62.2746 | 2016.9778 |  | 78.6174
519 | 3409.1348 |  | 62.2419 | 1859.121 |  | 72.4645
520 | 3409.5766 |  | 62.25 | 2071.538 |  | 80.744
521 | 3414.0795 |  | 62.3322 | 2812.041 |  | 109.6072
522 | 3418.5632 |  | 62.4141 | 2647.9132 |  | 103.2099
523 | 3423.0278 |  | 62.4956 | 2962.7368 |  | 115.481
524 | 3427.4731 |  | 62.5768 | 2639.0034 |  | 102.8626
525 | 3431.8994 |  | 62.6576 | 3113.5094 |  | 121.3578
526 | 3436.3065 |  | 62.738 | 2310.8817 |  | 90.0731
527 | 3436.6418 |  | 62.7442 | 1512.3258 |  | 58.9472
528 | 3434.7986 |  | 62.7105 | 715.9484 |  | 27.9061
529 | 2713.95 |  | 49.5497 | 0 |  | 0
530 | 2554.3059 |  | 46.635 | 0 |  | 0
531 | 2745.8788 |  | 50.1326 | 0 |  | 0
532 | 2873.5941 |  | 52.4644 | 0 |  | 0
533 | 3170.076 |  | 57.8774 | 0 |  | 0
534 | 3375.3327 |  | 61.6248 | 0 |  | 0
535 | 3431.0453 |  | 62.642 | 149.5441 |  | 5.8289
536 | 3435.5212 |  | 62.7237 | 350.325 |  | 13.6549
537 | 3435.9303 |  | 62.7312 | 555.1726 |  | 21.6394
538 | 3434.1587 |  | 62.6988 | 762.2009 |  | 29.7089
539 | 3432.4021 |  | 62.6667 | 969.2143 |  | 37.7779
540 | 3430.6603 |  | 62.6349 | 1176.2127 |  | 45.8462
541 | 3428.9334 |  | 62.6034 | 1383.1964 |  | 53.914
542 | 3427.2213 |  | 62.5722 | 1590.1652 |  | 61.9812
543 | 3425.5239 |  | 62.5412 | 1797.1193 |  | 70.0478
544 | 3426.0219 |  | 62.5503 | 2001.8781 |  | 78.0288
545 | 3430.57 |  | 62.6333 | 1837.6859 |  | 71.629
546 | 3435.1034 |  | 62.7161 | 2152.4406 |  | 83.8974
547 | 3439.6218 |  | 62.7986 | 2467.2105 |  | 96.1665
548 | 3444.1242 |  | 62.8808 | 2622.3522 |  | 102.2136
549 | 3448.6102 |  | 62.9627 | 3096.7986 |  | 120.7065
550 | 3453.0793 |  | 63.0443 | 2294.1089 |  | 89.4194
551 | 3453.4854 |  | 63.0517 | 1495.4822 |  | 58.2906
552 | 3451.7287 |  | 63.0196 | 699.0183 |  | 27.2462
553 | 2713.95 |  | 49.5497 | 0 |  | 0
554 | 2554.3059 |  | 46.635 | 0 |  | 0
555 | 2713.95 |  | 49.5497 | 0 |  | 0
556 | 2873.5941 |  | 52.4644 | 0 |  | 0
557 | 3217.443 |  | 58.7422 | 0 |  | 0
558 | 3438.4887 |  | 62.7779 | 0 |  | 0
559 | 3448.6547 |  | 62.9635 | 210.8796 |  | 8.2196
560 | 3453.2126 |  | 63.0467 | 427.3674 |  | 16.6579
561 | 3453.7047 |  | 63.0557 | 647.9211 |  | 25.2545
562 | 3452.0142 |  | 63.0248 | 870.6572 |  | 33.9363
563 | 3450.3383 |  | 62.9942 | 1093.3789 |  | 42.6175
564 | 3448.6767 |  | 62.9639 | 1316.0862 |  | 51.2982
565 | 3447.0295 |  | 62.9338 | 1538.7791 |  | 59.9783
566 | 3445.3965 |  | 62.904 | 1761.4577 |  | 68.6578
567 | 3443.7778 |  | 62.8744 | 1984.1221 |  | 77.3368
568 | 3444.3665 |  | 62.8852 | 1823.8893 |  | 71.0912
569 | 3449.0121 |  | 62.97 | 2106.6031 |  | 82.1108
570 | 3453.6445 |  | 63.0546 | 2389.3302 |  | 93.1309
571 | 3458.2628 |  | 63.1389 | 2927.5019 |  | 114.1076
572 | 3462.8659 |  | 63.2229 | 2922.8988 |  | 113.9282
573 | 3467.4535 |  | 63.3067 | 3237.5994 |  | 126.1946
574 | 3472.0257 |  | 63.3902 | 2402.8778 |  | 93.6589
575 | 3472.527 |  | 63.3993 | 1572.227 |  | 61.282
576 | 3470.844 |  | 63.3686 | 743.7606 |  | 28.9902
577 | 2713.95 |  | 49.5497 | 0 |  | 0
578 | 2554.3059 |  | 46.635 | 0 |  | 0
579 | 2713.95 |  | 49.5497 | 0 |  | 0
580 | 2873.5941 |  | 52.4644 | 0 |  | 0
581 | 3192.8823 |  | 58.2937 | 0 |  | 0
582 | 3405.7411 |  | 62.18 | 0 |  | 0
583 | 3468.6394 |  | 63.3283 | 149.9606 |  | 5.8451
584 | 3473.3183 |  | 63.4138 | 358.1405 |  | 13.9595
585 | 3477.9904 |  | 63.4991 | 566.3272 |  | 22.0742
586 | 3482.6551 |  | 63.5842 | 774.5213 |  | 30.1891
587 | 3487.3121 |  | 63.6693 | 982.7232 |  | 38.3044
588 | 3491.9606 |  | 63.7541 | 1190.9335 |  | 46.42
589 | 3496.6003 |  | 63.8388 | 1399.1526 |  | 54.5359
590 | 3501.2304 |  | 63.9234 | 1607.3813 |  | 62.6522
591 | 3505.8508 |  | 64.0077 | 1443.1168 |  | 56.2495
592 | 3510.4615 |  | 64.0919 | 1811.009 |  | 70.5892
593 | 3515.0619 |  | 64.1759 | 2178.9116 |  | 84.9292
594 | 3519.6508 |  | 64.2597 | 2546.8256 |  | 99.2697
595 | 3524.2278 |  | 64.3432 | 2103.2273 |  | 81.9792
596 | 3528.7938 |  | 64.4266 | 1659.64 |  | 64.6891
597 | 3533.3503 |  | 64.5098 | 1216.0622 |  | 47.3995
598 | 3537.8988 |  | 64.5928 | 772.4924 |  | 30.1101
599 | 3538.3447 |  | 64.601 | 333.0251 |  | 12.9806
600 | 3192.8823 |  | 58.2937 | 0 |  | 0
601 | 2713.95 |  | 49.5497 | 0 |  | 0
602 | 2554.3059 |  | 46.635 | 0 |  | 0
603 | 2713.95 |  | 49.5497 | 0 |  | 0
604 | 2873.5941 |  | 52.4644 | 0 |  | 0
605 | 3163.8561 |  | 57.7638 | 0 |  | 0
606 | 3367.0395 |  | 61.4734 | 0 |  | 0
607 | 3535.4216 |  | 64.5476 | 34.8014 |  | 1.3565
608 | 3540.1005 |  | 64.633 | 233.3059 |  | 9.0938
609 | 3544.7738 |  | 64.7184 | 431.816 |  | 16.8312
610 | 3549.4409 |  | 64.8036 | 630.3323 |  | 24.569
611 | 3554.101 |  | 64.8887 | 828.8556 |  | 32.307
612 | 3558.7536 |  | 64.9736 | 1027.3865 |  | 40.0453
613 | 3563.3978 |  | 65.0584 | 1225.9257 |  | 47.7839
614 | 3568.0333 |  | 65.143 | 1130.065 |  | 44.0475
615 | 3572.6601 |  | 65.2275 | 1034.213 |  | 40.3114
616 | 3577.2785 |  | 65.3118 | 938.3694 |  | 36.5756
617 | 3581.8886 |  | 65.396 | 842.5341 |  | 32.8401
618 | 3586.4907 |  | 65.48 | 746.7068 |  | 29.105
619 | 3591.085 |  | 65.5639 | 650.8872 |  | 25.3702
620 | 3595.6718 |  | 65.6476 | 555.0752 |  | 21.6356
621 | 3600.251 |  | 65.7312 | 869.7842 |  | 33.9023
622 | 3604.8223 |  | 65.8147 | 386.2806 |  | 15.0564
623 | 3512.1706 |  | 64.1231 | 0 |  | 0
624 | 3033.2382 |  | 55.3791 | 0 |  | 0
625 | 2554.3059 |  | 46.635 | 0 |  | 0
626 | 2554.3059 |  | 46.635 | 0 |  | 0
627 | 2736.7563 |  | 49.9661 | 0 |  | 0
628 | 2919.2067 |  | 53.2971 | 0 |  | 0
629 | 3101.6571 |  | 56.6282 | 0 |  | 0
630 | 3284.1075 |  | 59.9593 | 0 |  | 0
631 | 3466.558 |  | 63.2903 | 0 |  | 0
632 | 3608.3644 |  | 65.8794 | 40.644 |  | 1.5842
633 | 3608.8739 |  | 65.8887 | 222.5849 |  | 8.6759
634 | 3606.9224 |  | 65.853 | 406.9868 |  | 15.8635
635 | 3604.9856 |  | 65.8177 | 591.374 |  | 23.0505
636 | 3603.0634 |  | 65.7826 | 775.7466 |  | 30.2369
637 | 3601.1558 |  | 65.7478 | 868.8794 |  | 33.867
638 | 3599.2627 |  | 65.7132 | 870.7725 |  | 33.9408
639 | 3597.3841 |  | 65.6789 | 1328.7772 |  | 51.7928
640 | 3598.0094 |  | 65.6903 | 1510.6023 |  | 58.88
641 | 3602.8035 |  | 65.7778 | 1250.3777 |  | 48.737
642 | 3607.5854 |  | 65.8651 | 990.1651 |  | 38.5945
643 | 3612.3561 |  | 65.9522 | 857.6792 |  | 33.4305
644 | 3617.1158 |  | 66.0391 | 469.7735 |  | 18.3107
645 | 3621.8657 |  | 66.1259 | 209.5931 |  | 8.1695
646 | 3576.0282 |  | 65.289 | 0 |  | 0
647 | 2873.5941 |  | 52.4644 | 0 |  | 0
648 | 2713.95 |  | 49.5497 | 0 |  | 0
649 | 2554.3059 |  | 46.635 | 0 |  | 0
650 | 2554.3059 |  | 46.635 | 0 |  | 0
651 | 2713.95 |  | 49.5497 | 0 |  | 0
652 | 2873.5941 |  | 52.4644 | 0 |  | 0
653 | 3033.2382 |  | 55.3791 | 0 |  | 0
654 | 3192.8823 |  | 58.2937 | 0 |  | 0
655 | 3352.5264 |  | 61.2084 | 0 |  | 0
656 | 3512.1706 |  | 64.1231 | 0 |  | 0
657 | 3635.162 |  | 66.3686 | 36.6527 |  | 1.4286
658 | 3633.226 |  | 66.3333 | 198.2328 |  | 7.7267
659 | 3631.3044 |  | 66.2982 | 359.7985 |  | 14.0242
660 | 3629.3973 |  | 66.2634 | 521.3498 |  | 20.3211
661 | 3627.5044 |  | 66.2288 | 682.8867 |  | 26.6174
662 | 3625.6259 |  | 66.1945 | 844.4094 |  | 32.9132
663 | 3623.7616 |  | 66.1605 | 686.6296 |  | 26.7633
664 | 3624.4788 |  | 66.1736 | 845.5564 |  | 32.9579
665 | 3629.3901 |  | 66.2632 | 1479.2216 |  | 57.6568
666 | 3634.2864 |  | 66.3526 | 1314.6812 |  | 51.2434
667 | 3639.1674 |  | 66.4417 | 1629.0885 |  | 63.4983
668 | 3644.0326 |  | 66.5306 | 1273.0061 |  | 49.619
669 | 3648.8829 |  | 66.6191 | 916.9388 |  | 35.7403
670 | 3653.7193 |  | 66.7074 | 560.8854 |  | 21.8621
671 | 3654.3441 |  | 66.7188 | 209.0435 |  | 8.1481
672 | 3512.1706 |  | 64.1231 | 0 |  | 0

## Summer
Summer
| Hot Sink |  |  | Cold Sink
| Condenser Duty | Factor | Exergy Destruction | Condenser Duty | Factor | Exergy Destruction | Total Exergy Destruction
| Qcond, h | 0.018257 | ED, h | Qcond, c | 0.038978 | ED, c | ED
Total | 1999013.7215 |  | 36497 | 1028260.9548 |  | 40079 | 76576
Hours | kWh |  | kWh | kWh |  | kWh | kWh
1 | 2910.796 |  | 53.1436 | 0 |  | 0
2 | 2739.5727 |  | 50.0175 | 0 |  | 0
3 | 2910.796 |  | 53.1436 | 0 |  | 0
4 | 3082.0192 |  | 56.2697 | 0 |  | 0
5 | 3510.0775 |  | 64.0849 | 0 |  | 0
6 | 3720.8569 |  | 67.9332 | 46.0556 |  | 1.7951
7 | 3713.486 |  | 67.7986 | 310.2613 |  | 12.0933
8 | 3706.1516 |  | 67.6647 | 574.4306 |  | 22.3901
9 | 3698.8536 |  | 67.5315 | 838.5636 |  | 32.6854
10 | 3691.5919 |  | 67.3989 | 1102.6603 |  | 42.9793
11 | 3684.3662 |  | 67.267 | 1366.7209 |  | 53.2718
12 | 3677.1765 |  | 67.1357 | 1630.7455 |  | 63.5629
13 | 3670.0228 |  | 67.0051 | 1894.7342 |  | 73.8526
14 | 3662.9047 |  | 66.8751 | 2158.6872 |  | 84.1409
15 | 3655.8223 |  | 66.7458 | 1994.5463 |  | 77.7431
16 | 3648.7755 |  | 66.6172 | 2229.8909 |  | 86.9163
17 | 3642.5575 |  | 66.5036 | 3035.1509 |  | 118.3036
18 | 3636.4613 |  | 66.3923 | 2870.0238 |  | 111.8673
19 | 3630.3986 |  | 66.2816 | 3218.5331 |  | 125.4514
20 | 3624.3693 |  | 66.1716 | 2882.1158 |  | 112.3386
21 | 3618.3733 |  | 66.0621 | 3401.7817 |  | 132.594
22 | 3612.4104 |  | 65.9532 | 2551.6281 |  | 99.4569
23 | 3605.9515 |  | 65.8353 | 1701.9705 |  | 66.3391
24 | 3599.1741 |  | 65.7116 | 852.6315 |  | 33.2337
25 | 2910.796 |  | 53.1436 | 0 |  | 0
26 | 2739.5727 |  | 50.0175 | 0 |  | 0
27 | 2945.0406 |  | 53.7688 | 0 |  | 0
28 | 3082.0192 |  | 56.2697 | 0 |  | 0
29 | 3400.0054 |  | 62.0753 | 0 |  | 0
30 | 3565.0445 |  | 65.0885 | 55.1051 |  | 2.1479
31 | 3558.4792 |  | 64.9686 | 281.8146 |  | 10.9845
32 | 3551.9478 |  | 64.8493 | 508.4903 |  | 19.8198
33 | 3545.4499 |  | 64.7307 | 735.1324 |  | 28.6539
34 | 3538.9856 |  | 64.6127 | 961.7409 |  | 37.4866
35 | 3532.5547 |  | 64.4953 | 1188.316 |  | 46.318
36 | 3526.1572 |  | 64.3785 | 1414.8578 |  | 55.1481
37 | 3519.7928 |  | 64.2623 | 1641.3664 |  | 63.9769
38 | 3513.4615 |  | 64.1467 | 1867.8419 |  | 72.8044
39 | 3507.1632 |  | 64.0317 | 2094.2845 |  | 81.6306
40 | 3500.8978 |  | 63.9173 | 2320.6941 |  | 90.4556
41 | 3494.9297 |  | 63.8083 | 2155.4389 |  | 84.0143
42 | 3489.6107 |  | 63.7112 | 2503.2045 |  | 97.5695
43 | 3484.3225 |  | 63.6147 | 2850.9393 |  | 111.1234
44 | 3479.0651 |  | 63.5187 | 3027.42 |  | 118.0022
45 | 3473.8383 |  | 63.4233 | 3546.3166 |  | 138.2277
46 | 3468.6421 |  | 63.3284 | 2695.3964 |  | 105.0607
47 | 3463.4763 |  | 63.2341 | 1844.4457 |  | 71.8925
48 | 3458.2526 |  | 63.1387 | 993.5529 |  | 38.7265
49 | 2910.796 |  | 53.1436 | 0 |  | 0
50 | 2739.5727 |  | 50.0175 | 0 |  | 0
51 | 2910.796 |  | 53.1436 | 0 |  | 0
52 | 3082.0192 |  | 56.2697 | 0 |  | 0
53 | 3432.9858 |  | 62.6774 | 17.8221 |  | 0.69467
54 | 3427.137 |  | 62.5706 | 260.7493 |  | 10.1634
55 | 3421.3195 |  | 62.4644 | 503.6451 |  | 19.631
56 | 3416.3267 |  | 62.3733 | 745.7164 |  | 29.0664
57 | 3411.4516 |  | 62.2842 | 987.6699 |  | 38.4972
58 | 3406.6057 |  | 62.1958 | 1229.5942 |  | 47.9269
59 | 3401.7891 |  | 62.1078 | 1471.4892 |  | 57.3554
60 | 3397.0016 |  | 62.0204 | 1713.3551 |  | 66.7828
61 | 3392.2431 |  | 61.9335 | 1955.192 |  | 76.2091
62 | 3387.5136 |  | 61.8472 | 2196.9999 |  | 85.6343
63 | 3382.8128 |  | 61.7614 | 2438.7791 |  | 95.0583
64 | 3377.2592 |  | 61.66 | 2273.1094 |  | 88.6008
65 | 3371.7359 |  | 61.5591 | 2586.8346 |  | 100.8292
66 | 3366.2428 |  | 61.4589 | 2900.5297 |  | 113.0563
67 | 3360.7797 |  | 61.3591 | 3488.1519 |  | 135.9606
68 | 3355.3466 |  | 61.2599 | 3493.585 |  | 136.1723
69 | 3349.9434 |  | 61.1613 | 3841.4349 |  | 149.7307
70 | 3344.6581 |  | 61.0648 | 2956.359 |  | 115.2324
71 | 3340.1956 |  | 60.9833 | 2070.4604 |  | 80.702
72 | 3335.761 |  | 60.9023 | 1184.5339 |  | 46.1705
73 | 2910.796 |  | 53.1436 | 0 |  | 0
74 | 2739.5727 |  | 50.0175 | 0 |  | 0
75 | 2910.796 |  | 53.1436 | 0 |  | 0
76 | 3082.0192 |  | 56.2697 | 0 |  | 0
77 | 3317.2726 |  | 60.5648 | 107.1932 |  | 4.1782
78 | 3312.9881 |  | 60.4866 | 339.7754 |  | 13.2437
79 | 3308.7309 |  | 60.4088 | 572.3304 |  | 22.3082
80 | 3304.5008 |  | 60.3316 | 804.8582 |  | 31.3716
81 | 3300.2977 |  | 60.2549 | 1037.359 |  | 40.434
82 | 3296.1216 |  | 60.1786 | 1269.8328 |  | 49.4953
83 | 3291.9724 |  | 60.1029 | 1502.2798 |  | 58.5556
84 | 3287.8499 |  | 60.0276 | 1734.7 |  | 67.6148
85 | 3283.754 |  | 59.9528 | 1967.0936 |  | 76.673
86 | 3279.6847 |  | 59.8785 | 2199.4606 |  | 85.7302
87 | 3275.6419 |  | 59.8047 | 2032.2802 |  | 79.2138
88 | 3271.6254 |  | 59.7314 | 2435.8176 |  | 94.9429
89 | 3267.6352 |  | 59.6585 | 2839.3289 |  | 110.6708
90 | 3263.6712 |  | 59.5862 | 3242.8139 |  | 126.3978
91 | 3259.7332 |  | 59.5143 | 2775.8878 |  | 108.1981
92 | 3255.8213 |  | 59.4428 | 2308.9357 |  | 89.9973
93 | 3251.9352 |  | 59.3719 | 1841.9577 |  | 71.7955
94 | 3248.0749 |  | 59.3014 | 1374.954 |  | 53.5927
95 | 3244.2404 |  | 59.2314 | 907.9245 |  | 35.3889
96 | 3240.4314 |  | 59.1619 | 184.0344 |  | 7.1733
97 | 2910.796 |  | 53.1436 | 0 |  | 0
98 | 2739.5727 |  | 50.0175 | 0 |  | 0
99 | 2910.796 |  | 53.1436 | 0 |  | 0
100 | 3082.0192 |  | 56.2697 | 0 |  | 0
101 | 3222.4692 |  | 58.8339 | 170.8651 |  | 6.6599
102 | 3217.922 |  | 58.7509 | 393.3329 |  | 15.3313
103 | 3213.4014 |  | 58.6684 | 615.7741 |  | 24.0015
104 | 3208.9074 |  | 58.5863 | 838.1886 |  | 32.6708
105 | 3204.4398 |  | 58.5047 | 1060.5767 |  | 41.339
106 | 3199.9987 |  | 58.4237 | 1282.9384 |  | 50.0061
107 | 3195.5838 |  | 58.3431 | 1505.2738 |  | 58.6723
108 | 3191.7243 |  | 58.2726 | 1727.0539 |  | 67.3168
109 | 3188.2422 |  | 58.209 | 1948.4565 |  | 75.9466
110 | 3184.7845 |  | 58.1459 | 1854.0724 |  | 72.2677
111 | 3181.3511 |  | 58.0832 | 1759.6639 |  | 68.5879
112 | 3177.9418 |  | 58.021 | 1665.2313 |  | 64.9071
113 | 3174.5566 |  | 57.9592 | 1570.7746 |  | 61.2254
114 | 3171.1954 |  | 57.8978 | 1476.294 |  | 57.5427
115 | 3167.8581 |  | 57.8369 | 1381.7894 |  | 53.8591
116 | 3164.5446 |  | 57.7764 | 1287.261 |  | 50.1746
117 | 3161.2548 |  | 57.7163 | 1632.9974 |  | 63.6507
118 | 3157.9887 |  | 57.6567 | 1122.5936 |  | 43.7563
119 | 3154.3933 |  | 57.591 | 612.5191 |  | 23.8747
120 | 3150.2933 |  | 57.5162 | 102.9492 |  | 4.0127
121 | 2739.5727 |  | 50.0175 | 0 |  | 0
122 | 2739.5727 |  | 50.0175 | 0 |  | 0
123 | 2935.2564 |  | 53.5902 | 0 |  | 0
124 | 3130.9402 |  | 57.1628 | 0 |  | 0
125 | 3132.3349 |  | 57.1883 | 194.2891 |  | 7.573
126 | 3128.3739 |  | 57.116 | 393.9339 |  | 15.3547
127 | 3124.4374 |  | 57.0441 | 593.5541 |  | 23.1354
128 | 3120.5253 |  | 56.9727 | 793.1499 |  | 30.9153
129 | 3116.6377 |  | 56.9017 | 992.7213 |  | 38.6941
130 | 3112.7743 |  | 56.8312 | 1192.2685 |  | 46.472
131 | 3108.9351 |  | 56.7611 | 1391.7914 |  | 54.249
132 | 3105.12 |  | 56.6914 | 1591.2903 |  | 62.025
133 | 3101.3289 |  | 56.6222 | 1692.9232 |  | 65.9865
134 | 3097.5618 |  | 56.5534 | 1696.6904 |  | 66.1333
135 | 3093.8185 |  | 56.4851 | 2189.6431 |  | 85.3475
136 | 3090.099 |  | 56.4172 | 2389.0463 |  | 93.1198
137 | 3086.4032 |  | 56.3497 | 2118.7849 |  | 82.5856
138 | 3082.7309 |  | 56.2827 | 1848.4999 |  | 72.0505
139 | 3079.435 |  | 56.2225 | 1714.8172 |  | 66.8398
140 | 3076.6905 |  | 56.1724 | 1306.6258 |  | 50.9294
141 | 3073.9677 |  | 56.1227 | 1035.3913 |  | 40.3573
142 | 3071.2665 |  | 56.0733 | 764.1353 |  | 29.7843
143 | 3068.5868 |  | 56.0244 | 13.4325 |  | 0.52357
144 | 2910.796 |  | 53.1436 | 0 |  | 0
145 | 2739.5727 |  | 50.0175 | 0 |  | 0
146 | 2739.5727 |  | 50.0175 | 0 |  | 0
147 | 2910.796 |  | 53.1436 | 0 |  | 0
148 | 3057.5869 |  | 55.8236 | 24.4323 |  | 0.95232
149 | 3055.025 |  | 55.7768 | 198.2176 |  | 7.7261
150 | 3052.484 |  | 55.7304 | 371.9818 |  | 14.499
151 | 3049.9639 |  | 55.6844 | 545.7252 |  | 21.2712
152 | 3047.4646 |  | 55.6388 | 719.4478 |  | 28.0425
153 | 3044.9861 |  | 55.5935 | 893.1496 |  | 34.813
154 | 3042.4399 |  | 55.5471 | 1066.9191 |  | 41.5862
155 | 3039.1213 |  | 55.4865 | 1241.461 |  | 48.3894
156 | 3035.8248 |  | 55.4263 | 1415.9808 |  | 55.1918
157 | 3032.5503 |  | 55.3665 | 1590.4785 |  | 61.9934
158 | 3029.2979 |  | 55.3071 | 1764.9543 |  | 68.7941
159 | 3026.0674 |  | 55.2481 | 1596.9615 |  | 62.2461
160 | 3022.8587 |  | 55.1895 | 1771.3934 |  | 69.0451
161 | 3019.6718 |  | 55.1314 | 2459.4735 |  | 95.8649
162 | 3016.5066 |  | 55.0736 | 2291.4154 |  | 89.3144
163 | 3013.363 |  | 55.0162 | 2637.0056 |  | 102.7847
164 | 3010.2409 |  | 54.9592 | 2263.4365 |  | 88.2238
165 | 3007.1403 |  | 54.9026 | 1889.8459 |  | 73.6621
166 | 3004.3256 |  | 54.8512 | 1515.9693 |  | 59.0892
167 | 3002.1486 |  | 54.8114 | 1141.4551 |  | 44.4914
168 | 2999.9911 |  | 54.772 | 766.9213 |  | 29.8929
169 | 2910.796 |  | 53.1436 | 0 |  | 0
170 | 2739.5727 |  | 50.0175 | 0 |  | 0
171 | 2910.796 |  | 53.1436 | 0 |  | 0
172 | 2992.3725 |  | 54.633 | 89.6468 |  | 3.4942
173 | 2990.3078 |  | 54.5953 | 519.7696 |  | 20.2595
174 | 2988.2623 |  | 54.5579 | 778.6501 |  | 30.3501
175 | 2986.2358 |  | 54.5209 | 1037.5116 |  | 40.4399
176 | 2984.2282 |  | 54.4843 | 1296.3541 |  | 50.5291
177 | 2982.2395 |  | 54.4479 | 1555.1777 |  | 60.6174
178 | 2980.2696 |  | 54.412 | 1813.9826 |  | 70.7051
179 | 2978.3184 |  | 54.3764 | 2072.7687 |  | 80.792
180 | 2976.3859 |  | 54.3411 | 2331.5362 |  | 90.8782
181 | 2974.472 |  | 54.3061 | 2590.285 |  | 100.9637
182 | 2972.5765 |  | 54.2715 | 2849.0154 |  | 111.0484
183 | 2970.6995 |  | 54.2373 | 2679.6691 |  | 104.4477
184 | 2968.8409 |  | 54.2033 | 2909.8254 |  | 113.4186
185 | 2967.0006 |  | 54.1697 | 3710.7078 |  | 144.6353
186 | 2965.1784 |  | 54.1365 | 3541.3066 |  | 138.0324
187 | 2963.3745 |  | 54.1035 | 3885.5572 |  | 151.4505
188 | 2961.5886 |  | 54.0709 | 3544.8965 |  | 138.1723
189 | 2959.8207 |  | 54.0386 | 4060.3343 |  | 158.263
190 | 2958.0707 |  | 54.0067 | 3205.9678 |  | 124.9616
191 | 2956.3386 |  | 53.9751 | 2351.5835 |  | 91.6596
192 | 2954.6243 |  | 53.9438 | 1497.1813 |  | 58.3569
193 | 2910.796 |  | 53.1436 | 0 |  | 0
194 | 2739.5727 |  | 50.0175 | 0 |  | 0
195 | 2945.0406 |  | 53.7688 | 0 |  | 0
196 | 2948.4698 |  | 53.8314 | 133.5494 |  | 5.2055
197 | 2946.8409 |  | 53.8017 | 453.1644 |  | 17.6634
198 | 2945.2295 |  | 53.7722 | 674.9201 |  | 26.3069
199 | 2943.6353 |  | 53.7431 | 896.6585 |  | 34.9498
200 | 2942.0584 |  | 53.7143 | 1118.3797 |  | 43.592
201 | 2940.4986 |  | 53.6859 | 1340.0837 |  | 52.2335
202 | 2938.9559 |  | 53.6577 | 1561.7706 |  | 60.8744
203 | 2937.4303 |  | 53.6298 | 1783.4404 |  | 69.5146
204 | 2935.9216 |  | 53.6023 | 2005.0933 |  | 78.1542
205 | 2934.4299 |  | 53.5751 | 2226.7294 |  | 86.7931
206 | 2932.9549 |  | 53.5481 | 2448.3485 |  | 95.4313
207 | 2931.4967 |  | 53.5215 | 2669.951 |  | 104.0689
208 | 2930.0552 |  | 53.4952 | 2891.5367 |  | 112.7058
209 | 2928.6303 |  | 53.4692 | 2721.7383 |  | 106.0874
210 | 2927.222 |  | 53.4435 | 3065.5932 |  | 119.4901
211 | 2925.8302 |  | 53.4181 | 3409.4316 |  | 132.8922
212 | 2924.4548 |  | 53.3929 | 3582.0303 |  | 139.6197
213 | 2923.0957 |  | 53.3681 | 4097.0593 |  | 159.6944
214 | 2921.7529 |  | 53.3436 | 3242.2856 |  | 126.3772
215 | 2920.4264 |  | 53.3194 | 2387.4957 |  | 93.0594
216 | 2919.116 |  | 53.2955 | 1532.6896 |  | 59.7409
217 | 2910.796 |  | 53.1436 | 0 |  | 0
218 | 2739.5727 |  | 50.0175 | 0 |  | 0
219 | 2910.796 |  | 53.1436 | 0 |  | 0
220 | 2914.4433 |  | 53.2102 | 167.576 |  | 6.5317
221 | 2913.2108 |  | 53.1877 | 537.5971 |  | 20.9544
222 | 2911.9941 |  | 53.1654 | 775.8922 |  | 30.2426
223 | 2910.7931 |  | 53.1435 | 1014.1716 |  | 39.5302
224 | 2909.6078 |  | 53.1219 | 1252.4353 |  | 48.8172
225 | 2908.438 |  | 53.1005 | 1490.6835 |  | 58.1036
226 | 2907.2837 |  | 53.0795 | 1728.9162 |  | 67.3894
227 | 2906.1449 |  | 53.0587 | 1967.1334 |  | 76.6746
228 | 2905.0215 |  | 53.0381 | 2205.3352 |  | 85.9592
229 | 2903.9134 |  | 53.0179 | 2443.5217 |  | 95.2431
230 | 2902.8206 |  | 52.998 | 2681.693 |  | 104.5265
231 | 2901.7429 |  | 52.9783 | 2919.849 |  | 113.8093
232 | 2900.6804 |  | 52.9589 | 2749.6882 |  | 107.1768
233 | 2899.633 |  | 52.9398 | 3058.9376 |  | 119.2307
234 | 2898.6005 |  | 52.9209 | 3368.1719 |  | 131.284
235 | 2897.5831 |  | 52.9023 | 3951.3486 |  | 154.0149
236 | 2896.5805 |  | 52.884 | 3952.3512 |  | 154.054
237 | 2895.5927 |  | 52.866 | 4295.7856 |  | 167.4403
238 | 2894.6197 |  | 52.8482 | 3406.3975 |  | 132.7739
239 | 2893.6613 |  | 52.8307 | 2516.9947 |  | 98.107
240 | 2892.7177 |  | 52.8135 | 1627.5772 |  | 63.4394
241 | 2891.7886 |  | 52.7965 | 19.0074 |  | 0.74087
242 | 2739.5727 |  | 50.0175 | 0 |  | 0
243 | 2888.5091 |  | 52.7367 | 22.2869 |  | 0.86869
244 | 2886.7438 |  | 52.7044 | 195.2755 |  | 7.6114
245 | 2884.9945 |  | 52.6725 | 539.4713 |  | 21.0274
246 | 2883.2612 |  | 52.6409 | 769.5024 |  | 29.9935
247 | 2881.5437 |  | 52.6095 | 999.5175 |  | 38.959
248 | 2879.8421 |  | 52.5784 | 1229.5169 |  | 47.9239
249 | 2878.1562 |  | 52.5477 | 1459.5005 |  | 56.8881
250 | 2876.486 |  | 52.5172 | 1689.4684 |  | 65.8518
251 | 2874.8315 |  | 52.487 | 1919.4207 |  | 74.8148
252 | 2873.1925 |  | 52.457 | 2149.3574 |  | 83.7773
253 | 2871.569 |  | 52.4274 | 2379.2786 |  | 92.7391
254 | 2869.961 |  | 52.398 | 2609.1843 |  | 101.7003
255 | 2868.3684 |  | 52.369 | 2439.5537 |  | 95.0885
256 | 2866.7911 |  | 52.3402 | 2840.652 |  | 110.7224
257 | 2865.229 |  | 52.3116 | 3241.735 |  | 126.3558
258 | 2863.6822 |  | 52.2834 | 3642.8029 |  | 141.9885
259 | 2862.1505 |  | 52.2554 | 3173.4705 |  | 123.695
260 | 2860.6339 |  | 52.2277 | 2704.123 |  | 105.4008
261 | 2859.1324 |  | 52.2003 | 2234.7606 |  | 87.1061
262 | 2857.6458 |  | 52.1732 | 1765.3831 |  | 68.8108
263 | 2856.1741 |  | 52.1463 | 1295.9907 |  | 50.5149
264 | 2854.7172 |  | 52.1197 | 569.7486 |  | 22.2076
265 | 2853.2752 |  | 52.0934 | 57.5208 |  | 2.242
266 | 2739.5727 |  | 50.0175 | 0 |  | 0
267 | 2850.6004 |  | 52.0446 | 60.1955 |  | 2.3463
268 | 2849.2017 |  | 52.019 | 232.8176 |  | 9.0747
269 | 2847.8174 |  | 51.9938 | 545.5169 |  | 21.2631
270 | 2846.4477 |  | 51.9687 | 764.8072 |  | 29.8105
271 | 2845.0924 |  | 51.944 | 984.083 |  | 38.3574
272 | 2843.7516 |  | 51.9195 | 1203.3444 |  | 46.9037
273 | 2842.425 |  | 51.8953 | 1422.5915 |  | 55.4495
274 | 2841.1127 |  | 51.8713 | 1641.8244 |  | 63.9947
275 | 2839.8146 |  | 51.8476 | 1861.043 |  | 72.5394
276 | 2838.5307 |  | 51.8242 | 2080.2475 |  | 81.0835
277 | 2837.2609 |  | 51.801 | 2299.4378 |  | 89.6271
278 | 2836.0051 |  | 51.7781 | 2202.8517 |  | 85.8624
279 | 2834.7634 |  | 51.7554 | 2106.2516 |  | 82.0971
280 | 2833.5355 |  | 51.733 | 2009.6376 |  | 78.3313
281 | 2832.3215 |  | 51.7108 | 1913.0097 |  | 74.5649
282 | 2831.1214 |  | 51.6889 | 1816.368 |  | 70.7981
283 | 2829.935 |  | 51.6673 | 1719.7125 |  | 67.0306
284 | 2828.7623 |  | 51.6459 | 1623.0433 |  | 63.2627
285 | 2827.6033 |  | 51.6247 | 1966.6489 |  | 76.6557
286 | 2826.4579 |  | 51.6038 | 1454.1244 |  | 56.6786
287 | 2825.326 |  | 51.5831 | 941.5864 |  | 36.701
288 | 2824.2076 |  | 51.5627 | 429.035 |  | 16.7228
289 | 2739.5727 |  | 50.0175 | 0 |  | 0
290 | 2739.5727 |  | 50.0175 | 0 |  | 0
291 | 2821.1725 |  | 51.5073 | 114.084 |  | 4.4467
292 | 2820.1064 |  | 51.4878 | 310.8338 |  | 12.1156
293 | 2819.0535 |  | 51.4686 | 507.5705 |  | 19.784
294 | 2818.0138 |  | 51.4496 | 704.2939 |  | 27.4518
295 | 2816.9872 |  | 51.4309 | 901.0043 |  | 35.1192
296 | 2816.4146 |  | 51.4204 | 1097.2606 |  | 42.7688
297 | 2816.2947 |  | 51.4182 | 1293.0643 |  | 50.4008
298 | 2816.1861 |  | 51.4162 | 1488.8566 |  | 58.0324
299 | 2816.0888 |  | 51.4145 | 1684.6377 |  | 65.6635
300 | 2816.0026 |  | 51.4129 | 1880.4077 |  | 73.2942
301 | 2815.9276 |  | 51.4115 | 1978.3246 |  | 77.1108
302 | 2815.8636 |  | 51.4104 | 1978.3886 |  | 77.1133
303 | 2815.8107 |  | 51.4094 | 2467.6509 |  | 96.1836
304 | 2815.7687 |  | 51.4086 | 2663.3766 |  | 103.8126
305 | 2815.7377 |  | 51.4081 | 2389.4504 |  | 93.1356
306 | 2815.7175 |  | 51.4077 | 2115.5133 |  | 82.4581
307 | 2815.7082 |  | 51.4075 | 1978.5439 |  | 77.1193
308 | 2815.7097 |  | 51.4075 | 1567.6066 |  | 61.1019
309 | 2815.7219 |  | 51.4078 | 1293.6371 |  | 50.4232
310 | 2815.7447 |  | 51.4082 | 1019.657 |  | 39.744
311 | 2815.7782 |  | 51.4088 | 266.241 |  | 10.3775
312 | 2815.8223 |  | 51.4096 | 94.9736 |  | 3.7019
313 | 2739.5727 |  | 50.0175 | 0 |  | 0
314 | 2739.5727 |  | 50.0175 | 0 |  | 0
315 | 2816.2648 |  | 51.4177 | 94.5311 |  | 3.6846
316 | 2816.3496 |  | 51.4192 | 265.6696 |  | 10.3552
317 | 2816.4447 |  | 51.421 | 436.7978 |  | 17.0254
318 | 2816.5502 |  | 51.4229 | 607.9157 |  | 23.6952
319 | 2816.6658 |  | 51.425 | 779.0233 |  | 30.3646
320 | 2816.7917 |  | 51.4273 | 950.1207 |  | 37.0336
321 | 2816.9278 |  | 51.4298 | 1121.208 |  | 43.7022
322 | 2817.0739 |  | 51.4325 | 1292.2851 |  | 50.3705
323 | 2817.2301 |  | 51.4353 | 1463.3522 |  | 57.0383
324 | 2817.3963 |  | 51.4383 | 1634.4093 |  | 63.7057
325 | 2817.5725 |  | 51.4416 | 1805.4564 |  | 70.3728
326 | 2817.7585 |  | 51.445 | 1976.4936 |  | 77.0394
327 | 2817.9545 |  | 51.4485 | 1805.0744 |  | 70.3579
328 | 2818.1603 |  | 51.4523 | 1976.0919 |  | 77.0238
329 | 2818.3758 |  | 51.4562 | 2660.7695 |  | 103.711
330 | 2818.6011 |  | 51.4603 | 2489.3209 |  | 97.0283
331 | 2818.8361 |  | 51.4646 | 2831.5325 |  | 110.367
332 | 2819.0807 |  | 51.4691 | 2454.5967 |  | 95.6748
333 | 2819.3349 |  | 51.4737 | 2077.6512 |  | 80.9823
334 | 2819.5987 |  | 51.4785 | 1700.6962 |  | 66.2894
335 | 2819.8719 |  | 51.4835 | 1323.7317 |  | 51.5962
336 | 2820.1547 |  | 51.4887 | 946.7578 |  | 36.9026
337 | 2820.4468 |  | 51.494 | 90.3492 |  | 3.5216
338 | 2739.5727 |  | 50.0175 | 0 |  | 0
339 | 2821.1453 |  | 51.5068 | 89.6507 |  | 3.4944
340 | 2821.465 |  | 51.5126 | 260.5543 |  | 10.1558
341 | 2821.7939 |  | 51.5186 | 688.2836 |  | 26.8278
342 | 2822.1321 |  | 51.5248 | 944.7804 |  | 36.8255
343 | 2822.4793 |  | 51.5311 | 1201.268 |  | 46.8228
344 | 2822.8357 |  | 51.5376 | 1457.7466 |  | 56.8198
345 | 2823.2011 |  | 51.5443 | 1714.2161 |  | 66.8164
346 | 2823.5756 |  | 51.5512 | 1970.6766 |  | 76.8127
347 | 2823.959 |  | 51.5582 | 2227.1281 |  | 86.8086
348 | 2824.3513 |  | 51.5653 | 2483.5707 |  | 96.8042
349 | 2824.7525 |  | 51.5726 | 2740.0044 |  | 106.7994
350 | 2825.1626 |  | 51.5801 | 2996.4293 |  | 116.7943
351 | 2825.5815 |  | 51.5878 | 2824.7872 |  | 110.104
352 | 2826.0091 |  | 51.5956 | 3052.6573 |  | 118.9859
353 | 2826.4454 |  | 51.6036 | 3851.263 |  | 150.1138
354 | 2826.8904 |  | 51.6117 | 3679.5947 |  | 143.4226
355 | 2827.344 |  | 51.62 | 4021.5877 |  | 156.7527
356 | 2827.8062 |  | 51.6284 | 3678.6789 |  | 143.3869
357 | 2828.2769 |  | 51.637 | 4191.878 |  | 163.3903
358 | 2828.7562 |  | 51.6457 | 3335.2823 |  | 130.002
359 | 2829.2439 |  | 51.6546 | 2478.6782 |  | 96.6135
360 | 2829.74 |  | 51.6637 | 1622.0656 |  | 63.2246
361 | 2830.2445 |  | 51.6729 | 80.5515 |  | 3.1397
362 | 2739.5727 |  | 50.0175 | 0 |  | 0
363 | 2831.3782 |  | 51.6936 | 113.6624 |  | 4.4303
364 | 2831.9071 |  | 51.7033 | 250.1122 |  | 9.7488
365 | 2832.4442 |  | 51.7131 | 567.5612 |  | 22.1223
366 | 2832.9895 |  | 51.723 | 787.1601 |  | 30.6818
367 | 2833.5429 |  | 51.7331 | 1006.751 |  | 39.241
368 | 2834.1044 |  | 51.7434 | 1226.3337 |  | 47.7998
369 | 2834.6739 |  | 51.7538 | 1445.9084 |  | 56.3584
370 | 2835.2514 |  | 51.7643 | 1665.4751 |  | 64.9166
371 | 2835.8369 |  | 51.775 | 1885.0338 |  | 73.4745
372 | 2836.4304 |  | 51.7859 | 2104.5846 |  | 82.0321
373 | 2837.0317 |  | 51.7968 | 2324.1275 |  | 90.5894
374 | 2837.6408 |  | 51.808 | 2543.6626 |  | 99.1464
375 | 2838.2578 |  | 51.8192 | 2763.1899 |  | 107.7031
376 | 2838.8825 |  | 51.8306 | 2982.7094 |  | 116.2595
377 | 2839.515 |  | 51.8422 | 2810.8536 |  | 109.5609
378 | 2840.1551 |  | 51.8539 | 3152.6601 |  | 122.8838
379 | 2840.8029 |  | 51.8657 | 3494.4589 |  | 136.2064
380 | 2841.4583 |  | 51.8776 | 3665.0267 |  | 142.8547
381 | 2842.1213 |  | 51.8898 | 4178.0337 |  | 162.8506
382 | 2842.7918 |  | 51.902 | 3321.2467 |  | 129.455
383 | 2843.4698 |  | 51.9144 | 2464.4523 |  | 96.059
384 | 2844.1552 |  | 51.9269 | 1607.6504 |  | 62.6627
385 | 2844.8481 |  | 51.9395 | 65.9479 |  | 2.5705
386 | 2739.5727 |  | 50.0175 | 0 |  | 0
387 | 2846.4029 |  | 51.9679 | 64.393 |  | 2.5099
388 | 2847.1171 |  | 51.981 | 234.9021 |  | 9.156
389 | 2847.8386 |  | 51.9941 | 602.9693 |  | 23.5024
390 | 2848.5673 |  | 52.0074 | 839.319 |  | 32.7148
391 | 2849.3031 |  | 52.0209 | 1075.6615 |  | 41.9269
392 | 2850.0462 |  | 52.0344 | 1311.9969 |  | 51.1388
393 | 2850.7963 |  | 52.0481 | 1548.3252 |  | 60.3503
394 | 2851.5535 |  | 52.062 | 1784.6464 |  | 69.5616
395 | 2852.3178 |  | 52.0759 | 2020.9605 |  | 78.7726
396 | 2853.089 |  | 52.09 | 2257.2677 |  | 87.9834
397 | 2853.8672 |  | 52.1042 | 2493.5679 |  | 97.1938
398 | 2854.0351 |  | 52.1073 | 2730.4784 |  | 106.4281
399 | 2853.9468 |  | 52.1057 | 2967.6451 |  | 115.6723
400 | 2853.867 |  | 52.1042 | 2796.5016 |  | 109.0015
401 | 2853.7957 |  | 52.1029 | 3104.7748 |  | 121.0173
402 | 2853.7329 |  | 52.1018 | 3413.0396 |  | 133.0328
403 | 2853.6784 |  | 52.1008 | 3995.2533 |  | 155.7263
404 | 2853.6323 |  | 52.0999 | 3995.2993 |  | 155.7281
405 | 2853.5946 |  | 52.0992 | 4337.7837 |  | 169.0773
406 | 2853.5651 |  | 52.0987 | 3447.452 |  | 134.3742
407 | 2853.5439 |  | 52.0983 | 2557.1121 |  | 99.6707
408 | 2853.5309 |  | 52.0981 | 1666.764 |  | 64.9668
409 | 2853.5261 |  | 52.098 | 57.2698 |  | 2.2323
410 | 2739.5727 |  | 50.0175 | 0 |  | 0
411 | 2853.711 |  | 52.1014 | 57.085 |  | 2.225
412 | 2853.7297 |  | 52.1017 | 228.2895 |  | 8.8982
413 | 2853.7565 |  | 52.1022 | 570.7094 |  | 22.245
414 | 2853.7912 |  | 52.1028 | 798.9723 |  | 31.1422
415 | 2853.8339 |  | 52.1036 | 1027.2274 |  | 40.0391
416 | 2853.8846 |  | 52.1045 | 1255.4744 |  | 48.9357
417 | 2853.9431 |  | 52.1056 | 1483.7137 |  | 57.8319
418 | 2854.0094 |  | 52.1068 | 1711.945 |  | 66.7279
419 | 2854.0836 |  | 52.1082 | 1940.1686 |  | 75.6235
420 | 2854.1656 |  | 52.1097 | 2168.3843 |  | 84.5189
421 | 2854.2553 |  | 52.1113 | 2396.5924 |  | 93.4139
422 | 2854.3527 |  | 52.1131 | 2624.7927 |  | 102.3087
423 | 2854.4577 |  | 52.115 | 2453.4643 |  | 95.6307
424 | 2854.5704 |  | 52.117 | 2852.8726 |  | 111.1988
425 | 2854.6907 |  | 52.1192 | 3252.2734 |  | 126.7665
426 | 2854.8186 |  | 52.1216 | 3651.6665 |  | 142.334
427 | 2854.954 |  | 52.124 | 3180.6671 |  | 123.9755
428 | 2855.0968 |  | 52.1267 | 2709.6602 |  | 105.6166
429 | 2855.2472 |  | 52.1294 | 2238.6458 |  | 87.2575
430 | 2855.4049 |  | 52.1323 | 1767.624 |  | 68.8981
431 | 2855.57 |  | 52.1353 | 1296.5948 |  | 50.5384
432 | 2855.7425 |  | 52.1384 | 568.7233 |  | 22.1676
433 | 2855.9223 |  | 52.1417 | 54.8737 |  | 2.1389
434 | 2739.5727 |  | 50.0175 | 0 |  | 0
435 | 2856.4816 |  | 52.1519 | 54.3144 |  | 2.1171
436 | 2856.6823 |  | 52.1556 | 225.337 |  | 8.7831
437 | 2856.8902 |  | 52.1594 | 536.4442 |  | 20.9094
438 | 2857.1052 |  | 52.1633 | 754.1497 |  | 29.3951
439 | 2857.3274 |  | 52.1674 | 971.8481 |  | 37.8805
440 | 2857.5566 |  | 52.1716 | 1189.5394 |  | 46.3657
441 | 2857.7929 |  | 52.1759 | 1407.2237 |  | 54.8505
442 | 2858.0361 |  | 52.1803 | 1624.901 |  | 63.3351
443 | 2858.2864 |  | 52.1849 | 1842.5712 |  | 71.8194
444 | 2858.5436 |  | 52.1896 | 2060.2346 |  | 80.3034
445 | 2858.8077 |  | 52.1944 | 2277.891 |  | 88.7872
446 | 2859.0787 |  | 52.1994 | 2179.7782 |  | 84.963
447 | 2859.3565 |  | 52.2044 | 2081.6585 |  | 81.1385
448 | 2859.6412 |  | 52.2096 | 1983.532 |  | 77.3137
449 | 2859.9326 |  | 52.2149 | 1885.3987 |  | 73.4887
450 | 2860.2307 |  | 52.2204 | 1787.2586 |  | 69.6634
451 | 2860.5356 |  | 52.226 | 1689.1119 |  | 65.8379
452 | 2860.8471 |  | 52.2316 | 1590.9585 |  | 62.0121
453 | 2861.1653 |  | 52.2374 | 1933.0869 |  | 75.3475
454 | 2861.4901 |  | 52.2434 | 1419.0922 |  | 55.3131
455 | 2861.8215 |  | 52.2494 | 905.0909 |  | 35.2785
456 | 2862.1594 |  | 52.2556 | 391.0831 |  | 15.2436
457 | 2739.5727 |  | 50.0175 | 0 |  | 0
458 | 2739.5727 |  | 50.0175 | 0 |  | 0
459 | 2863.6082 |  | 52.282 | 71.6482 |  | 2.7927
460 | 2863.9702 |  | 52.2887 | 266.97 |  | 10.4059
461 | 2864.3386 |  | 52.2954 | 462.2854 |  | 18.0189
462 | 2864.7133 |  | 52.3022 | 657.5944 |  | 25.6316
463 | 2865.0944 |  | 52.3092 | 852.8971 |  | 33.2441
464 | 2865.4817 |  | 52.3163 | 1048.1935 |  | 40.8563
465 | 2865.8754 |  | 52.3234 | 1243.4836 |  | 48.4683
466 | 2866.2752 |  | 52.3307 | 1438.7675 |  | 56.08
467 | 2866.6813 |  | 52.3382 | 1634.0452 |  | 63.6915
468 | 2867.0936 |  | 52.3457 | 1829.3167 |  | 71.3028
469 | 2867.512 |  | 52.3533 | 1926.7402 |  | 75.1001
470 | 2867.9365 |  | 52.3611 | 1926.3157 |  | 75.0836
471 | 2868.3671 |  | 52.3689 | 2415.0945 |  | 94.1351
472 | 2868.8037 |  | 52.3769 | 2610.3416 |  | 101.7454
473 | 2869.2464 |  | 52.385 | 2335.9417 |  | 91.0499
474 | 2869.695 |  | 52.3932 | 2061.5358 |  | 80.3542
475 | 2870.1496 |  | 52.4015 | 1924.1025 |  | 74.9973
476 | 2870.6102 |  | 52.4099 | 1512.7061 |  | 58.962
477 | 2871.0766 |  | 52.4184 | 1238.2824 |  | 48.2655
478 | 2871.549 |  | 52.427 | 963.8528 |  | 37.5689
479 | 2872.0271 |  | 52.4358 | 209.9921 |  | 8.185
480 | 2872.5111 |  | 52.4446 | 38.2849 |  | 1.4923
481 | 2739.5727 |  | 50.0175 | 0 |  | 0
482 | 2739.5727 |  | 50.0175 | 0 |  | 0
483 | 2874.531 |  | 52.4815 | 36.2649 |  | 1.4135
484 | 2875.0355 |  | 52.4907 | 206.9838 |  | 8.0678
485 | 2875.5456 |  | 52.5 | 377.6969 |  | 14.7218
486 | 2876.0614 |  | 52.5094 | 548.4045 |  | 21.3756
487 | 2876.5828 |  | 52.5189 | 719.1064 |  | 28.0292
488 | 2877.1097 |  | 52.5286 | 889.8027 |  | 34.6826
489 | 2877.6423 |  | 52.5383 | 1060.4934 |  | 41.3357
490 | 2878.1803 |  | 52.5481 | 1231.1787 |  | 47.9887
491 | 2878.7239 |  | 52.558 | 1401.8584 |  | 54.6414
492 | 2879.2729 |  | 52.568 | 1572.5327 |  | 61.2939
493 | 2879.8273 |  | 52.5782 | 1743.2015 |  | 67.9462
494 | 2880.3872 |  | 52.5884 | 1913.865 |  | 74.5983
495 | 2880.9525 |  | 52.5987 | 1742.0764 |  | 67.9023
496 | 2881.5231 |  | 52.6091 | 1912.7291 |  | 74.554
497 | 2882.099 |  | 52.6196 | 2597.0463 |  | 101.2272
498 | 2882.6802 |  | 52.6303 | 2425.2418 |  | 94.5306
499 | 2883.2667 |  | 52.641 | 2767.1019 |  | 107.8556
500 | 2883.8585 |  | 52.6518 | 2389.8189 |  | 93.1499
501 | 2884.4554 |  | 52.6627 | 2012.5307 |  | 78.4441
502 | 2885.0576 |  | 52.6737 | 1635.2373 |  | 63.738
503 | 2885.6649 |  | 52.6847 | 1257.9388 |  | 49.0317
504 | 2886.2773 |  | 52.6959 | 880.6351 |  | 34.3252
505 | 2886.8949 |  | 52.7072 | 23.9011 |  | 0.93161
506 | 2739.5727 |  | 50.0175 | 0 |  | 0
507 | 2888.432 |  | 52.7353 | 22.3639 |  | 0.8717
508 | 2889.0634 |  | 52.7468 | 192.9558 |  | 7.521
509 | 2889.6998 |  | 52.7584 | 620.3777 |  | 24.181
510 | 2890.3411 |  | 52.7701 | 876.5713 |  | 34.1668
511 | 2890.9874 |  | 52.7819 | 1132.7599 |  | 44.1525
512 | 2891.6386 |  | 52.7938 | 1388.9436 |  | 54.138
513 | 2892.2948 |  | 52.8058 | 1645.1225 |  | 64.1233
514 | 2892.9557 |  | 52.8179 | 1901.2964 |  | 74.1084
515 | 2893.6216 |  | 52.83 | 2157.4656 |  | 84.0933
516 | 2894.2922 |  | 52.8423 | 2413.6299 |  | 94.078
517 | 2894.9676 |  | 52.8546 | 2669.7894 |  | 104.0626
518 | 2895.6478 |  | 52.867 | 2925.9441 |  | 114.0469
519 | 2896.3327 |  | 52.8795 | 2754.0359 |  | 107.3463
520 | 2897.0223 |  | 52.8921 | 2981.644 |  | 116.218
521 | 2897.7166 |  | 52.9048 | 3779.9918 |  | 147.3358
522 | 2898.4156 |  | 52.9175 | 3608.0695 |  | 140.6347
523 | 2899.1192 |  | 52.9304 | 3949.8125 |  | 153.9551
524 | 2899.8274 |  | 52.9433 | 3606.6577 |  | 140.5796
525 | 2900.5402 |  | 52.9563 | 4119.6148 |  | 160.5736
526 | 2901.2575 |  | 52.9694 | 3262.781 |  | 127.1761
527 | 2901.9794 |  | 52.9826 | 2405.9427 |  | 93.7784
528 | 2902.7057 |  | 52.9959 | 1549.0999 |  | 60.3805
529 | 2903.4366 |  | 53.0092 | 7.3594 |  | 0.28685
530 | 2739.5727 |  | 50.0175 | 0 |  | 0
531 | 2905.2368 |  | 53.0421 | 39.8038 |  | 1.5515
532 | 2905.9795 |  | 53.0556 | 176.0398 |  | 6.8616
533 | 2906.7265 |  | 53.0693 | 493.2789 |  | 19.2269
534 | 2907.4779 |  | 53.083 | 712.6717 |  | 27.7784
535 | 2908.2336 |  | 53.0968 | 932.0603 |  | 36.3297
536 | 2908.9936 |  | 53.1107 | 1151.4445 |  | 44.8808
537 | 2909.7579 |  | 53.1246 | 1370.8244 |  | 53.4317
538 | 2910.5265 |  | 53.1387 | 1590.2001 |  | 61.9825
539 | 2911.2993 |  | 53.1528 | 1809.5715 |  | 70.5331
540 | 2912.0763 |  | 53.1669 | 2028.9387 |  | 79.0836
541 | 2912.8575 |  | 53.1812 | 2248.3017 |  | 87.6339
542 | 2913.6429 |  | 53.1956 | 2467.6606 |  | 96.184
543 | 2914.4324 |  | 53.21 | 2687.0153 |  | 104.734
544 | 2915.226 |  | 53.2245 | 2906.3659 |  | 113.2838
545 | 2916.0237 |  | 53.239 | 2734.3449 |  | 106.5788
546 | 2916.8255 |  | 53.2537 | 3075.9897 |  | 119.8954
547 | 2917.6313 |  | 53.2684 | 3417.6305 |  | 133.2118
548 | 2918.4411 |  | 53.2832 | 3588.044 |  | 139.8541
549 | 2919.255 |  | 53.298 | 4100.9 |  | 159.8441
550 | 2920.0728 |  | 53.3129 | 3243.9657 |  | 126.4427
551 | 2920.8945 |  | 53.3279 | 2387.0275 |  | 93.0411
552 | 2921.7202 |  | 53.343 | 1530.0854 |  | 59.6394
553 | 2910.796 |  | 53.1436 | 0 |  | 0
554 | 2739.5727 |  | 50.0175 | 0 |  | 0
555 | 2910.796 |  | 53.1436 | 0 |  | 0
556 | 2925.5021 |  | 53.4121 | 156.5171 |  | 6.1007
557 | 2926.3451 |  | 53.4275 | 524.4628 |  | 20.4424
558 | 2927.1918 |  | 53.4429 | 760.6945 |  | 29.6502
559 | 2928.0423 |  | 53.4584 | 996.9223 |  | 38.8579
560 | 2928.8966 |  | 53.474 | 1233.1465 |  | 48.0654
561 | 2929.7546 |  | 53.4897 | 1469.3669 |  | 57.2727
562 | 2930.6163 |  | 53.5054 | 1705.5836 |  | 66.4799
563 | 2931.4817 |  | 53.5212 | 1941.7966 |  | 75.687
564 | 2932.3507 |  | 53.5371 | 2178.006 |  | 84.8939
565 | 2933.2234 |  | 53.553 | 2414.2117 |  | 94.1007
566 | 2934.0996 |  | 53.569 | 2650.4139 |  | 103.3074
567 | 2934.9795 |  | 53.5851 | 2886.6124 |  | 112.5139
568 | 2935.863 |  | 53.6012 | 2714.5056 |  | 105.8055
569 | 2936.75 |  | 53.6174 | 3021.8206 |  | 117.784
570 | 2937.6405 |  | 53.6337 | 3329.132 |  | 129.7623
571 | 2938.5345 |  | 53.65 | 3910.3971 |  | 152.4187
572 | 2939.432 |  | 53.6664 | 3909.4996 |  | 152.3838
573 | 2940.333 |  | 53.6828 | 4251.0452 |  | 165.6965
574 | 2941.2374 |  | 53.6994 | 3359.7797 |  | 130.9569
575 | 2942.1453 |  | 53.7159 | 2468.5107 |  | 96.2172
576 | 2943.0565 |  | 53.7326 | 1577.2384 |  | 61.4773
577 | 2910.796 |  | 53.1436 | 0 |  | 0
578 | 2739.5727 |  | 50.0175 | 0 |  | 0
579 | 2910.796 |  | 53.1436 | 0 |  | 0
580 | 2947.2783 |  | 53.8096 | 134.741 |  | 5.2519
581 | 2948.2037 |  | 53.8265 | 476.2622 |  | 18.5637
582 | 2949.1323 |  | 53.8435 | 703.6312 |  | 27.426
583 | 2950.0643 |  | 53.8605 | 930.997 |  | 36.2882
584 | 2950.9995 |  | 53.8776 | 1158.3595 |  | 45.1503
585 | 2951.9378 |  | 53.8947 | 1385.7189 |  | 54.0123
586 | 2952.8794 |  | 53.9119 | 1613.075 |  | 62.8741
587 | 2953.8242 |  | 53.9292 | 1840.428 |  | 71.7359
588 | 2954.7721 |  | 53.9465 | 2067.7778 |  | 80.5975
589 | 2955.7232 |  | 53.9638 | 2295.1245 |  | 89.4589
590 | 2956.6773 |  | 53.9812 | 2522.468 |  | 98.3203
591 | 2957.6346 |  | 53.9987 | 2350.2875 |  | 91.6091
592 | 2958.5949 |  | 54.0163 | 2748.8482 |  | 107.1441
593 | 2959.5583 |  | 54.0338 | 3147.4058 |  | 122.679
594 | 2960.5247 |  | 54.0515 | 3545.9604 |  | 138.2138
595 | 2961.4941 |  | 54.0692 | 3074.1269 |  | 119.8228
596 | 2962.4665 |  | 54.0869 | 2602.2904 |  | 101.4316
597 | 2963.4419 |  | 54.1048 | 2130.451 |  | 83.0403
598 | 2964.4203 |  | 54.1226 | 1658.6086 |  | 64.6489
599 | 2965.4015 |  | 54.1405 | 1186.7633 |  | 46.2574
600 | 2966.3857 |  | 54.1585 | 458.0801 |  | 17.855
601 | 2910.796 |  | 53.1436 | 0 |  | 0
602 | 2739.5727 |  | 50.0175 | 0 |  | 0
603 | 2910.796 |  | 53.1436 | 0 |  | 0
604 | 2971.0212 |  | 54.2431 | 110.998 |  | 4.3265
605 | 2972.0166 |  | 54.2613 | 421.3177 |  | 16.422
606 | 2973.0148 |  | 54.2795 | 638.2401 |  | 24.8772
607 | 2974.0158 |  | 54.2978 | 855.1596 |  | 33.3323
608 | 2975.0195 |  | 54.3161 | 1072.0764 |  | 41.7872
609 | 2976.026 |  | 54.3345 | 1288.9905 |  | 50.242
610 | 2977.0353 |  | 54.3529 | 1505.9018 |  | 58.6968
611 | 2978.0472 |  | 54.3714 | 1722.8104 |  | 67.1514
612 | 2979.0618 |  | 54.3899 | 1939.7163 |  | 75.6059
613 | 2980.0792 |  | 54.4085 | 2156.6196 |  | 84.0603
614 | 2981.0991 |  | 54.4271 | 2057.7577 |  | 80.2069
615 | 2982.1217 |  | 54.4458 | 1958.8933 |  | 76.3534
616 | 2983.1469 |  | 54.4645 | 1860.0262 |  | 72.4998
617 | 2984.1748 |  | 54.4833 | 1761.1565 |  | 68.646
618 | 2985.2052 |  | 54.5021 | 1662.2842 |  | 64.7922
619 | 2986.2381 |  | 54.521 | 1563.4093 |  | 60.9383
620 | 2987.2736 |  | 54.5399 | 1464.5319 |  | 57.0843
621 | 2988.3117 |  | 54.5588 | 1805.9405 |  | 70.3916
622 | 2989.3522 |  | 54.5778 | 1291.2301 |  | 50.3293
623 | 2990.3953 |  | 54.5969 | 776.5172 |  | 30.2669
624 | 2991.4408 |  | 54.6159 | 261.8018 |  | 10.2045
625 | 2739.5727 |  | 50.0175 | 0 |  | 0
626 | 2739.5727 |  | 50.0175 | 0 |  | 0
627 | 2935.2564 |  | 53.5902 | 0 |  | 0
628 | 2996.7227 |  | 54.7124 | 134.2175 |  | 5.2315
629 | 2997.7753 |  | 54.7316 | 328.8486 |  | 12.8178
630 | 2998.8304 |  | 54.7509 | 523.4774 |  | 20.404
631 | 2999.8878 |  | 54.7702 | 718.1037 |  | 27.9901
632 | 3000.9475 |  | 54.7895 | 912.7277 |  | 35.5761
633 | 3002.0096 |  | 54.8089 | 1107.3494 |  | 43.1621
634 | 3003.074 |  | 54.8283 | 1301.9688 |  | 50.7479
635 | 3004.1406 |  | 54.8478 | 1496.5859 |  | 58.3337
636 | 3005.2096 |  | 54.8673 | 1691.2007 |  | 65.9193
637 | 3006.2808 |  | 54.8869 | 1787.9713 |  | 69.6912
638 | 3007.3543 |  | 54.9065 | 1786.8979 |  | 69.6494
639 | 3008.43 |  | 54.9261 | 2275.0316 |  | 88.6758
640 | 3009.5079 |  | 54.9458 | 2469.6375 |  | 96.2611
641 | 3010.588 |  | 54.9655 | 2194.6001 |  | 85.5407
642 | 3011.6702 |  | 54.9853 | 1919.5606 |  | 74.8203
643 | 3012.7546 |  | 55.0051 | 1781.4975 |  | 69.4389
644 | 3013.8412 |  | 55.0249 | 1369.4751 |  | 53.3792
645 | 3014.9299 |  | 55.0448 | 1094.4291 |  | 42.6585
646 | 3016.0207 |  | 55.0647 | 819.3811 |  | 31.9377
647 | 3017.1136 |  | 55.0847 | 64.9057 |  | 2.5299
648 | 2910.796 |  | 53.1436 | 0 |  | 0
649 | 2739.5727 |  | 50.0175 | 0 |  | 0
650 | 2739.5727 |  | 50.0175 | 0 |  | 0
651 | 2910.796 |  | 53.1436 | 0 |  | 0
652 | 3024.2608 |  | 55.2151 | 57.7584 |  | 2.2513
653 | 3025.3583 |  | 55.2352 | 227.8842 |  | 8.8824
654 | 3026.4578 |  | 55.2553 | 398.008 |  | 15.5135
655 | 3027.5593 |  | 55.2754 | 568.1299 |  | 22.1445
656 | 3028.6627 |  | 55.2955 | 738.2497 |  | 28.7754
657 | 3029.7681 |  | 55.3157 | 908.3676 |  | 35.4062
658 | 3030.8754 |  | 55.3359 | 1078.4836 |  | 42.0369
659 | 3031.9847 |  | 55.3562 | 1248.5976 |  | 48.6676
660 | 3033.0959 |  | 55.3765 | 1418.7097 |  | 55.2982
661 | 3034.2089 |  | 55.3968 | 1588.82 |  | 61.9287
662 | 3035.3238 |  | 55.4171 | 1758.9283 |  | 68.5592
663 | 3036.4406 |  | 55.4375 | 1586.5882 |  | 61.8417
664 | 3037.5593 |  | 55.4579 | 1756.6929 |  | 68.4721
665 | 3038.6797 |  | 55.4784 | 2440.4656 |  | 95.124
666 | 3039.802 |  | 55.4989 | 2268.12 |  | 88.4064
667 | 3040.9261 |  | 55.5194 | 2609.4426 |  | 101.7104
668 | 3042.0519 |  | 55.54 | 2231.6255 |  | 86.9839
669 | 3043.7086 |  | 55.5702 | 1853.2775 |  | 72.2367
670 | 3045.7185 |  | 55.6069 | 1474.5764 |  | 57.4758
671 | 3047.7284 |  | 55.6436 | 1095.8752 |  | 42.7148
672 | 3049.7384 |  | 55.6803 | 717.174 |  | 27.9539