## DC Cooler Duty
|  |  | Hourly Power Demand Coefficient (from graph) | Hourly Power Demand Coefficient (from graph) | Summer Heat Rejection Coefficient | Winter Heat Rejection Coefficient |  | Data Centre Hourly Power Demand | Hourly Cooler Duty Winter (75.6% of power demand) |  | Hourly Heat Cooler Duty Spring/Autumn (82.8% of power demand) |  | Hourly Cooler Duty Summer (90% of power demand)
% values from literature |  |  |  |  | 90% | 16% | 75.6% |  | 75.6% |  | 82.8% |  | 90%
Max DC Demand (MW) | My input |  |  | 7 | 6.3 | 5.292 |  | MWh | MWh | GJ/s | MWh | GJ/s | MWh | GJ/s
Max Coeff | From row E |  |  | 2.1 | 1.89 | 1.5876 | Checksum
Coeff to Demand Multiplier |  |  |  | 3.3333 | 3.3333 | 3.3333 | 6.3 | 5.292
[7 empty] | 1.5876 | 7
Hours | [6 empty] | MWh/week | 736.6781 | 556.9286 | 2004.943 | 609.9694 | 0 | 663.0103 | 2386.837
1 | 0 | Monday | 0.85 | 0.85 | 0.765 | 0.6426 | 0.6426 | 2.8333 | 2.142 | 7.7112 | 2.346 |  | 2.55 | 9.18
2 | 1 | Monday | 0.8 | 0.8 | 0.72 | 0.6048 | 0.6048 | 2.6667 | 2.016 | 7.2576 | 2.208 |  | 2.4 | 8.64
3 | 2 | Monday | 0.875 | 0.85 | 0.765 | 0.6426 | 0.6426 | 2.8333 | 2.142 | 7.7112 | 2.346 |  | 2.55 | 9.18
4 | 3 | Monday | 0.95 | 0.9 | 0.81 | 0.6804 | 0.6804 | 3 | 2.268 | 8.1648 | 2.484 |  | 2.7 | 9.72
5 | 4 | Monday | 1.025 | 1.025 | 0.9225 | 0.7749 | 0.7749 | 3.4167 | 2.583 | 9.2988 | 2.829 |  | 3.075 | 11.07
6 | 5 | Monday | 1.1 | 1.1 | 0.99 | 0.8316 | 0.8316 | 3.6667 | 2.772 | 9.9792 | 3.036 |  | 3.3 | 11.88
7 | 6 | Monday | 1.175 | 1.175 | 1.0575 | 0.8883 | 0.8883 | 3.9167 | 2.961 | 10.6596 | 3.243 |  | 3.525 | 12.69
8 | 7 | Monday | 1.25 | 1.25 | 1.125 | 0.945 | 0.945 | 4.1667 | 3.15 | 11.34 | 3.45 |  | 3.75 | 13.5
9 | 8 | Monday | 1.325 | 1.325 | 1.1925 | 1.0017 | 1.0017 | 4.4167 | 3.339 | 12.0204 | 3.657 |  | 3.975 | 14.31
10 | 9 | Monday | 1.4 | 1.4 | 1.26 | 1.0584 | 1.0584 | 4.6667 | 3.528 | 12.7008 | 3.864 |  | 4.2 | 15.12
11 | 10 | Monday | 1.475 | 1.475 | 1.3275 | 1.1151 | 1.1151 | 4.9167 | 3.717 | 13.3812 | 4.071 |  | 4.425 | 15.93
12 | 11 | Monday | 1.55 | 1.55 | 1.395 | 1.1718 | 1.1718 | 5.1667 | 3.906 | 14.0616 | 4.278 |  | 4.65 | 16.74
13 | 12 | Monday | 1.625 | 1.625 | 1.4625 | 1.2285 | 1.2285 | 5.4167 | 4.095 | 14.742 | 4.485 |  | 4.875 | 17.55
14 | 13 | Monday | 1.7 | 1.7 | 1.53 | 1.2852 | 1.2852 | 5.6667 | 4.284 | 15.4224 | 4.692 |  | 5.1 | 18.36
15 | 14 | Monday | 1.65 | 1.65 | 1.485 | 1.2474 | 1.2474 | 5.5 | 4.158 | 14.9688 | 4.554 |  | 4.95 | 17.82
16 | 15 | Monday | 1.7167 | 1.7167 | 1.545 | 1.2978 | 1.2978 | 5.7222 | 4.326 | 15.5736 | 4.738 |  | 5.15 | 18.54
17 | 16 | Monday | 1.7833 | 1.95 | 1.755 | 1.4742 | 1.4742 | 6.5 | 4.914 | 17.6904 | 5.382 |  | 5.85 | 21.06
18 | 17 | Monday | 1.85 | 1.9 | 1.71 | 1.4364 | 1.4364 | 6.3333 | 4.788 | 17.2368 | 5.244 |  | 5.7 | 20.52
19 | 18 | Monday | 1.9167 | 2 | 1.8 | 1.512 | 1.512 | 6.6667 | 5.04 | 18.144 | 5.52 |  | 6 | 21.6
20 | 19 | Monday | 1.9833 | 1.9 | 1.71 | 1.4364 | 1.4364 | 6.3333 | 4.788 | 17.2368 | 5.244 |  | 5.7 | 20.52
21 | 20 | Monday | 2.05 | 2.05 | 1.845 | 1.5498 | 1.5498 | 6.8333 | 5.166 | 18.5976 | 5.658 |  | 6.15 | 22.14
22 | 21 | Monday | 1.8 | 1.8 | 1.62 | 1.3608 | 1.3608 | 6 | 4.536 | 16.3296 | 4.968 |  | 5.4 | 19.44
23 | 22 | Monday | 1.55 | 1.55 | 1.395 | 1.1718 | 1.1718 | 5.1667 | 3.906 | 14.0616 | 4.278 |  | 4.65 | 16.74
24 | 23 | Monday | 1.3 | 1.3 | 1.17 | 0.9828 | 0.9828 | 4.3333 | 3.276 | 11.7936 | 3.588 |  | 3.9 | 14.04
25 | 0 | Tuesday | 1.05 | 0.85 | 0.765 | 0.6426 | 0.6426 | 2.8333 | 2.142 | 7.7112 | 2.346 |  | 2.55 | 9.18
26 | 1 | Tuesday | 0.8 | 0.8 | 0.72 | 0.6048 | 0.6048 | 2.6667 | 2.016 | 7.2576 | 2.208 |  | 2.4 | 8.64
27 | 2 | Tuesday | 0.86429 | 0.86 | 0.774 | 0.65016 | 0.65016 | 2.8667 | 2.1672 | 7.8019 | 2.3736 |  | 2.58 | 9.288
28 | 3 | Tuesday | 0.92857 | 0.9 | 0.81 | 0.6804 | 0.6804 | 3 | 2.268 | 8.1648 | 2.484 |  | 2.7 | 9.72
29 | 4 | Tuesday | 0.99286 | 0.99286 | 0.89357 | 0.7506 | 0.7506 | 3.3095 | 2.502 | 9.0072 | 2.7403 |  | 2.9786 | 10.7229
30 | 5 | Tuesday | 1.0571 | 1.0571 | 0.95143 | 0.7992 | 0.7992 | 3.5238 | 2.664 | 9.5904 | 2.9177 |  | 3.1714 | 11.4171
31 | 6 | Tuesday | 1.1214 | 1.1214 | 1.0093 | 0.8478 | 0.8478 | 3.7381 | 2.826 | 10.1736 | 3.0951 |  | 3.3643 | 12.1114
32 | 7 | Tuesday | 1.1857 | 1.1857 | 1.0671 | 0.8964 | 0.8964 | 3.9524 | 2.988 | 10.7568 | 3.2726 |  | 3.5571 | 12.8057
33 | 8 | Tuesday | 1.25 | 1.25 | 1.125 | 0.945 | 0.945 | 4.1667 | 3.15 | 11.34 | 3.45 |  | 3.75 | 13.5
34 | 9 | Tuesday | 1.3143 | 1.3143 | 1.1829 | 0.9936 | 0.9936 | 4.381 | 3.312 | 11.9232 | 3.6274 |  | 3.9429 | 14.1943
35 | 10 | Tuesday | 1.3786 | 1.3786 | 1.2407 | 1.0422 | 1.0422 | 4.5952 | 3.474 | 12.5064 | 3.8049 |  | 4.1357 | 14.8886
36 | 11 | Tuesday | 1.4429 | 1.4429 | 1.2986 | 1.0908 | 1.0908 | 4.8095 | 3.636 | 13.0896 | 3.9823 |  | 4.3286 | 15.5829
37 | 12 | Tuesday | 1.5071 | 1.5071 | 1.3564 | 1.1394 | 1.1394 | 5.0238 | 3.798 | 13.6728 | 4.1597 |  | 4.5214 | 16.2771
38 | 13 | Tuesday | 1.5714 | 1.5714 | 1.4143 | 1.188 | 1.188 | 5.2381 | 3.96 | 14.256 | 4.3371 |  | 4.7143 | 16.9714
39 | 14 | Tuesday | 1.6357 | 1.6357 | 1.4721 | 1.2366 | 1.2366 | 5.4524 | 4.122 | 14.8392 | 4.5146 |  | 4.9071 | 17.6657
40 | 15 | Tuesday | 1.7 | 1.7 | 1.53 | 1.2852 | 1.2852 | 5.6667 | 4.284 | 15.4224 | 4.692 |  | 5.1 | 18.36
41 | 16 | Tuesday | 1.65 | 1.65 | 1.485 | 1.2474 | 1.2474 | 5.5 | 4.158 | 14.9688 | 4.554 |  | 4.95 | 17.82
42 | 17 | Tuesday | 1.75 | 1.75 | 1.575 | 1.323 | 1.323 | 5.8333 | 4.41 | 15.876 | 4.83 |  | 5.25 | 18.9
43 | 18 | Tuesday | 1.85 | 1.85 | 1.665 | 1.3986 | 1.3986 | 6.1667 | 4.662 | 16.7832 | 5.106 |  | 5.55 | 19.98
44 | 19 | Tuesday | 1.95 | 1.9 | 1.71 | 1.4364 | 1.4364 | 6.3333 | 4.788 | 17.2368 | 5.244 |  | 5.7 | 20.52
45 | 20 | Tuesday | 2.05 | 2.05 | 1.845 | 1.5498 | 1.5498 | 6.8333 | 5.166 | 18.5976 | 5.658 |  | 6.15 | 22.14
46 | 21 | Tuesday | 1.8 | 1.8 | 1.62 | 1.3608 | 1.3608 | 6 | 4.536 | 16.3296 | 4.968 |  | 5.4 | 19.44
47 | 22 | Tuesday | 1.55 | 1.55 | 1.395 | 1.1718 | 1.1718 | 5.1667 | 3.906 | 14.0616 | 4.278 |  | 4.65 | 16.74
48 | 23 | Tuesday | 1.3 | 1.3 | 1.17 | 0.9828 | 0.9828 | 4.3333 | 3.276 | 11.7936 | 3.588 |  | 3.9 | 14.04
49 | 0 | Wednesday | 1.05 | 0.85 | 0.765 | 0.6426 | 0.6426 | 2.8333 | 2.142 | 7.7112 | 2.346 |  | 2.55 | 9.18
50 | 1 | Wednesday | 0.8 | 0.8 | 0.72 | 0.6048 | 0.6048 | 2.6667 | 2.016 | 7.2576 | 2.208 |  | 2.4 | 8.64
51 | 2 | Wednesday | 0.86923 | 0.85 | 0.765 | 0.6426 | 0.6426 | 2.8333 | 2.142 | 7.7112 | 2.346 |  | 2.55 | 9.18
52 | 3 | Wednesday | 0.93846 | 0.9 | 0.81 | 0.6804 | 0.6804 | 3 | 2.268 | 8.1648 | 2.484 |  | 2.7 | 9.72
53 | 4 | Wednesday | 1.0077 | 1.0077 | 0.90692 | 0.76182 | 0.76182 | 3.359 | 2.5394 | 9.1418 | 2.7812 |  | 3.0231 | 10.8831
54 | 5 | Wednesday | 1.0769 | 1.0769 | 0.96923 | 0.81415 | 0.81415 | 3.5897 | 2.7138 | 9.7698 | 2.9723 |  | 3.2308 | 11.6308
55 | 6 | Wednesday | 1.1462 | 1.1462 | 1.0315 | 0.86649 | 0.86649 | 3.8205 | 2.8883 | 10.3979 | 3.1634 |  | 3.4385 | 12.3785
56 | 7 | Wednesday | 1.2154 | 1.2154 | 1.0938 | 0.91883 | 0.91883 | 4.0513 | 3.0628 | 11.026 | 3.3545 |  | 3.6462 | 13.1262
57 | 8 | Wednesday | 1.2846 | 1.2846 | 1.1562 | 0.97117 | 0.97117 | 4.2821 | 3.2372 | 11.654 | 3.5455 |  | 3.8538 | 13.8738
58 | 9 | Wednesday | 1.3538 | 1.3538 | 1.2185 | 1.0235 | 1.0235 | 4.5128 | 3.4117 | 12.2821 | 3.7366 |  | 4.0615 | 14.6215
59 | 10 | Wednesday | 1.4231 | 1.4231 | 1.2808 | 1.0758 | 1.0758 | 4.7436 | 3.5862 | 12.9102 | 3.9277 |  | 4.2692 | 15.3692
60 | 11 | Wednesday | 1.4923 | 1.4923 | 1.3431 | 1.1282 | 1.1282 | 4.9744 | 3.7606 | 13.5382 | 4.1188 |  | 4.4769 | 16.1169
61 | 12 | Wednesday | 1.5615 | 1.5615 | 1.4054 | 1.1805 | 1.1805 | 5.2051 | 3.9351 | 14.1663 | 4.3098 |  | 4.6846 | 16.8646
62 | 13 | Wednesday | 1.6308 | 1.6308 | 1.4677 | 1.2329 | 1.2329 | 5.4359 | 4.1095 | 14.7943 | 4.5009 |  | 4.8923 | 17.6123
63 | 14 | Wednesday | 1.7 | 1.7 | 1.53 | 1.2852 | 1.2852 | 5.6667 | 4.284 | 15.4224 | 4.692 |  | 5.1 | 18.36
64 | 15 | Wednesday | 1.65 | 1.65 | 1.485 | 1.2474 | 1.2474 | 5.5 | 4.158 | 14.9688 | 4.554 |  | 4.95 | 17.82
65 | 16 | Wednesday | 1.74 | 1.74 | 1.566 | 1.3154 | 1.3154 | 5.8 | 4.3848 | 15.7853 | 4.8024 |  | 5.22 | 18.792
66 | 17 | Wednesday | 1.83 | 1.83 | 1.647 | 1.3835 | 1.3835 | 6.1 | 4.6116 | 16.6018 | 5.0508 |  | 5.49 | 19.764
67 | 18 | Wednesday | 1.92 | 2 | 1.8 | 1.512 | 1.512 | 6.6667 | 5.04 | 18.144 | 5.52 |  | 6 | 21.6
68 | 19 | Wednesday | 2.01 | 2 | 1.8 | 1.512 | 1.512 | 6.6667 | 5.04 | 18.144 | 5.52 |  | 6 | 21.6
69 | 20 | Wednesday | 2.1 | 2.1 | 1.89 | 1.5876 | 1.5876 | 7 | 5.292 | 19.0512 | 5.796 |  | 6.3 | 22.68
70 | 21 | Wednesday | 1.84 | 1.84 | 1.656 | 1.391 | 1.391 | 6.1333 | 4.6368 | 16.6925 | 5.0784 |  | 5.52 | 19.872
71 | 22 | Wednesday | 1.58 | 1.58 | 1.422 | 1.1945 | 1.1945 | 5.2667 | 3.9816 | 14.3338 | 4.3608 |  | 4.74 | 17.064
72 | 23 | Wednesday | 1.32 | 1.32 | 1.188 | 0.99792 | 0.99792 | 4.4 | 3.3264 | 11.975 | 3.6432 |  | 3.96 | 14.256
73 | 0 | Thursday | 1.06 | 0.85 | 0.765 | 0.6426 | 0.6426 | 2.8333 | 2.142 | 7.7112 | 2.346 |  | 2.55 | 9.18
74 | 1 | Thursday | 0.8 | 0.8 | 0.72 | 0.6048 | 0.6048 | 2.6667 | 2.016 | 7.2576 | 2.208 |  | 2.4 | 8.64
75 | 2 | Thursday | 0.86667 | 0.85 | 0.765 | 0.6426 | 0.6426 | 2.8333 | 2.142 | 7.7112 | 2.346 |  | 2.55 | 9.18
76 | 3 | Thursday | 0.93333 | 0.9 | 0.81 | 0.6804 | 0.6804 | 3 | 2.268 | 8.1648 | 2.484 |  | 2.7 | 9.72
77 | 4 | Thursday | 1 | 1 | 0.9 | 0.756 | 0.756 | 3.3333 | 2.52 | 9.072 | 2.76 |  | 3 | 10.8
78 | 5 | Thursday | 1.0667 | 1.0667 | 0.96 | 0.8064 | 0.8064 | 3.5556 | 2.688 | 9.6768 | 2.944 |  | 3.2 | 11.52
79 | 6 | Thursday | 1.1333 | 1.1333 | 1.02 | 0.8568 | 0.8568 | 3.7778 | 2.856 | 10.2816 | 3.128 |  | 3.4 | 12.24
80 | 7 | Thursday | 1.2 | 1.2 | 1.08 | 0.9072 | 0.9072 | 4 | 3.024 | 10.8864 | 3.312 |  | 3.6 | 12.96
81 | 8 | Thursday | 1.2667 | 1.2667 | 1.14 | 0.9576 | 0.9576 | 4.2222 | 3.192 | 11.4912 | 3.496 |  | 3.8 | 13.68
82 | 9 | Thursday | 1.3333 | 1.3333 | 1.2 | 1.008 | 1.008 | 4.4444 | 3.36 | 12.096 | 3.68 |  | 4 | 14.4
83 | 10 | Thursday | 1.4 | 1.4 | 1.26 | 1.0584 | 1.0584 | 4.6667 | 3.528 | 12.7008 | 3.864 |  | 4.2 | 15.12
84 | 11 | Thursday | 1.4667 | 1.4667 | 1.32 | 1.1088 | 1.1088 | 4.8889 | 3.696 | 13.3056 | 4.048 |  | 4.4 | 15.84
85 | 12 | Thursday | 1.5333 | 1.5333 | 1.38 | 1.1592 | 1.1592 | 5.1111 | 3.864 | 13.9104 | 4.232 |  | 4.6 | 16.56
86 | 13 | Thursday | 1.6 | 1.6 | 1.44 | 1.2096 | 1.2096 | 5.3333 | 4.032 | 14.5152 | 4.416 |  | 4.8 | 17.28
87 | 14 | Thursday | 1.55 | 1.55 | 1.395 | 1.1718 | 1.1718 | 5.1667 | 3.906 | 14.0616 | 4.278 |  | 4.65 | 16.74
88 | 15 | Thursday | 1.6667 | 1.6667 | 1.5 | 1.26 | 1.26 | 5.5556 | 4.2 | 15.12 | 4.6 |  | 5 | 18
89 | 16 | Thursday | 1.7833 | 1.7833 | 1.605 | 1.3482 | 1.3482 | 5.9444 | 4.494 | 16.1784 | 4.922 |  | 5.35 | 19.26
90 | 17 | Thursday | 1.9 | 1.9 | 1.71 | 1.4364 | 1.4364 | 6.3333 | 4.788 | 17.2368 | 5.244 |  | 5.7 | 20.52
91 | 18 | Thursday | 1.7625 | 1.7625 | 1.5862 | 1.3324 | 1.3324 | 5.875 | 4.4415 | 15.9894 | 4.8645 |  | 5.2875 | 19.035
92 | 19 | Thursday | 1.625 | 1.625 | 1.4625 | 1.2285 | 1.2285 | 5.4167 | 4.095 | 14.742 | 4.485 |  | 4.875 | 17.55
93 | 20 | Thursday | 1.4875 | 1.4875 | 1.3388 | 1.1245 | 1.1245 | 4.9583 | 3.7485 | 13.4946 | 4.1055 |  | 4.4625 | 16.065
94 | 21 | Thursday | 1.35 | 1.35 | 1.215 | 1.0206 | 1.0206 | 4.5 | 3.402 | 12.2472 | 3.726 |  | 4.05 | 14.58
95 | 22 | Thursday | 1.2125 | 1.2125 | 1.0913 | 0.91665 | 0.91665 | 4.0417 | 3.0555 | 10.9998 | 3.3465 |  | 3.6375 | 13.095
96 | 23 | Thursday | 1.075 | 1 | 0.9 | 0.756 | 0.756 | 3.3333 | 2.52 | 9.072 | 2.76 |  | 3 | 10.8
97 | 0 | Friday | 0.9375 | 0.85 | 0.765 | 0.6426 | 0.6426 | 2.8333 | 2.142 | 7.7112 | 2.346 |  | 2.55 | 9.18
98 | 1 | Friday | 0.8 | 0.8 | 0.72 | 0.6048 | 0.6048 | 2.6667 | 2.016 | 7.2576 | 2.208 |  | 2.4 | 8.64
99 | 2 | Friday | 0.86364 | 0.85 | 0.765 | 0.6426 | 0.6426 | 2.8333 | 2.142 | 7.7112 | 2.346 |  | 2.55 | 9.18
100 | 3 | Friday | 0.92727 | 0.9 | 0.81 | 0.6804 | 0.6804 | 3 | 2.268 | 8.1648 | 2.484 |  | 2.7 | 9.72
101 | 4 | Friday | 0.99091 | 0.99091 | 0.89182 | 0.74913 | 0.74913 | 3.303 | 2.4971 | 8.9895 | 2.7349 |  | 2.9727 | 10.7018
102 | 5 | Friday | 1.0545 | 1.0545 | 0.94909 | 0.79724 | 0.79724 | 3.5152 | 2.6575 | 9.5668 | 2.9105 |  | 3.1636 | 11.3891
103 | 6 | Friday | 1.1182 | 1.1182 | 1.0064 | 0.84535 | 0.84535 | 3.7273 | 2.8178 | 10.1441 | 3.0862 |  | 3.3545 | 12.0764
104 | 7 | Friday | 1.1818 | 1.1818 | 1.0636 | 0.89345 | 0.89345 | 3.9394 | 2.9782 | 10.7215 | 3.2618 |  | 3.5455 | 12.7636
105 | 8 | Friday | 1.2455 | 1.2455 | 1.1209 | 0.94156 | 0.94156 | 4.1515 | 3.1385 | 11.2988 | 3.4375 |  | 3.7364 | 13.4509
106 | 9 | Friday | 1.3091 | 1.3091 | 1.1782 | 0.98967 | 0.98967 | 4.3636 | 3.2989 | 11.8761 | 3.6131 |  | 3.9273 | 14.1382
107 | 10 | Friday | 1.3727 | 1.3727 | 1.2355 | 1.0378 | 1.0378 | 4.5758 | 3.4593 | 12.4534 | 3.7887 |  | 4.1182 | 14.8255
108 | 11 | Friday | 1.4364 | 1.4364 | 1.2927 | 1.0859 | 1.0859 | 4.7879 | 3.6196 | 13.0307 | 3.9644 |  | 4.3091 | 15.5127
109 | 12 | Friday | 1.5 | 1.5 | 1.35 | 1.134 | 1.134 | 5 | 3.78 | 13.608 | 4.14 |  | 4.5 | 16.2
110 | 13 | Friday | 1.4714 | 1.4714 | 1.3243 | 1.1124 | 1.1124 | 4.9048 | 3.708 | 13.3488 | 4.0611 |  | 4.4143 | 15.8914
111 | 14 | Friday | 1.4429 | 1.4429 | 1.2986 | 1.0908 | 1.0908 | 4.8095 | 3.636 | 13.0896 | 3.9823 |  | 4.3286 | 15.5829
112 | 15 | Friday | 1.4143 | 1.4143 | 1.2729 | 1.0692 | 1.0692 | 4.7143 | 3.564 | 12.8304 | 3.9034 |  | 4.2429 | 15.2743
113 | 16 | Friday | 1.3857 | 1.3857 | 1.2471 | 1.0476 | 1.0476 | 4.619 | 3.492 | 12.5712 | 3.8246 |  | 4.1571 | 14.9657
114 | 17 | Friday | 1.3571 | 1.3571 | 1.2214 | 1.026 | 1.026 | 4.5238 | 3.42 | 12.312 | 3.7457 |  | 4.0714 | 14.6571
115 | 18 | Friday | 1.3286 | 1.3286 | 1.1957 | 1.0044 | 1.0044 | 4.4286 | 3.348 | 12.0528 | 3.6669 |  | 3.9857 | 14.3486
116 | 19 | Friday | 1.3 | 1.3 | 1.17 | 0.9828 | 0.9828 | 4.3333 | 3.276 | 11.7936 | 3.588 |  | 3.9 | 14.04
117 | 20 | Friday | 1.4 | 1.4 | 1.26 | 1.0584 | 1.0584 | 4.6667 | 3.528 | 12.7008 | 3.864 |  | 4.2 | 15.12
118 | 21 | Friday | 1.25 | 1.25 | 1.125 | 0.945 | 0.945 | 4.1667 | 3.15 | 11.34 | 3.45 |  | 3.75 | 13.5
119 | 22 | Friday | 1.1 | 1.1 | 0.99 | 0.8316 | 0.8316 | 3.6667 | 2.772 | 9.9792 | 3.036 |  | 3.3 | 11.88
120 | 23 | Friday | 0.95 | 0.95 | 0.855 | 0.7182 | 0.7182 | 3.1667 | 2.394 | 8.6184 | 2.622 |  | 2.85 | 10.26
121 | 0 | Saturday | 0.8 | 0.8 | 0.72 | 0.6048 | 0.6048 | 2.6667 | 2.016 | 7.2576 | 2.208 |  | 2.4 | 8.64
122 | 1 | Saturday | 0.8 | 0.8 | 0.72 | 0.6048 | 0.6048 | 2.6667 | 2.016 | 7.2576 | 2.208 |  | 2.4 | 8.64
123 | 2 | Saturday | 0.85714 | 0.85714 | 0.77143 | 0.648 | 0.648 | 2.8571 | 2.16 | 7.776 | 2.3657 |  | 2.5714 | 9.2571
124 | 3 | Saturday | 0.91429 | 0.91429 | 0.82286 | 0.6912 | 0.6912 | 3.0476 | 2.304 | 8.2944 | 2.5234 |  | 2.7429 | 9.8743
125 | 4 | Saturday | 0.97143 | 0.97143 | 0.87429 | 0.7344 | 0.7344 | 3.2381 | 2.448 | 8.8128 | 2.6811 |  | 2.9143 | 10.4914
126 | 5 | Saturday | 1.0286 | 1.0286 | 0.92571 | 0.7776 | 0.7776 | 3.4286 | 2.592 | 9.3312 | 2.8389 |  | 3.0857 | 11.1086
127 | 6 | Saturday | 1.0857 | 1.0857 | 0.97714 | 0.8208 | 0.8208 | 3.619 | 2.736 | 9.8496 | 2.9966 |  | 3.2571 | 11.7257
128 | 7 | Saturday | 1.1429 | 1.1429 | 1.0286 | 0.864 | 0.864 | 3.8095 | 2.88 | 10.368 | 3.1543 |  | 3.4286 | 12.3429
129 | 8 | Saturday | 1.2 | 1.2 | 1.08 | 0.9072 | 0.9072 | 4 | 3.024 | 10.8864 | 3.312 |  | 3.6 | 12.96
130 | 9 | Saturday | 1.2571 | 1.2571 | 1.1314 | 0.9504 | 0.9504 | 4.1905 | 3.168 | 11.4048 | 3.4697 |  | 3.7714 | 13.5771
131 | 10 | Saturday | 1.3143 | 1.3143 | 1.1829 | 0.9936 | 0.9936 | 4.381 | 3.312 | 11.9232 | 3.6274 |  | 3.9429 | 14.1943
132 | 11 | Saturday | 1.3714 | 1.3714 | 1.2343 | 1.0368 | 1.0368 | 4.5714 | 3.456 | 12.4416 | 3.7851 |  | 4.1143 | 14.8114
133 | 12 | Saturday | 1.4286 | 1.4 | 1.26 | 1.0584 | 1.0584 | 4.6667 | 3.528 | 12.7008 | 3.864 |  | 4.2 | 15.12
134 | 13 | Saturday | 1.4857 | 1.4 | 1.26 | 1.0584 | 1.0584 | 4.6667 | 3.528 | 12.7008 | 3.864 |  | 4.2 | 15.12
135 | 14 | Saturday | 1.5429 | 1.5429 | 1.3886 | 1.1664 | 1.1664 | 5.1429 | 3.888 | 13.9968 | 4.2583 |  | 4.6286 | 16.6629
136 | 15 | Saturday | 1.6 | 1.6 | 1.44 | 1.2096 | 1.2096 | 5.3333 | 4.032 | 14.5152 | 4.416 |  | 4.8 | 17.28
137 | 16 | Saturday | 1.52 | 1.52 | 1.368 | 1.1491 | 1.1491 | 5.0667 | 3.8304 | 13.7894 | 4.1952 |  | 4.56 | 16.416
138 | 17 | Saturday | 1.44 | 1.44 | 1.296 | 1.0886 | 1.0886 | 4.8 | 3.6288 | 13.0637 | 3.9744 |  | 4.32 | 15.552
139 | 18 | Saturday | 1.36 | 1.4 | 1.26 | 1.0584 | 1.0584 | 4.6667 | 3.528 | 12.7008 | 3.864 |  | 4.2 | 15.12
140 | 19 | Saturday | 1.28 | 1.28 | 1.152 | 0.96768 | 0.96768 | 4.2667 | 3.2256 | 11.6122 | 3.5328 |  | 3.84 | 13.824
141 | 20 | Saturday | 1.2 | 1.2 | 1.08 | 0.9072 | 0.9072 | 4 | 3.024 | 10.8864 | 3.312 |  | 3.6 | 12.96
142 | 21 | Saturday | 1.12 | 1.12 | 1.008 | 0.84672 | 0.84672 | 3.7333 | 2.8224 | 10.1606 | 3.0912 |  | 3.36 | 12.096
143 | 22 | Saturday | 1.04 | 0.9 | 0.81 | 0.6804 | 0.6804 | 3 | 2.268 | 8.1648 | 2.484 |  | 2.7 | 9.72
144 | 23 | Saturday | 0.96 | 0.85 | 0.765 | 0.6426 | 0.6426 | 2.8333 | 2.142 | 7.7112 | 2.346 |  | 2.55 | 9.18
145 | 0 | Sunday | 0.88 | 0.8 | 0.72 | 0.6048 | 0.6048 | 2.6667 | 2.016 | 7.2576 | 2.208 |  | 2.4 | 8.64
146 | 1 | Sunday | 0.8 | 0.8 | 0.72 | 0.6048 | 0.6048 | 2.6667 | 2.016 | 7.2576 | 2.208 |  | 2.4 | 8.64
147 | 2 | Sunday | 0.85 | 0.85 | 0.765 | 0.6426 | 0.6426 | 2.8333 | 2.142 | 7.7112 | 2.346 |  | 2.55 | 9.18
148 | 3 | Sunday | 0.9 | 0.9 | 0.81 | 0.6804 | 0.6804 | 3 | 2.268 | 8.1648 | 2.484 |  | 2.7 | 9.72
149 | 4 | Sunday | 0.95 | 0.95 | 0.855 | 0.7182 | 0.7182 | 3.1667 | 2.394 | 8.6184 | 2.622 |  | 2.85 | 10.26
150 | 5 | Sunday | 1 | 1 | 0.9 | 0.756 | 0.756 | 3.3333 | 2.52 | 9.072 | 2.76 |  | 3 | 10.8
151 | 6 | Sunday | 1.05 | 1.05 | 0.945 | 0.7938 | 0.7938 | 3.5 | 2.646 | 9.5256 | 2.898 |  | 3.15 | 11.34
152 | 7 | Sunday | 1.1 | 1.1 | 0.99 | 0.8316 | 0.8316 | 3.6667 | 2.772 | 9.9792 | 3.036 |  | 3.3 | 11.88
153 | 8 | Sunday | 1.15 | 1.15 | 1.035 | 0.8694 | 0.8694 | 3.8333 | 2.898 | 10.4328 | 3.174 |  | 3.45 | 12.42
154 | 9 | Sunday | 1.2 | 1.2 | 1.08 | 0.9072 | 0.9072 | 4 | 3.024 | 10.8864 | 3.312 |  | 3.6 | 12.96
155 | 10 | Sunday | 1.25 | 1.25 | 1.125 | 0.945 | 0.945 | 4.1667 | 3.15 | 11.34 | 3.45 |  | 3.75 | 13.5
156 | 11 | Sunday | 1.3 | 1.3 | 1.17 | 0.9828 | 0.9828 | 4.3333 | 3.276 | 11.7936 | 3.588 |  | 3.9 | 14.04
157 | 12 | Sunday | 1.35 | 1.35 | 1.215 | 1.0206 | 1.0206 | 4.5 | 3.402 | 12.2472 | 3.726 |  | 4.05 | 14.58
158 | 13 | Sunday | 1.4 | 1.4 | 1.26 | 1.0584 | 1.0584 | 4.6667 | 3.528 | 12.7008 | 3.864 |  | 4.2 | 15.12
159 | 14 | Sunday | 1.45 | 1.35 | 1.215 | 1.0206 | 1.0206 | 4.5 | 3.402 | 12.2472 | 3.726 |  | 4.05 | 14.58
160 | 15 | Sunday | 1.5 | 1.4 | 1.26 | 1.0584 | 1.0584 | 4.6667 | 3.528 | 12.7008 | 3.864 |  | 4.2 | 15.12
161 | 16 | Sunday | 1.55 | 1.6 | 1.44 | 1.2096 | 1.2096 | 5.3333 | 4.032 | 14.5152 | 4.416 |  | 4.8 | 17.28
162 | 17 | Sunday | 1.6 | 1.55 | 1.395 | 1.1718 | 1.1718 | 5.1667 | 3.906 | 14.0616 | 4.278 |  | 4.65 | 16.74
163 | 18 | Sunday | 1.65 | 1.65 | 1.485 | 1.2474 | 1.2474 | 5.5 | 4.158 | 14.9688 | 4.554 |  | 4.95 | 17.82
164 | 19 | Sunday | 1.54 | 1.54 | 1.386 | 1.1642 | 1.1642 | 5.1333 | 3.8808 | 13.9709 | 4.2504 |  | 4.62 | 16.632
165 | 20 | Sunday | 1.43 | 1.43 | 1.287 | 1.0811 | 1.0811 | 4.7667 | 3.6036 | 12.973 | 3.9468 |  | 4.29 | 15.444
166 | 21 | Sunday | 1.32 | 1.32 | 1.188 | 0.99792 | 0.99792 | 4.4 | 3.3264 | 11.975 | 3.6432 |  | 3.96 | 14.256
167 | 22 | Sunday | 1.21 | 1.21 | 1.089 | 0.91476 | 0.91476 | 4.0333 | 3.0492 | 10.9771 | 3.3396 |  | 3.63 | 13.068
168 | 23 | Sunday | 1.1 | 1.1 | 0.99 | 0.8316 | 0.8316 | 3.6667 | 2.772 | 9.9792 | 3.036 |  | 3.3 | 11.88
|  |  | 222.4 | 221.0034 |  | 167.0786 | 167.0786 |  | 556.9286 | 2004.943 | 609.9694 |  | 663.0103 | 2386.837
Note on G2: % reduction of summer load
Note on L2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Average of summer + winter coefficients

## Thermal Store Sizing
Daily Heat Release
| Winter |  |  |  |  | Summer
| MWh/day |  |  |  |  | MWh/day
Monday | 87.801 |  |  |  |  | 104.525
Tuesday | 84.2112 |  |  |  |  | 100.2514
Wednesday | 86.5678 |  |  |  |  | 103.0569
Thursday | 79.9785 |  |  |  |  | 95.2125
Friday | 73.1029 |  |  |  |  | 87.0273
Saturday | 71.5572 |  |  |  |  | 85.1871
Sunday | 73.71 |  |  |  |  | 87.75
Total | 556.9286 |  |  |  |  | 663.0103
Max daily winter heat release | Q | 87.801 | MWh/day
|  | 316083.6 | MJ/day
Thermal store operating temperature range | dt | 10 | °K |  | CheckSum
Water specific heat capacity | cp | 4.18 | kJ/kg°K | MJ/t°K | 316083600
Thermal store mass | m | 7561.8086 | tonnes | m = Q/(cp x dt) | 7561808.6124
Equivalent volume |  | 7561.8086 | m3 | Cross reference with literature
Cube side length |  | 19.628 | m

## R410a Enthalpy
Evaporator Temp | 10 | °C
Condensor Temp | 35 | °C
Superheat | 5 | °C
Intercooler superheat (2') | 2 | °C
Compressor Efficiency | 0%
§
|  | Saturated | Single Stage | Two Stage
Pc | bar(a) | 22 | 22 | 22
Pi | bar(a) |  |  | 15.5563
Pe | bar(a) | 11 | 11 | 11
h6 | kJ/kg |  | 260 | 260
h5 | kJ/kg |  | 260 | 260
h4 | kJ/kg |  |  | 438
h3 | kJ/kg |  | 448
h2' | kJ/kg |  |  | 430
h2 | kJ/kg |  |  | 439
h1 | kJ/kg |  | 432 | 432
T2' | °C |  |  | 22
T2 | °C |  |  | 29
T1 | °C |  |  | 15
T4 | °C |  |  | 41
CoPref |  |  | 10.75 | 11.4667 | 6.25%

## Winter Energy Calcs
| Winter Cooler Duty | Refrigerant Mass Flow Rate | Intercooler Heat Rejection | Stage 1 Compressor Power | Stage 2 Compressor Power | Total Compressor Power | Single Stage Compressor Power | 2-Stage Improvement
|  | ṁ=Cooler Duty/(h1-h6) | Qi=ṁ(h2-h2') | Qcp1=ṁ(h1-h2) | Qcp2=ṁ(h2'-h4) | Qcp1+Qcp2
Hours | kJ/s | kg/s | kJ/s | kJ/s | kJ/s | kJ/s | kJ/s
1 | 7.7112 | 0.044833 | 0.40349 | 0.31383 | 0.35866 | 0.67249 | 0.71732 | 6.25%
2 | 7.2576 | 0.042195 | 0.37976 | 0.29537 | 0.33756 | 0.63293 | 0.67513 | 6.25%
3 | 7.7112 | 0.044833 | 0.40349 | 0.31383 | 0.35866 | 0.67249 | 0.71732 | 6.25%
4 | 8.1648 | 0.04747 | 0.42723 | 0.33229 | 0.37976 | 0.71205 | 0.75952 | 6.25%
5 | 9.2988 | 0.054063 | 0.48657 | 0.37844 | 0.4325 | 0.81094 | 0.865 | 6.25%
6 | 9.9792 | 0.058019 | 0.52217 | 0.40613 | 0.46415 | 0.87028 | 0.9283 | 6.25%
7 | 10.6596 | 0.061974 | 0.55777 | 0.43382 | 0.4958 | 0.92962 | 0.99159 | 6.25%
8 | 11.34 | 0.06593 | 0.59337 | 0.46151 | 0.52744 | 0.98895 | 1.0549 | 6.25%
9 | 12.0204 | 0.069886 | 0.62897 | 0.4892 | 0.55909 | 1.0483 | 1.1182 | 6.25%
10 | 12.7008 | 0.073842 | 0.66458 | 0.51689 | 0.59073 | 1.1076 | 1.1815 | 6.25%
11 | 13.3812 | 0.077798 | 0.70018 | 0.54458 | 0.62238 | 1.167 | 1.2448 | 6.25%
12 | 14.0616 | 0.081753 | 0.73578 | 0.57227 | 0.65403 | 1.2263 | 1.3081 | 6.25%
13 | 14.742 | 0.085709 | 0.77138 | 0.59997 | 0.68567 | 1.2856 | 1.3713 | 6.25%
14 | 15.4224 | 0.089665 | 0.80699 | 0.62766 | 0.71732 | 1.345 | 1.4346 | 6.25%
15 | 14.9688 | 0.087028 | 0.78325 | 0.6092 | 0.69622 | 1.3054 | 1.3924 | 6.25%
16 | 15.5736 | 0.090544 | 0.8149 | 0.63381 | 0.72435 | 1.3582 | 1.4487 | 6.25%
17 | 17.6904 | 0.10285 | 0.92566 | 0.71996 | 0.82281 | 1.5428 | 1.6456 | 6.25%
18 | 17.2368 | 0.10021 | 0.90193 | 0.7015 | 0.80171 | 1.5032 | 1.6034 | 6.25%
19 | 18.144 | 0.10549 | 0.9494 | 0.73842 | 0.84391 | 1.5823 | 1.6878 | 6.25%
20 | 17.2368 | 0.10021 | 0.90193 | 0.7015 | 0.80171 | 1.5032 | 1.6034 | 6.25%
21 | 18.5976 | 0.10813 | 0.97313 | 0.75688 | 0.865 | 1.6219 | 1.73 | 6.25%
22 | 16.3296 | 0.09494 | 0.85446 | 0.66458 | 0.75952 | 1.4241 | 1.519 | 6.25%
23 | 14.0616 | 0.081753 | 0.73578 | 0.57227 | 0.65403 | 1.2263 | 1.3081 | 6.25%
24 | 11.7936 | 0.068567 | 0.61711 | 0.47997 | 0.54854 | 1.0285 | 1.0971 | 6.25%
25 | 7.7112 | 0.044833 | 0.40349 | 0.31383 | 0.35866 | 0.67249 | 0.71732 | 6.25%
26 | 7.2576 | 0.042195 | 0.37976 | 0.29537 | 0.33756 | 0.63293 | 0.67513 | 6.25%
27 | 7.8019 | 0.04536 | 0.40824 | 0.31752 | 0.36288 | 0.6804 | 0.72576 | 6.25%
28 | 8.1648 | 0.04747 | 0.42723 | 0.33229 | 0.37976 | 0.71205 | 0.75952 | 6.25%
29 | 9.0072 | 0.052367 | 0.47131 | 0.36657 | 0.41894 | 0.78551 | 0.83788 | 6.25%
30 | 9.5904 | 0.055758 | 0.50182 | 0.39031 | 0.44607 | 0.83637 | 0.89213 | 6.25%
31 | 10.1736 | 0.059149 | 0.53234 | 0.41404 | 0.47319 | 0.88723 | 0.94638 | 6.25%
32 | 10.7568 | 0.06254 | 0.56286 | 0.43778 | 0.50032 | 0.93809 | 1.0006 | 6.25%
33 | 11.34 | 0.06593 | 0.59337 | 0.46151 | 0.52744 | 0.98895 | 1.0549 | 6.25%
34 | 11.9232 | 0.069321 | 0.62389 | 0.48525 | 0.55457 | 1.0398 | 1.1091 | 6.25%
35 | 12.5064 | 0.072712 | 0.6544 | 0.50898 | 0.58169 | 1.0907 | 1.1634 | 6.25%
36 | 13.0896 | 0.076102 | 0.68492 | 0.53272 | 0.60882 | 1.1415 | 1.2176 | 6.25%
37 | 13.6728 | 0.079493 | 0.71544 | 0.55645 | 0.63594 | 1.1924 | 1.2719 | 6.25%
38 | 14.256 | 0.082884 | 0.74595 | 0.58019 | 0.66307 | 1.2433 | 1.3261 | 6.25%
39 | 14.8392 | 0.086274 | 0.77647 | 0.60392 | 0.6902 | 1.2941 | 1.3804 | 6.25%
40 | 15.4224 | 0.089665 | 0.80699 | 0.62766 | 0.71732 | 1.345 | 1.4346 | 6.25%
41 | 14.9688 | 0.087028 | 0.78325 | 0.6092 | 0.69622 | 1.3054 | 1.3924 | 6.25%
42 | 15.876 | 0.092302 | 0.83072 | 0.64612 | 0.73842 | 1.3845 | 1.4768 | 6.25%
43 | 16.7832 | 0.097577 | 0.87819 | 0.68304 | 0.78061 | 1.4637 | 1.5612 | 6.25%
44 | 17.2368 | 0.10021 | 0.90193 | 0.7015 | 0.80171 | 1.5032 | 1.6034 | 6.25%
45 | 18.5976 | 0.10813 | 0.97313 | 0.75688 | 0.865 | 1.6219 | 1.73 | 6.25%
46 | 16.3296 | 0.09494 | 0.85446 | 0.66458 | 0.75952 | 1.4241 | 1.519 | 6.25%
47 | 14.0616 | 0.081753 | 0.73578 | 0.57227 | 0.65403 | 1.2263 | 1.3081 | 6.25%
48 | 11.7936 | 0.068567 | 0.61711 | 0.47997 | 0.54854 | 1.0285 | 1.0971 | 6.25%
49 | 7.7112 | 0.044833 | 0.40349 | 0.31383 | 0.35866 | 0.67249 | 0.71732 | 6.25%
50 | 7.2576 | 0.042195 | 0.37976 | 0.29537 | 0.33756 | 0.63293 | 0.67513 | 6.25%
51 | 7.7112 | 0.044833 | 0.40349 | 0.31383 | 0.35866 | 0.67249 | 0.71732 | 6.25%
52 | 8.1648 | 0.04747 | 0.42723 | 0.33229 | 0.37976 | 0.71205 | 0.75952 | 6.25%
53 | 9.1418 | 0.05315 | 0.47835 | 0.37205 | 0.4252 | 0.79725 | 0.8504 | 6.25%
54 | 9.7698 | 0.056801 | 0.51121 | 0.39761 | 0.45441 | 0.85202 | 0.90882 | 6.25%
55 | 10.3979 | 0.060453 | 0.54408 | 0.42317 | 0.48362 | 0.90679 | 0.96725 | 6.25%
56 | 11.026 | 0.064104 | 0.57694 | 0.44873 | 0.51284 | 0.96157 | 1.0257 | 6.25%
57 | 11.654 | 0.067756 | 0.6098 | 0.47429 | 0.54205 | 1.0163 | 1.0841 | 6.25%
58 | 12.2821 | 0.071408 | 0.64267 | 0.49985 | 0.57126 | 1.0711 | 1.1425 | 6.25%
59 | 12.9102 | 0.075059 | 0.67553 | 0.52541 | 0.60047 | 1.1259 | 1.2009 | 6.25%
60 | 13.5382 | 0.078711 | 0.70839 | 0.55097 | 0.62968 | 1.1807 | 1.2594 | 6.25%
61 | 14.1663 | 0.082362 | 0.74126 | 0.57653 | 0.6589 | 1.2354 | 1.3178 | 6.25%
62 | 14.7943 | 0.086014 | 0.77412 | 0.6021 | 0.68811 | 1.2902 | 1.3762 | 6.25%
63 | 15.4224 | 0.089665 | 0.80699 | 0.62766 | 0.71732 | 1.345 | 1.4346 | 6.25%
64 | 14.9688 | 0.087028 | 0.78325 | 0.6092 | 0.69622 | 1.3054 | 1.3924 | 6.25%
65 | 15.7853 | 0.091775 | 0.82597 | 0.64242 | 0.7342 | 1.3766 | 1.4684 | 6.25%
66 | 16.6018 | 0.096522 | 0.8687 | 0.67565 | 0.77217 | 1.4478 | 1.5443 | 6.25%
67 | 18.144 | 0.10549 | 0.9494 | 0.73842 | 0.84391 | 1.5823 | 1.6878 | 6.25%
68 | 18.144 | 0.10549 | 0.9494 | 0.73842 | 0.84391 | 1.5823 | 1.6878 | 6.25%
69 | 19.0512 | 0.11076 | 0.99687 | 0.77534 | 0.8861 | 1.6614 | 1.7722 | 6.25%
70 | 16.6925 | 0.097049 | 0.87344 | 0.67935 | 0.77639 | 1.4557 | 1.5528 | 6.25%
71 | 14.3338 | 0.083336 | 0.75002 | 0.58335 | 0.66669 | 1.25 | 1.3334 | 6.25%
72 | 11.975 | 0.069622 | 0.6266 | 0.48736 | 0.55698 | 1.0443 | 1.114 | 6.25%
73 | 7.7112 | 0.044833 | 0.40349 | 0.31383 | 0.35866 | 0.67249 | 0.71732 | 6.25%
74 | 7.2576 | 0.042195 | 0.37976 | 0.29537 | 0.33756 | 0.63293 | 0.67513 | 6.25%
75 | 7.7112 | 0.044833 | 0.40349 | 0.31383 | 0.35866 | 0.67249 | 0.71732 | 6.25%
76 | 8.1648 | 0.04747 | 0.42723 | 0.33229 | 0.37976 | 0.71205 | 0.75952 | 6.25%
77 | 9.072 | 0.052744 | 0.4747 | 0.36921 | 0.42195 | 0.79116 | 0.84391 | 6.25%
78 | 9.6768 | 0.05626 | 0.50634 | 0.39382 | 0.45008 | 0.84391 | 0.90017 | 6.25%
79 | 10.2816 | 0.059777 | 0.53799 | 0.41844 | 0.47821 | 0.89665 | 0.95643 | 6.25%
80 | 10.8864 | 0.063293 | 0.56964 | 0.44305 | 0.50634 | 0.9494 | 1.0127 | 6.25%
81 | 11.4912 | 0.066809 | 0.60128 | 0.46767 | 0.53447 | 1.0021 | 1.0689 | 6.25%
82 | 12.096 | 0.070326 | 0.63293 | 0.49228 | 0.5626 | 1.0549 | 1.1252 | 6.25%
83 | 12.7008 | 0.073842 | 0.66458 | 0.51689 | 0.59073 | 1.1076 | 1.1815 | 6.25%
84 | 13.3056 | 0.077358 | 0.69622 | 0.54151 | 0.61887 | 1.1604 | 1.2377 | 6.25%
85 | 13.9104 | 0.080874 | 0.72787 | 0.56612 | 0.647 | 1.2131 | 1.294 | 6.25%
86 | 14.5152 | 0.084391 | 0.75952 | 0.59073 | 0.67513 | 1.2659 | 1.3503 | 6.25%
87 | 14.0616 | 0.081753 | 0.73578 | 0.57227 | 0.65403 | 1.2263 | 1.3081 | 6.25%
88 | 15.12 | 0.087907 | 0.79116 | 0.61535 | 0.70326 | 1.3186 | 1.4065 | 6.25%
89 | 16.1784 | 0.09406 | 0.84654 | 0.65842 | 0.75248 | 1.4109 | 1.505 | 6.25%
90 | 17.2368 | 0.10021 | 0.90193 | 0.7015 | 0.80171 | 1.5032 | 1.6034 | 6.25%
91 | 15.9894 | 0.092962 | 0.83665 | 0.65073 | 0.74369 | 1.3944 | 1.4874 | 6.25%
92 | 14.742 | 0.085709 | 0.77138 | 0.59997 | 0.68567 | 1.2856 | 1.3713 | 6.25%
93 | 13.4946 | 0.078457 | 0.70611 | 0.5492 | 0.62766 | 1.1769 | 1.2553 | 6.25%
94 | 12.2472 | 0.071205 | 0.64084 | 0.49843 | 0.56964 | 1.0681 | 1.1393 | 6.25%
95 | 10.9998 | 0.063952 | 0.57557 | 0.44767 | 0.51162 | 0.95928 | 1.0232 | 6.25%
96 | 9.072 | 0.052744 | 0.4747 | 0.36921 | 0.42195 | 0.79116 | 0.84391 | 6.25%
97 | 7.7112 | 0.044833 | 0.40349 | 0.31383 | 0.35866 | 0.67249 | 0.71732 | 6.25%
98 | 7.2576 | 0.042195 | 0.37976 | 0.29537 | 0.33756 | 0.63293 | 0.67513 | 6.25%
99 | 7.7112 | 0.044833 | 0.40349 | 0.31383 | 0.35866 | 0.67249 | 0.71732 | 6.25%
100 | 8.1648 | 0.04747 | 0.42723 | 0.33229 | 0.37976 | 0.71205 | 0.75952 | 6.25%
101 | 8.9895 | 0.052265 | 0.47038 | 0.36585 | 0.41812 | 0.78397 | 0.83624 | 6.25%
102 | 9.5668 | 0.055621 | 0.50059 | 0.38935 | 0.44497 | 0.83432 | 0.88994 | 6.25%
103 | 10.1441 | 0.058978 | 0.5308 | 0.41284 | 0.47182 | 0.88466 | 0.94364 | 6.25%
104 | 10.7215 | 0.062334 | 0.56101 | 0.43634 | 0.49867 | 0.93501 | 0.99734 | 6.25%
105 | 11.2988 | 0.06569 | 0.59121 | 0.45983 | 0.52552 | 0.98536 | 1.051 | 6.25%
106 | 11.8761 | 0.069047 | 0.62142 | 0.48333 | 0.55238 | 1.0357 | 1.1048 | 6.25%
107 | 12.4534 | 0.072403 | 0.65163 | 0.50682 | 0.57923 | 1.0861 | 1.1585 | 6.25%
108 | 13.0307 | 0.07576 | 0.68184 | 0.53032 | 0.60608 | 1.1364 | 1.2122 | 6.25%
109 | 13.608 | 0.079116 | 0.71205 | 0.55381 | 0.63293 | 1.1867 | 1.2659 | 6.25%
110 | 13.3488 | 0.077609 | 0.69848 | 0.54327 | 0.62087 | 1.1641 | 1.2417 | 6.25%
111 | 13.0896 | 0.076102 | 0.68492 | 0.53272 | 0.60882 | 1.1415 | 1.2176 | 6.25%
112 | 12.8304 | 0.074595 | 0.67136 | 0.52217 | 0.59676 | 1.1189 | 1.1935 | 6.25%
113 | 12.5712 | 0.073088 | 0.6578 | 0.51162 | 0.58471 | 1.0963 | 1.1694 | 6.25%
114 | 12.312 | 0.071581 | 0.64423 | 0.50107 | 0.57265 | 1.0737 | 1.1453 | 6.25%
115 | 12.0528 | 0.070074 | 0.63067 | 0.49052 | 0.5606 | 1.0511 | 1.1212 | 6.25%
116 | 11.7936 | 0.068567 | 0.61711 | 0.47997 | 0.54854 | 1.0285 | 1.0971 | 6.25%
117 | 12.7008 | 0.073842 | 0.66458 | 0.51689 | 0.59073 | 1.1076 | 1.1815 | 6.25%
118 | 11.34 | 0.06593 | 0.59337 | 0.46151 | 0.52744 | 0.98895 | 1.0549 | 6.25%
119 | 9.9792 | 0.058019 | 0.52217 | 0.40613 | 0.46415 | 0.87028 | 0.9283 | 6.25%
120 | 8.6184 | 0.050107 | 0.45096 | 0.35075 | 0.40086 | 0.7516 | 0.80171 | 6.25%
121 | 7.2576 | 0.042195 | 0.37976 | 0.29537 | 0.33756 | 0.63293 | 0.67513 | 6.25%
122 | 7.2576 | 0.042195 | 0.37976 | 0.29537 | 0.33756 | 0.63293 | 0.67513 | 6.25%
123 | 7.776 | 0.045209 | 0.40688 | 0.31647 | 0.36167 | 0.67814 | 0.72335 | 6.25%
124 | 8.2944 | 0.048223 | 0.43401 | 0.33756 | 0.38579 | 0.72335 | 0.77157 | 6.25%
125 | 8.8128 | 0.051237 | 0.46113 | 0.35866 | 0.4099 | 0.76856 | 0.8198 | 6.25%
126 | 9.3312 | 0.054251 | 0.48826 | 0.37976 | 0.43401 | 0.81377 | 0.86802 | 6.25%
127 | 9.8496 | 0.057265 | 0.51539 | 0.40086 | 0.45812 | 0.85898 | 0.91624 | 6.25%
128 | 10.368 | 0.060279 | 0.54251 | 0.42195 | 0.48223 | 0.90419 | 0.96447 | 6.25%
129 | 10.8864 | 0.063293 | 0.56964 | 0.44305 | 0.50634 | 0.9494 | 1.0127 | 6.25%
130 | 11.4048 | 0.066307 | 0.59676 | 0.46415 | 0.53046 | 0.9946 | 1.0609 | 6.25%
131 | 11.9232 | 0.069321 | 0.62389 | 0.48525 | 0.55457 | 1.0398 | 1.1091 | 6.25%
132 | 12.4416 | 0.072335 | 0.65101 | 0.50634 | 0.57868 | 1.085 | 1.1574 | 6.25%
133 | 12.7008 | 0.073842 | 0.66458 | 0.51689 | 0.59073 | 1.1076 | 1.1815 | 6.25%
134 | 12.7008 | 0.073842 | 0.66458 | 0.51689 | 0.59073 | 1.1076 | 1.1815 | 6.25%
135 | 13.9968 | 0.081377 | 0.73239 | 0.56964 | 0.65101 | 1.2207 | 1.302 | 6.25%
136 | 14.5152 | 0.084391 | 0.75952 | 0.59073 | 0.67513 | 1.2659 | 1.3503 | 6.25%
137 | 13.7894 | 0.080171 | 0.72154 | 0.5612 | 0.64137 | 1.2026 | 1.2827 | 6.25%
138 | 13.0637 | 0.075952 | 0.68356 | 0.53166 | 0.60761 | 1.1393 | 1.2152 | 6.25%
139 | 12.7008 | 0.073842 | 0.66458 | 0.51689 | 0.59073 | 1.1076 | 1.1815 | 6.25%
140 | 11.6122 | 0.067513 | 0.60761 | 0.47259 | 0.5401 | 1.0127 | 1.0802 | 6.25%
141 | 10.8864 | 0.063293 | 0.56964 | 0.44305 | 0.50634 | 0.9494 | 1.0127 | 6.25%
142 | 10.1606 | 0.059073 | 0.53166 | 0.41351 | 0.47259 | 0.8861 | 0.94518 | 6.25%
143 | 8.1648 | 0.04747 | 0.42723 | 0.33229 | 0.37976 | 0.71205 | 0.75952 | 6.25%
144 | 7.7112 | 0.044833 | 0.40349 | 0.31383 | 0.35866 | 0.67249 | 0.71732 | 6.25%
145 | 7.2576 | 0.042195 | 0.37976 | 0.29537 | 0.33756 | 0.63293 | 0.67513 | 6.25%
146 | 7.2576 | 0.042195 | 0.37976 | 0.29537 | 0.33756 | 0.63293 | 0.67513 | 6.25%
147 | 7.7112 | 0.044833 | 0.40349 | 0.31383 | 0.35866 | 0.67249 | 0.71732 | 6.25%
148 | 8.1648 | 0.04747 | 0.42723 | 0.33229 | 0.37976 | 0.71205 | 0.75952 | 6.25%
149 | 8.6184 | 0.050107 | 0.45096 | 0.35075 | 0.40086 | 0.7516 | 0.80171 | 6.25%
150 | 9.072 | 0.052744 | 0.4747 | 0.36921 | 0.42195 | 0.79116 | 0.84391 | 6.25%
151 | 9.5256 | 0.055381 | 0.49843 | 0.38767 | 0.44305 | 0.83072 | 0.8861 | 6.25%
152 | 9.9792 | 0.058019 | 0.52217 | 0.40613 | 0.46415 | 0.87028 | 0.9283 | 6.25%
153 | 10.4328 | 0.060656 | 0.5459 | 0.42459 | 0.48525 | 0.90984 | 0.97049 | 6.25%
154 | 10.8864 | 0.063293 | 0.56964 | 0.44305 | 0.50634 | 0.9494 | 1.0127 | 6.25%
155 | 11.34 | 0.06593 | 0.59337 | 0.46151 | 0.52744 | 0.98895 | 1.0549 | 6.25%
156 | 11.7936 | 0.068567 | 0.61711 | 0.47997 | 0.54854 | 1.0285 | 1.0971 | 6.25%
157 | 12.2472 | 0.071205 | 0.64084 | 0.49843 | 0.56964 | 1.0681 | 1.1393 | 6.25%
158 | 12.7008 | 0.073842 | 0.66458 | 0.51689 | 0.59073 | 1.1076 | 1.1815 | 6.25%
159 | 12.2472 | 0.071205 | 0.64084 | 0.49843 | 0.56964 | 1.0681 | 1.1393 | 6.25%
160 | 12.7008 | 0.073842 | 0.66458 | 0.51689 | 0.59073 | 1.1076 | 1.1815 | 6.25%
161 | 14.5152 | 0.084391 | 0.75952 | 0.59073 | 0.67513 | 1.2659 | 1.3503 | 6.25%
162 | 14.0616 | 0.081753 | 0.73578 | 0.57227 | 0.65403 | 1.2263 | 1.3081 | 6.25%
163 | 14.9688 | 0.087028 | 0.78325 | 0.6092 | 0.69622 | 1.3054 | 1.3924 | 6.25%
164 | 13.9709 | 0.081226 | 0.73103 | 0.56858 | 0.64981 | 1.2184 | 1.2996 | 6.25%
165 | 12.973 | 0.075424 | 0.67882 | 0.52797 | 0.60339 | 1.1314 | 1.2068 | 6.25%
166 | 11.975 | 0.069622 | 0.6266 | 0.48736 | 0.55698 | 1.0443 | 1.114 | 6.25%
167 | 10.9771 | 0.06382 | 0.57438 | 0.44674 | 0.51056 | 0.95731 | 1.0211 | 6.25%
168 | 9.9792 | 0.058019 | 0.52217 | 0.40613 | 0.46415 | 0.87028 | 0.9283 | 6.25%

## DC Cooler Heat Released
|  |  |  | Cooling Duty (MWh) |  |  |  | Heat Released (MWh) |  |  | DN250 max | 6.13 | MW
|  |  | Total | 556.9286 | 609.9694 | 663.0103 |  | 656.3802 | 705.6379 | 756.8187
|  |  | Max | 5.292 | 5.796 | 6.3 |  | 6.237 | 6.7051 | 7.1914
|  |  | Min | 2.016 | 2.208 | 2.4 |  | 2.376 | 2.5543 | 2.7396
|  |  | Average | 3.3151 | 3.6308 | 3.9465 |  | 3.907 | 4.2002 | 4.5049
[7 empty] | > max design | 1
0.5952%
Count | Day | Time | WE/WD | Winter | Spring/Autumn | Summer |  | Winter | Spring/Autumn | Summer
1 | Wednesday | 0:00 | weekday | 2.142 | 2.346 | 2.55 |  | 2.5245 | 2.7139 | 2.9108
2 | Wednesday | 1:00 | weekday | 2.016 | 2.208 | 2.4 |  | 2.376 | 2.5543 | 2.7396
3 | Wednesday | 2:00 | weekday | 2.142 | 2.346 | 2.55 |  | 2.5245 | 2.7139 | 2.9108
4 | Wednesday | 3:00 | weekday | 2.268 | 2.484 | 2.7 |  | 2.673 | 2.8736 | 3.082
5 | Wednesday | 4:00 | weekday | 2.583 | 2.829 | 3.075 |  | 3.0442 | 3.2727 | 3.5101
6 | Wednesday | 5:00 | weekday | 2.772 | 3.036 | 3.3 |  | 3.267 | 3.5122 | 3.7669
7 | Wednesday | 6:00 | weekday | 2.961 | 3.243 | 3.525 |  | 3.4897 | 3.7516 | 4.0237
8 | Wednesday | 7:00 | weekday | 3.15 | 3.45 | 3.75 |  | 3.7125 | 3.9911 | 4.2806
9 | Wednesday | 8:00 | weekday | 3.339 | 3.657 | 3.975 |  | 3.9352 | 4.2306 | 4.5374
10 | Wednesday | 9:00 | weekday | 3.528 | 3.864 | 4.2 |  | 4.158 | 4.47 | 4.7943
11 | Wednesday | 10:00 | weekday | 3.717 | 4.071 | 4.425 |  | 4.3807 | 4.7095 | 5.0511
12 | Wednesday | 11:00 | weekday | 3.906 | 4.278 | 4.65 |  | 4.6035 | 4.949 | 5.3079
13 | Wednesday | 12:00 | weekday | 4.095 | 4.485 | 4.875 |  | 4.8262 | 5.1884 | 5.5648
14 | Wednesday | 13:00 | weekday | 4.284 | 4.692 | 5.1 |  | 5.049 | 5.4279 | 5.8216
15 | Wednesday | 14:00 | weekday | 4.158 | 4.554 | 4.95 |  | 4.9005 | 5.2683 | 5.6504
16 | Wednesday | 15:00 | weekday | 4.326 | 4.738 | 5.15 |  | 5.0985 | 5.4811 | 5.8787
17 | Wednesday | 16:00 | weekday | 4.914 | 5.382 | 5.85 |  | 5.7915 | 6.2261 | 6.6777
18 | Wednesday | 17:00 | weekday | 4.788 | 5.244 | 5.7 |  | 5.643 | 6.0665 | 6.5065
19 | Wednesday | 18:00 | weekday | 5.04 | 5.52 | 6 |  | 5.94 | 6.3858 | 6.8489
20 | Wednesday | 19:00 | weekday | 4.788 | 5.244 | 5.7 |  | 5.643 | 6.0665 | 6.5065
21 | Wednesday | 20:00 | weekday | 5.166 | 5.658 | 6.15 |  | 6.0885 | 6.5454 | 7.0202
22 | Wednesday | 21:00 | weekday | 4.536 | 4.968 | 5.4 |  | 5.346 | 5.7472 | 6.164
23 | Wednesday | 22:00 | weekday | 3.906 | 4.278 | 4.65 |  | 4.6035 | 4.949 | 5.3079
24 | Wednesday | 23:00 | weekday | 3.276 | 3.588 | 3.9 |  | 3.861 | 4.1507 | 4.4518
25 | Thursday | 24:00 | weekday | 2.142 | 2.346 | 2.55 |  | 2.5245 | 2.7139 | 2.9108
26 | Thursday | 25:00 | weekday | 2.016 | 2.208 | 2.4 |  | 2.376 | 2.5543 | 2.7396
27 | Thursday | 26:00 | weekday | 2.1672 | 2.3736 | 2.58 |  | 2.5542 | 2.7459 | 2.945
28 | Thursday | 27:00 | weekday | 2.268 | 2.484 | 2.7 |  | 2.673 | 2.8736 | 3.082
29 | Thursday | 28:00 | weekday | 2.502 | 2.7403 | 2.9786 |  | 2.9488 | 3.1701 | 3.4
30 | Thursday | 29:00 | weekday | 2.664 | 2.9177 | 3.1714 |  | 3.1397 | 3.3753 | 3.6201
31 | Thursday | 30:00 | weekday | 2.826 | 3.0951 | 3.3643 |  | 3.3306 | 3.5806 | 3.8403
32 | Thursday | 31:00 | weekday | 2.988 | 3.2726 | 3.5571 |  | 3.5216 | 3.7858 | 4.0604
33 | Thursday | 32:00 | weekday | 3.15 | 3.45 | 3.75 |  | 3.7125 | 3.9911 | 4.2806
34 | Thursday | 33:00 | weekday | 3.312 | 3.6274 | 3.9429 |  | 3.9034 | 4.1964 | 4.5007
35 | Thursday | 34:00 | weekday | 3.474 | 3.8049 | 4.1357 |  | 4.0944 | 4.4016 | 4.7209
36 | Thursday | 35:00 | weekday | 3.636 | 3.9823 | 4.3286 |  | 4.2853 | 4.6069 | 4.941
37 | Thursday | 36:00 | weekday | 3.798 | 4.1597 | 4.5214 |  | 4.4762 | 4.8121 | 5.1612
38 | Thursday | 37:00 | weekday | 3.96 | 4.3371 | 4.7143 |  | 4.6671 | 5.0174 | 5.3813
39 | Thursday | 38:00 | weekday | 4.122 | 4.5146 | 4.9071 |  | 4.8581 | 5.2226 | 5.6014
40 | Thursday | 39:00 | weekday | 4.284 | 4.692 | 5.1 |  | 5.049 | 5.4279 | 5.8216
41 | Thursday | 40:00 | weekday | 4.158 | 4.554 | 4.95 |  | 4.9005 | 5.2683 | 5.6504
42 | Thursday | 41:00 | weekday | 4.41 | 4.83 | 5.25 |  | 5.1975 | 5.5875 | 5.9928
43 | Thursday | 42:00 | weekday | 4.662 | 5.106 | 5.55 |  | 5.4945 | 5.9068 | 6.3353
44 | Thursday | 43:00 | weekday | 4.788 | 5.244 | 5.7 |  | 5.643 | 6.0665 | 6.5065
45 | Thursday | 44:00 | weekday | 5.166 | 5.658 | 6.15 |  | 6.0885 | 6.5454 | 7.0202
46 | Thursday | 45:00 | weekday | 4.536 | 4.968 | 5.4 |  | 5.346 | 5.7472 | 6.164
47 | Thursday | 46:00 | weekday | 3.906 | 4.278 | 4.65 |  | 4.6035 | 4.949 | 5.3079
48 | Thursday | 47:00 | weekday | 3.276 | 3.588 | 3.9 |  | 3.861 | 4.1507 | 4.4518
49 | Friday | 48:00 | weekday | 2.142 | 2.346 | 2.55 |  | 2.5245 | 2.7139 | 2.9108
50 | Friday | 49:00 | weekday | 2.016 | 2.208 | 2.4 |  | 2.376 | 2.5543 | 2.7396
51 | Friday | 50:00 | weekday | 2.142 | 2.346 | 2.55 |  | 2.5245 | 2.7139 | 2.9108
52 | Friday | 51:00 | weekday | 2.268 | 2.484 | 2.7 |  | 2.673 | 2.8736 | 3.082
53 | Friday | 52:00 | weekday | 2.5394 | 2.7812 | 3.0231 |  | 2.9928 | 3.2174 | 3.4508
54 | Friday | 53:00 | weekday | 2.7138 | 2.9723 | 3.2308 |  | 3.1985 | 3.4385 | 3.6879
55 | Friday | 54:00 | weekday | 2.8883 | 3.1634 | 3.4385 |  | 3.4041 | 3.6595 | 3.925
56 | Friday | 55:00 | weekday | 3.0628 | 3.3545 | 3.6462 |  | 3.6097 | 3.8806 | 4.162
57 | Friday | 56:00 | weekday | 3.2372 | 3.5455 | 3.8538 |  | 3.8153 | 4.1016 | 4.3991
58 | Friday | 57:00 | weekday | 3.4117 | 3.7366 | 4.0615 |  | 4.0209 | 4.3227 | 4.6362
59 | Friday | 58:00 | weekday | 3.5862 | 3.9277 | 4.2692 |  | 4.2265 | 4.5437 | 4.8733
60 | Friday | 59:00 | weekday | 3.7606 | 4.1188 | 4.4769 |  | 4.4322 | 4.7648 | 5.1104
61 | Friday | 60:00 | weekday | 3.9351 | 4.3098 | 4.6846 |  | 4.6378 | 4.9858 | 5.3474
62 | Friday | 61:00 | weekday | 4.1095 | 4.5009 | 4.8923 |  | 4.8434 | 5.2069 | 5.5845
63 | Friday | 62:00 | weekday | 4.284 | 4.692 | 5.1 |  | 5.049 | 5.4279 | 5.8216
64 | Friday | 63:00 | weekday | 4.158 | 4.554 | 4.95 |  | 4.9005 | 5.2683 | 5.6504
65 | Friday | 64:00 | weekday | 4.3848 | 4.8024 | 5.22 |  | 5.1678 | 5.5556 | 5.9586
66 | Friday | 65:00 | weekday | 4.6116 | 5.0508 | 5.49 |  | 5.4351 | 5.843 | 6.2668
67 | Friday | 66:00 | weekday | 5.04 | 5.52 | 6 |  | 5.94 | 6.3858 | 6.8489
68 | Friday | 67:00 | weekday | 5.04 | 5.52 | 6 |  | 5.94 | 6.3858 | 6.8489
69 | Friday | 68:00 | weekday | 5.292 | 5.796 | 6.3 |  | 6.237 | 6.7051 | 7.1914
70 | Friday | 69:00 | weekday | 4.6368 | 5.0784 | 5.52 |  | 5.4648 | 5.8749 | 6.301
71 | Friday | 70:00 | weekday | 3.9816 | 4.3608 | 4.74 |  | 4.6926 | 5.0448 | 5.4107
72 | Friday | 71:00 | weekday | 3.3264 | 3.6432 | 3.96 |  | 3.9204 | 4.2146 | 4.5203
73 | Saturday | 72:00 | weekend | 2.142 | 2.346 | 2.55 |  | 2.5245 | 2.7139 | 2.9108
74 | Saturday | 73:00 | weekend | 2.016 | 2.208 | 2.4 |  | 2.376 | 2.5543 | 2.7396
75 | Saturday | 74:00 | weekend | 2.142 | 2.346 | 2.55 |  | 2.5245 | 2.7139 | 2.9108
76 | Saturday | 75:00 | weekend | 2.268 | 2.484 | 2.7 |  | 2.673 | 2.8736 | 3.082
77 | Saturday | 76:00 | weekend | 2.52 | 2.76 | 3 |  | 2.97 | 3.1929 | 3.4245
78 | Saturday | 77:00 | weekend | 2.688 | 2.944 | 3.2 |  | 3.168 | 3.4057 | 3.6528
79 | Saturday | 78:00 | weekend | 2.856 | 3.128 | 3.4 |  | 3.366 | 3.6186 | 3.8811
80 | Saturday | 79:00 | weekend | 3.024 | 3.312 | 3.6 |  | 3.564 | 3.8315 | 4.1094
81 | Saturday | 80:00 | weekend | 3.192 | 3.496 | 3.8 |  | 3.762 | 4.0443 | 4.3377
82 | Saturday | 81:00 | weekend | 3.36 | 3.68 | 4 |  | 3.96 | 4.2572 | 4.566
83 | Saturday | 82:00 | weekend | 3.528 | 3.864 | 4.2 |  | 4.158 | 4.47 | 4.7943
84 | Saturday | 83:00 | weekend | 3.696 | 4.048 | 4.4 |  | 4.356 | 4.6829 | 5.0225
85 | Saturday | 84:00 | weekend | 3.864 | 4.232 | 4.6 |  | 4.554 | 4.8958 | 5.2508
86 | Saturday | 85:00 | weekend | 4.032 | 4.416 | 4.8 |  | 4.752 | 5.1086 | 5.4791
87 | Saturday | 86:00 | weekend | 3.906 | 4.278 | 4.65 |  | 4.6035 | 4.949 | 5.3079
88 | Saturday | 87:00 | weekend | 4.2 | 4.6 | 5 |  | 4.95 | 5.3215 | 5.7074
89 | Saturday | 88:00 | weekend | 4.494 | 4.922 | 5.35 |  | 5.2965 | 5.694 | 6.107
90 | Saturday | 89:00 | weekend | 4.788 | 5.244 | 5.7 |  | 5.643 | 6.0665 | 6.5065
91 | Saturday | 90:00 | weekend | 4.4415 | 4.8645 | 5.2875 |  | 5.2346 | 5.6275 | 6.0356
92 | Saturday | 91:00 | weekend | 4.095 | 4.485 | 4.875 |  | 4.8262 | 5.1884 | 5.5648
93 | Saturday | 92:00 | weekend | 3.7485 | 4.1055 | 4.4625 |  | 4.4179 | 4.7494 | 5.0939
94 | Saturday | 93:00 | weekend | 3.402 | 3.726 | 4.05 |  | 4.0095 | 4.3104 | 4.623
95 | Saturday | 94:00 | weekend | 3.0555 | 3.3465 | 3.6375 |  | 3.6011 | 3.8714 | 4.1522
96 | Saturday | 95:00 | weekend | 2.52 | 2.76 | 3 |  | 2.97 | 3.1929 | 3.4245
97 | Sunday | 96:00 | weekend | 2.142 | 2.346 | 2.55 |  | 2.5245 | 2.7139 | 2.9108
98 | Sunday | 97:00 | weekend | 2.016 | 2.208 | 2.4 |  | 2.376 | 2.5543 | 2.7396
99 | Sunday | 98:00 | weekend | 2.142 | 2.346 | 2.55 |  | 2.5245 | 2.7139 | 2.9108
100 | Sunday | 99:00 | weekend | 2.268 | 2.484 | 2.7 |  | 2.673 | 2.8736 | 3.082
101 | Sunday | 100:00 | weekend | 2.4971 | 2.7349 | 2.9727 |  | 2.943 | 3.1639 | 3.3933
102 | Sunday | 101:00 | weekend | 2.6575 | 2.9105 | 3.1636 |  | 3.132 | 3.367 | 3.6113
103 | Sunday | 102:00 | weekend | 2.8178 | 3.0862 | 3.3545 |  | 3.321 | 3.5702 | 3.8292
104 | Sunday | 103:00 | weekend | 2.9782 | 3.2618 | 3.5455 |  | 3.51 | 3.7734 | 4.0471
105 | Sunday | 104:00 | weekend | 3.1385 | 3.4375 | 3.7364 |  | 3.699 | 3.9766 | 4.265
106 | Sunday | 105:00 | weekend | 3.2989 | 3.6131 | 3.9273 |  | 3.888 | 4.1798 | 4.4829
107 | Sunday | 106:00 | weekend | 3.4593 | 3.7887 | 4.1182 |  | 4.077 | 4.383 | 4.7009
108 | Sunday | 107:00 | weekend | 3.6196 | 3.9644 | 4.3091 |  | 4.266 | 4.5861 | 4.9188
109 | Sunday | 108:00 | weekend | 3.78 | 4.14 | 4.5 |  | 4.455 | 4.7893 | 5.1367
110 | Sunday | 109:00 | weekend | 3.708 | 4.0611 | 4.4143 |  | 4.3701 | 4.6981 | 5.0389
111 | Sunday | 110:00 | weekend | 3.636 | 3.9823 | 4.3286 |  | 4.2853 | 4.6069 | 4.941
112 | Sunday | 111:00 | weekend | 3.564 | 3.9034 | 4.2429 |  | 4.2004 | 4.5156 | 4.8432
113 | Sunday | 112:00 | weekend | 3.492 | 3.8246 | 4.1571 |  | 4.1156 | 4.4244 | 4.7453
114 | Sunday | 113:00 | weekend | 3.42 | 3.7457 | 4.0714 |  | 4.0307 | 4.3332 | 4.6475
115 | Sunday | 114:00 | weekend | 3.348 | 3.6669 | 3.9857 |  | 3.9459 | 4.242 | 4.5496
116 | Sunday | 115:00 | weekend | 3.276 | 3.588 | 3.9 |  | 3.861 | 4.1507 | 4.4518
117 | Sunday | 116:00 | weekend | 3.528 | 3.864 | 4.2 |  | 4.158 | 4.47 | 4.7943
118 | Sunday | 117:00 | weekend | 3.15 | 3.45 | 3.75 |  | 3.7125 | 3.9911 | 4.2806
119 | Sunday | 118:00 | weekend | 2.772 | 3.036 | 3.3 |  | 3.267 | 3.5122 | 3.7669
120 | Sunday | 119:00 | weekend | 2.394 | 2.622 | 2.85 |  | 2.8215 | 3.0332 | 3.2532
121 | Monday | 120:00 | weekday | 2.016 | 2.208 | 2.4 |  | 2.376 | 2.5543 | 2.7396
122 | Monday | 121:00 | weekday | 2.016 | 2.208 | 2.4 |  | 2.376 | 2.5543 | 2.7396
123 | Monday | 122:00 | weekday | 2.16 | 2.3657 | 2.5714 |  | 2.5457 | 2.7368 | 2.9353
124 | Monday | 123:00 | weekday | 2.304 | 2.5234 | 2.7429 |  | 2.7154 | 2.9192 | 3.1309
125 | Monday | 124:00 | weekday | 2.448 | 2.6811 | 2.9143 |  | 2.8851 | 3.1017 | 3.3266
126 | Monday | 125:00 | weekday | 2.592 | 2.8389 | 3.0857 |  | 3.0549 | 3.2841 | 3.5223
127 | Monday | 126:00 | weekday | 2.736 | 2.9966 | 3.2571 |  | 3.2246 | 3.4666 | 3.718
128 | Monday | 127:00 | weekday | 2.88 | 3.1543 | 3.4286 |  | 3.3943 | 3.649 | 3.9137
129 | Monday | 128:00 | weekday | 3.024 | 3.312 | 3.6 |  | 3.564 | 3.8315 | 4.1094
130 | Monday | 129:00 | weekday | 3.168 | 3.4697 | 3.7714 |  | 3.7337 | 4.0139 | 4.305
131 | Monday | 130:00 | weekday | 3.312 | 3.6274 | 3.9429 |  | 3.9034 | 4.1964 | 4.5007
132 | Monday | 131:00 | weekday | 3.456 | 3.7851 | 4.1143 |  | 4.0731 | 4.3788 | 4.6964
133 | Monday | 132:00 | weekday | 3.528 | 3.864 | 4.2 |  | 4.158 | 4.47 | 4.7943
134 | Monday | 133:00 | weekday | 3.528 | 3.864 | 4.2 |  | 4.158 | 4.47 | 4.7943
135 | Monday | 134:00 | weekday | 3.888 | 4.2583 | 4.6286 |  | 4.5823 | 4.9262 | 5.2835
136 | Monday | 135:00 | weekday | 4.032 | 4.416 | 4.8 |  | 4.752 | 5.1086 | 5.4791
137 | Monday | 136:00 | weekday | 3.8304 | 4.1952 | 4.56 |  | 4.5144 | 4.8532 | 5.2052
138 | Monday | 137:00 | weekday | 3.6288 | 3.9744 | 4.32 |  | 4.2768 | 4.5978 | 4.9312
139 | Monday | 138:00 | weekday | 3.528 | 3.864 | 4.2 |  | 4.158 | 4.47 | 4.7943
140 | Monday | 139:00 | weekday | 3.2256 | 3.5328 | 3.84 |  | 3.8016 | 4.0869 | 4.3833
141 | Monday | 140:00 | weekday | 3.024 | 3.312 | 3.6 |  | 3.564 | 3.8315 | 4.1094
142 | Monday | 141:00 | weekday | 2.8224 | 3.0912 | 3.36 |  | 3.3264 | 3.576 | 3.8354
143 | Monday | 142:00 | weekday | 2.268 | 2.484 | 2.7 |  | 2.673 | 2.8736 | 3.082
144 | Monday | 143:00 | weekday | 2.142 | 2.346 | 2.55 |  | 2.5245 | 2.7139 | 2.9108
145 | Tueday | 144:00 | weekday | 2.016 | 2.208 | 2.4 |  | 2.376 | 2.5543 | 2.7396
146 | Tueday | 145:00 | weekday | 2.016 | 2.208 | 2.4 |  | 2.376 | 2.5543 | 2.7396
147 | Tueday | 146:00 | weekday | 2.142 | 2.346 | 2.55 |  | 2.5245 | 2.7139 | 2.9108
148 | Tueday | 147:00 | weekday | 2.268 | 2.484 | 2.7 |  | 2.673 | 2.8736 | 3.082
149 | Tueday | 148:00 | weekday | 2.394 | 2.622 | 2.85 |  | 2.8215 | 3.0332 | 3.2532
150 | Tueday | 149:00 | weekday | 2.52 | 2.76 | 3 |  | 2.97 | 3.1929 | 3.4245
151 | Tueday | 150:00 | weekday | 2.646 | 2.898 | 3.15 |  | 3.1185 | 3.3525 | 3.5957
152 | Tueday | 151:00 | weekday | 2.772 | 3.036 | 3.3 |  | 3.267 | 3.5122 | 3.7669
153 | Tueday | 152:00 | weekday | 2.898 | 3.174 | 3.45 |  | 3.4155 | 3.6718 | 3.9381
154 | Tueday | 153:00 | weekday | 3.024 | 3.312 | 3.6 |  | 3.564 | 3.8315 | 4.1094
155 | Tueday | 154:00 | weekday | 3.15 | 3.45 | 3.75 |  | 3.7125 | 3.9911 | 4.2806
156 | Tueday | 155:00 | weekday | 3.276 | 3.588 | 3.9 |  | 3.861 | 4.1507 | 4.4518
157 | Tueday | 156:00 | weekday | 3.402 | 3.726 | 4.05 |  | 4.0095 | 4.3104 | 4.623
158 | Tueday | 157:00 | weekday | 3.528 | 3.864 | 4.2 |  | 4.158 | 4.47 | 4.7943
159 | Tueday | 158:00 | weekday | 3.402 | 3.726 | 4.05 |  | 4.0095 | 4.3104 | 4.623
160 | Tueday | 159:00 | weekday | 3.528 | 3.864 | 4.2 |  | 4.158 | 4.47 | 4.7943
161 | Tueday | 160:00 | weekday | 4.032 | 4.416 | 4.8 |  | 4.752 | 5.1086 | 5.4791
162 | Tueday | 161:00 | weekday | 3.906 | 4.278 | 4.65 |  | 4.6035 | 4.949 | 5.3079
163 | Tueday | 162:00 | weekday | 4.158 | 4.554 | 4.95 |  | 4.9005 | 5.2683 | 5.6504
164 | Tueday | 163:00 | weekday | 3.8808 | 4.2504 | 4.62 |  | 4.5738 | 4.917 | 5.2737
165 | Tueday | 164:00 | weekday | 3.6036 | 3.9468 | 4.29 |  | 4.2471 | 4.5658 | 4.897
166 | Tueday | 165:00 | weekday | 3.3264 | 3.6432 | 3.96 |  | 3.9204 | 4.2146 | 4.5203
167 | Tueday | 166:00 | weekday | 3.0492 | 3.3396 | 3.63 |  | 3.5937 | 3.8634 | 4.1436
168 | Tueday | 167:00 | weekday | 2.772 | 3.036 | 3.3 |  | 3.267 | 3.5122 | 3.7669
Note on J2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Includes compressor power

## DC Cooler Power
Data Centre Refrigerator Compressor Electricity Consumption, P (MWh)
P =Qh/(CoP+1)
|  |  |  | Winter | Spring/Autumn | Summer
|  |  | CoP (from Home Heat Demand) | 4.6 | 5.3759 | 6.0677
|  |  | Total (MWh per week) | 99.4515 | 95.6685 | 93.8084
|  |  | Max | 0.945 | 0.90905 | 0.89138
Count | Day | Time | WE/WD | (MWh)
1 | Wednesday | 0:00 | weekday | 0.3825 | 0.36795 | 0.3608
2 | Wednesday | 1:00 | weekday | 0.36 | 0.34631 | 0.33957
3 | Wednesday | 2:00 | weekday | 0.3825 | 0.36795 | 0.3608
4 | Wednesday | 3:00 | weekday | 0.405 | 0.38959 | 0.38202
5 | Wednesday | 4:00 | weekday | 0.46125 | 0.4437 | 0.43508
6 | Wednesday | 5:00 | weekday | 0.495 | 0.47617 | 0.46691
7 | Wednesday | 6:00 | weekday | 0.52875 | 0.50864 | 0.49875
8 | Wednesday | 7:00 | weekday | 0.5625 | 0.5411 | 0.53058
9 | Wednesday | 8:00 | weekday | 0.59625 | 0.57357 | 0.56242
10 | Wednesday | 9:00 | weekday | 0.63 | 0.60604 | 0.59425
11 | Wednesday | 10:00 | weekday | 0.66375 | 0.6385 | 0.62609
12 | Wednesday | 11:00 | weekday | 0.6975 | 0.67097 | 0.65792
13 | Wednesday | 12:00 | weekday | 0.73125 | 0.70343 | 0.68976
14 | Wednesday | 13:00 | weekday | 0.765 | 0.7359 | 0.72159
15 | Wednesday | 14:00 | weekday | 0.7425 | 0.71426 | 0.70037
16 | Wednesday | 15:00 | weekday | 0.7725 | 0.74311 | 0.72867
17 | Wednesday | 16:00 | weekday | 0.8775 | 0.84412 | 0.82771
18 | Wednesday | 17:00 | weekday | 0.855 | 0.82248 | 0.80649
19 | Wednesday | 18:00 | weekday | 0.9 | 0.86576 | 0.84893
20 | Wednesday | 19:00 | weekday | 0.855 | 0.82248 | 0.80649
21 | Wednesday | 20:00 | weekday | 0.9225 | 0.88741 | 0.87015
22 | Wednesday | 21:00 | weekday | 0.81 | 0.77919 | 0.76404
23 | Wednesday | 22:00 | weekday | 0.6975 | 0.67097 | 0.65792
24 | Wednesday | 23:00 | weekday | 0.585 | 0.56275 | 0.55181
25 | Thursday | 24:00 | weekday | 0.3825 | 0.36795 | 0.3608
26 | Thursday | 25:00 | weekday | 0.36 | 0.34631 | 0.33957
27 | Thursday | 26:00 | weekday | 0.387 | 0.37228 | 0.36504
28 | Thursday | 27:00 | weekday | 0.405 | 0.38959 | 0.38202
29 | Thursday | 28:00 | weekday | 0.44679 | 0.42979 | 0.42143
30 | Thursday | 29:00 | weekday | 0.47571 | 0.45762 | 0.44872
31 | Thursday | 30:00 | weekday | 0.50464 | 0.48545 | 0.47601
32 | Thursday | 31:00 | weekday | 0.53357 | 0.51327 | 0.5033
33 | Thursday | 32:00 | weekday | 0.5625 | 0.5411 | 0.53058
34 | Thursday | 33:00 | weekday | 0.59143 | 0.56893 | 0.55787
35 | Thursday | 34:00 | weekday | 0.62036 | 0.59676 | 0.58516
36 | Thursday | 35:00 | weekday | 0.64929 | 0.62459 | 0.61244
37 | Thursday | 36:00 | weekday | 0.67821 | 0.65242 | 0.63973
38 | Thursday | 37:00 | weekday | 0.70714 | 0.68024 | 0.66702
39 | Thursday | 38:00 | weekday | 0.73607 | 0.70807 | 0.6943
40 | Thursday | 39:00 | weekday | 0.765 | 0.7359 | 0.72159
41 | Thursday | 40:00 | weekday | 0.7425 | 0.71426 | 0.70037
42 | Thursday | 41:00 | weekday | 0.7875 | 0.75754 | 0.74282
43 | Thursday | 42:00 | weekday | 0.8325 | 0.80083 | 0.78526
44 | Thursday | 43:00 | weekday | 0.855 | 0.82248 | 0.80649
45 | Thursday | 44:00 | weekday | 0.9225 | 0.88741 | 0.87015
46 | Thursday | 45:00 | weekday | 0.81 | 0.77919 | 0.76404
47 | Thursday | 46:00 | weekday | 0.6975 | 0.67097 | 0.65792
48 | Thursday | 47:00 | weekday | 0.585 | 0.56275 | 0.55181
49 | Friday | 48:00 | weekday | 0.3825 | 0.36795 | 0.3608
50 | Friday | 49:00 | weekday | 0.36 | 0.34631 | 0.33957
51 | Friday | 50:00 | weekday | 0.3825 | 0.36795 | 0.3608
52 | Friday | 51:00 | weekday | 0.405 | 0.38959 | 0.38202
53 | Friday | 52:00 | weekday | 0.45346 | 0.43621 | 0.42773
54 | Friday | 53:00 | weekday | 0.48462 | 0.46618 | 0.45712
55 | Friday | 54:00 | weekday | 0.51577 | 0.49615 | 0.4865
56 | Friday | 55:00 | weekday | 0.54692 | 0.52612 | 0.51589
57 | Friday | 56:00 | weekday | 0.57808 | 0.55609 | 0.54528
58 | Friday | 57:00 | weekday | 0.60923 | 0.58606 | 0.57466
59 | Friday | 58:00 | weekday | 0.64038 | 0.61602 | 0.60405
60 | Friday | 59:00 | weekday | 0.67154 | 0.64599 | 0.63343
61 | Friday | 60:00 | weekday | 0.70269 | 0.67596 | 0.66282
62 | Friday | 61:00 | weekday | 0.73385 | 0.70593 | 0.69221
63 | Friday | 62:00 | weekday | 0.765 | 0.7359 | 0.72159
64 | Friday | 63:00 | weekday | 0.7425 | 0.71426 | 0.70037
65 | Friday | 64:00 | weekday | 0.783 | 0.75322 | 0.73857
66 | Friday | 65:00 | weekday | 0.8235 | 0.79217 | 0.77677
67 | Friday | 66:00 | weekday | 0.9 | 0.86576 | 0.84893
68 | Friday | 67:00 | weekday | 0.9 | 0.86576 | 0.84893
69 | Friday | 68:00 | weekday | 0.945 | 0.90905 | 0.89138
70 | Friday | 69:00 | weekday | 0.828 | 0.7965 | 0.78102
71 | Friday | 70:00 | weekday | 0.711 | 0.68395 | 0.67066
72 | Friday | 71:00 | weekday | 0.594 | 0.5714 | 0.56029
73 | Saturday | 72:00 | weekend | 0.3825 | 0.36795 | 0.3608
74 | Saturday | 73:00 | weekend | 0.36 | 0.34631 | 0.33957
75 | Saturday | 74:00 | weekend | 0.3825 | 0.36795 | 0.3608
76 | Saturday | 75:00 | weekend | 0.405 | 0.38959 | 0.38202
77 | Saturday | 76:00 | weekend | 0.45 | 0.43288 | 0.42447
78 | Saturday | 77:00 | weekend | 0.48 | 0.46174 | 0.45276
79 | Saturday | 78:00 | weekend | 0.51 | 0.4906 | 0.48106
80 | Saturday | 79:00 | weekend | 0.54 | 0.51946 | 0.50936
81 | Saturday | 80:00 | weekend | 0.57 | 0.54832 | 0.53766
82 | Saturday | 81:00 | weekend | 0.6 | 0.57718 | 0.56595
83 | Saturday | 82:00 | weekend | 0.63 | 0.60604 | 0.59425
84 | Saturday | 83:00 | weekend | 0.66 | 0.63489 | 0.62255
85 | Saturday | 84:00 | weekend | 0.69 | 0.66375 | 0.65085
86 | Saturday | 85:00 | weekend | 0.72 | 0.69261 | 0.67915
87 | Saturday | 86:00 | weekend | 0.6975 | 0.67097 | 0.65792
88 | Saturday | 87:00 | weekend | 0.75 | 0.72147 | 0.70744
89 | Saturday | 88:00 | weekend | 0.8025 | 0.77197 | 0.75696
90 | Saturday | 89:00 | weekend | 0.855 | 0.82248 | 0.80649
91 | Saturday | 90:00 | weekend | 0.79312 | 0.76296 | 0.74812
92 | Saturday | 91:00 | weekend | 0.73125 | 0.70343 | 0.68976
93 | Saturday | 92:00 | weekend | 0.66938 | 0.64391 | 0.63139
94 | Saturday | 93:00 | weekend | 0.6075 | 0.58439 | 0.57303
95 | Saturday | 94:00 | weekend | 0.54563 | 0.52487 | 0.51466
96 | Saturday | 95:00 | weekend | 0.45 | 0.43288 | 0.42447
97 | Sunday | 96:00 | weekend | 0.3825 | 0.36795 | 0.3608
98 | Sunday | 97:00 | weekend | 0.36 | 0.34631 | 0.33957
99 | Sunday | 98:00 | weekend | 0.3825 | 0.36795 | 0.3608
100 | Sunday | 99:00 | weekend | 0.405 | 0.38959 | 0.38202
101 | Sunday | 100:00 | weekend | 0.44591 | 0.42895 | 0.42061
102 | Sunday | 101:00 | weekend | 0.47455 | 0.45649 | 0.44762
103 | Sunday | 102:00 | weekend | 0.50318 | 0.48404 | 0.47463
104 | Sunday | 103:00 | weekend | 0.53182 | 0.51159 | 0.50164
105 | Sunday | 104:00 | weekend | 0.56045 | 0.53914 | 0.52865
106 | Sunday | 105:00 | weekend | 0.58909 | 0.56668 | 0.55566
107 | Sunday | 106:00 | weekend | 0.61773 | 0.59423 | 0.58268
108 | Sunday | 107:00 | weekend | 0.64636 | 0.62178 | 0.60969
109 | Sunday | 108:00 | weekend | 0.675 | 0.64932 | 0.6367
110 | Sunday | 109:00 | weekend | 0.66214 | 0.63696 | 0.62457
111 | Sunday | 110:00 | weekend | 0.64929 | 0.62459 | 0.61244
112 | Sunday | 111:00 | weekend | 0.63643 | 0.61222 | 0.60032
113 | Sunday | 112:00 | weekend | 0.62357 | 0.59985 | 0.58819
114 | Sunday | 113:00 | weekend | 0.61071 | 0.58748 | 0.57606
115 | Sunday | 114:00 | weekend | 0.59786 | 0.57512 | 0.56393
116 | Sunday | 115:00 | weekend | 0.585 | 0.56275 | 0.55181
117 | Sunday | 116:00 | weekend | 0.63 | 0.60604 | 0.59425
118 | Sunday | 117:00 | weekend | 0.5625 | 0.5411 | 0.53058
119 | Sunday | 118:00 | weekend | 0.495 | 0.47617 | 0.46691
120 | Sunday | 119:00 | weekend | 0.4275 | 0.41124 | 0.40324
121 | Monday | 120:00 | weekday | 0.36 | 0.34631 | 0.33957
122 | Monday | 121:00 | weekday | 0.36 | 0.34631 | 0.33957
123 | Monday | 122:00 | weekday | 0.38571 | 0.37104 | 0.36383
124 | Monday | 123:00 | weekday | 0.41143 | 0.39578 | 0.38808
125 | Monday | 124:00 | weekday | 0.43714 | 0.42051 | 0.41234
126 | Monday | 125:00 | weekday | 0.46286 | 0.44525 | 0.43659
127 | Monday | 126:00 | weekday | 0.48857 | 0.46999 | 0.46085
128 | Monday | 127:00 | weekday | 0.51429 | 0.49472 | 0.4851
129 | Monday | 128:00 | weekday | 0.54 | 0.51946 | 0.50936
130 | Monday | 129:00 | weekday | 0.56571 | 0.54419 | 0.53361
131 | Monday | 130:00 | weekday | 0.59143 | 0.56893 | 0.55787
132 | Monday | 131:00 | weekday | 0.61714 | 0.59367 | 0.58212
133 | Monday | 132:00 | weekday | 0.63 | 0.60604 | 0.59425
134 | Monday | 133:00 | weekday | 0.63 | 0.60604 | 0.59425
135 | Monday | 134:00 | weekday | 0.69429 | 0.66788 | 0.65489
136 | Monday | 135:00 | weekday | 0.72 | 0.69261 | 0.67915
137 | Monday | 136:00 | weekday | 0.684 | 0.65798 | 0.64519
138 | Monday | 137:00 | weekday | 0.648 | 0.62335 | 0.61123
139 | Monday | 138:00 | weekday | 0.63 | 0.60604 | 0.59425
140 | Monday | 139:00 | weekday | 0.576 | 0.55409 | 0.54332
141 | Monday | 140:00 | weekday | 0.54 | 0.51946 | 0.50936
142 | Monday | 141:00 | weekday | 0.504 | 0.48483 | 0.4754
143 | Monday | 142:00 | weekday | 0.405 | 0.38959 | 0.38202
144 | Monday | 143:00 | weekday | 0.3825 | 0.36795 | 0.3608
145 | Tueday | 144:00 | weekday | 0.36 | 0.34631 | 0.33957
146 | Tueday | 145:00 | weekday | 0.36 | 0.34631 | 0.33957
147 | Tueday | 146:00 | weekday | 0.3825 | 0.36795 | 0.3608
148 | Tueday | 147:00 | weekday | 0.405 | 0.38959 | 0.38202
149 | Tueday | 148:00 | weekday | 0.4275 | 0.41124 | 0.40324
150 | Tueday | 149:00 | weekday | 0.45 | 0.43288 | 0.42447
151 | Tueday | 150:00 | weekday | 0.4725 | 0.45453 | 0.44569
152 | Tueday | 151:00 | weekday | 0.495 | 0.47617 | 0.46691
153 | Tueday | 152:00 | weekday | 0.5175 | 0.49781 | 0.48814
154 | Tueday | 153:00 | weekday | 0.54 | 0.51946 | 0.50936
155 | Tueday | 154:00 | weekday | 0.5625 | 0.5411 | 0.53058
156 | Tueday | 155:00 | weekday | 0.585 | 0.56275 | 0.55181
157 | Tueday | 156:00 | weekday | 0.6075 | 0.58439 | 0.57303
158 | Tueday | 157:00 | weekday | 0.63 | 0.60604 | 0.59425
159 | Tueday | 158:00 | weekday | 0.6075 | 0.58439 | 0.57303
160 | Tueday | 159:00 | weekday | 0.63 | 0.60604 | 0.59425
161 | Tueday | 160:00 | weekday | 0.72 | 0.69261 | 0.67915
162 | Tueday | 161:00 | weekday | 0.6975 | 0.67097 | 0.65792
163 | Tueday | 162:00 | weekday | 0.7425 | 0.71426 | 0.70037
164 | Tueday | 163:00 | weekday | 0.693 | 0.66664 | 0.65368
165 | Tueday | 164:00 | weekday | 0.6435 | 0.61902 | 0.60699
166 | Tueday | 165:00 | weekday | 0.594 | 0.5714 | 0.56029
167 | Tueday | 166:00 | weekday | 0.5445 | 0.52379 | 0.5136
168 | Tueday | 167:00 | weekday | 0.495 | 0.47617 | 0.46691
|  |  | Total | 99.4515 | 95.6685 | 93.8084

## Four-Weekly Cooler Duty & Power
Simulink Work Space File |  | DCHrW | DCHrS_A | DCHrS | DC_CpW | DC_CpS_A | DC_CpS
Four Weekly Demand (kWh per 672 hours)
|  | Cooler Duty (kWh) |  |  | Chiller Compressor Power (kWh) |  |  |  | Combined Duty and Compressor Power (kWh)
[8 empty] | Total | 2625520.6582 | 2822551.6866 | 3027274.6764
| Hour | Winter | Spring/Autumn | Summer | Winter | Spring/Autumn | Summer |  | Winter | Spring/Autumn | Summer
1 | 1 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
2 | 2 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
3 | 3 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
4 | 4 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
5 | 5 | 2583 | 2829 | 3075 | 461.25 | 443.7044 | 435.0775 |  | 3044.25 | 3272.7044 | 3510.0775
6 | 6 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
7 | 7 | 2961 | 3243 | 3525 | 528.75 | 508.6367 | 498.7474 |  | 3489.75 | 3751.6367 | 4023.7474
8 | 8 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
9 | 9 | 3339 | 3657 | 3975 | 596.25 | 573.5691 | 562.4172 |  | 3935.25 | 4230.5691 | 4537.4172
10 | 10 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
11 | 11 | 3717 | 4071 | 4425 | 663.75 | 638.5014 | 626.0871 |  | 4380.75 | 4709.5014 | 5051.0871
12 | 12 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
13 | 13 | 4095 | 4485 | 4875 | 731.25 | 703.4338 | 689.757 |  | 4826.25 | 5188.4338 | 5564.757
14 | 14 | 4284 | 4692 | 5100 | 765 | 735.9 | 721.5919 |  | 5049 | 5427.9 | 5821.5919
15 | 15 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
16 | 16 | 4326 | 4738 | 5150 | 772.5 | 743.1147 | 728.6663 |  | 5098.5 | 5481.1147 | 5878.6663
17 | 17 | 4914 | 5382 | 5850 | 877.5 | 844.1205 | 827.7084 |  | 5791.5 | 6226.1205 | 6677.7084
18 | 18 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
19 | 19 | 5040 | 5520 | 6000 | 900 | 865.7647 | 848.9317 |  | 5940 | 6385.7647 | 6848.9317
20 | 20 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
21 | 21 | 5166 | 5658 | 6150 | 922.5 | 887.4088 | 870.155 |  | 6088.5 | 6545.4088 | 7020.155
22 | 22 | 4536 | 4968 | 5400 | 810 | 779.1882 | 764.0385 |  | 5346 | 5747.1882 | 6164.0385
23 | 23 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
24 | 24 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
25 | 25 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
26 | 26 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
27 | 27 | 2167.2 | 2373.6 | 2580 | 387 | 372.2788 | 365.0406 |  | 2554.2 | 2745.8788 | 2945.0406
28 | 28 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
29 | 29 | 2502 | 2740.2857 | 2978.5714 | 446.7857 | 429.7903 | 421.4339 |  | 2948.7857 | 3170.076 | 3400.0054
30 | 30 | 2664 | 2917.7143 | 3171.4286 | 475.7143 | 457.6185 | 448.721 |  | 3139.7143 | 3375.3327 | 3620.1496
31 | 31 | 2826 | 3095.1429 | 3364.2857 | 504.6429 | 485.4466 | 476.0081 |  | 3330.6429 | 3580.5895 | 3840.2938
32 | 32 | 2988 | 3272.5714 | 3557.1429 | 533.5714 | 513.2748 | 503.2952 |  | 3521.5714 | 3785.8462 | 4060.4381
33 | 33 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
34 | 34 | 3312 | 3627.4286 | 3942.8571 | 591.4286 | 568.9311 | 557.8694 |  | 3903.4286 | 4196.3596 | 4500.7265
35 | 35 | 3474 | 3804.8571 | 4135.7143 | 620.3571 | 596.7592 | 585.1565 |  | 4094.3571 | 4401.6164 | 4720.8708
36 | 36 | 3636 | 3982.2857 | 4328.5714 | 649.2857 | 624.5874 | 612.4436 |  | 4285.2857 | 4606.8731 | 4941.015
37 | 37 | 3798 | 4159.7143 | 4521.4286 | 678.2143 | 652.4155 | 639.7306 |  | 4476.2143 | 4812.1298 | 5161.1592
38 | 38 | 3960 | 4337.1429 | 4714.2857 | 707.1429 | 680.2437 | 667.0177 |  | 4667.1429 | 5017.3865 | 5381.3035
39 | 39 | 4122 | 4514.5714 | 4907.1429 | 736.0714 | 708.0718 | 694.3048 |  | 4858.0714 | 5222.6432 | 5601.4477
40 | 40 | 4284 | 4692 | 5100 | 765 | 735.9 | 721.5919 |  | 5049 | 5427.9 | 5821.5919
41 | 41 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
42 | 42 | 4410 | 4830 | 5250 | 787.5 | 757.5441 | 742.8152 |  | 5197.5 | 5587.5441 | 5992.8152
43 | 43 | 4662 | 5106 | 5550 | 832.5 | 800.8323 | 785.2618 |  | 5494.5 | 5906.8323 | 6335.2618
44 | 44 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
45 | 45 | 5166 | 5658 | 6150 | 922.5 | 887.4088 | 870.155 |  | 6088.5 | 6545.4088 | 7020.155
46 | 46 | 4536 | 4968 | 5400 | 810 | 779.1882 | 764.0385 |  | 5346 | 5747.1882 | 6164.0385
47 | 47 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
48 | 48 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
49 | 49 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
50 | 50 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
51 | 51 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
52 | 52 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
53 | 53 | 2539.3846 | 2781.2308 | 3023.0769 | 453.4615 | 436.2122 | 427.731 |  | 2992.8462 | 3217.443 | 3450.8079
54 | 54 | 2713.8462 | 2972.3077 | 3230.7692 | 484.6154 | 466.181 | 457.1171 |  | 3198.4615 | 3438.4887 | 3687.8863
55 | 55 | 2888.3077 | 3163.3846 | 3438.4615 | 515.7692 | 496.1497 | 486.5031 |  | 3404.0769 | 3659.5344 | 3924.9647
56 | 56 | 3062.7692 | 3354.4615 | 3646.1538 | 546.9231 | 526.1185 | 515.8892 |  | 3609.6923 | 3880.5801 | 4162.0431
57 | 57 | 3237.2308 | 3545.5385 | 3853.8462 | 578.0769 | 556.0873 | 545.2753 |  | 3815.3077 | 4101.6258 | 4399.1215
58 | 58 | 3411.6923 | 3736.6154 | 4061.5385 | 609.2308 | 586.0561 | 574.6614 |  | 4020.9231 | 4322.6715 | 4636.1999
59 | 59 | 3586.1538 | 3927.6923 | 4269.2308 | 640.3846 | 616.0249 | 604.0475 |  | 4226.5385 | 4543.7172 | 4873.2783
60 | 60 | 3760.6154 | 4118.7692 | 4476.9231 | 671.5385 | 645.9936 | 633.4336 |  | 4432.1538 | 4764.7629 | 5110.3567
61 | 61 | 3935.0769 | 4309.8462 | 4684.6154 | 702.6923 | 675.9624 | 662.8197 |  | 4637.7692 | 4985.8086 | 5347.4351
62 | 62 | 4109.5385 | 4500.9231 | 4892.3077 | 733.8462 | 705.9312 | 692.2058 |  | 4843.3846 | 5206.8543 | 5584.5135
63 | 63 | 4284 | 4692 | 5100 | 765 | 735.9 | 721.5919 |  | 5049 | 5427.9 | 5821.5919
64 | 64 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
65 | 65 | 4384.8 | 4802.4 | 5220 | 783 | 753.2152 | 738.5705 |  | 5167.8 | 5555.6152 | 5958.5705
66 | 66 | 4611.6 | 5050.8 | 5490 | 823.5 | 792.1747 | 776.7725 |  | 5435.1 | 5842.9747 | 6266.7725
67 | 67 | 5040 | 5520 | 6000 | 900 | 865.7647 | 848.9317 |  | 5940 | 6385.7647 | 6848.9317
68 | 68 | 5040 | 5520 | 6000 | 900 | 865.7647 | 848.9317 |  | 5940 | 6385.7647 | 6848.9317
69 | 69 | 5292 | 5796 | 6300 | 945 | 909.0529 | 891.3782 |  | 6237 | 6705.0529 | 7191.3782
70 | 70 | 4636.8 | 5078.4 | 5520 | 828 | 796.5035 | 781.0171 |  | 5464.8 | 5874.9035 | 6301.0171
71 | 71 | 3981.6 | 4360.8 | 4740 | 711 | 683.9541 | 670.656 |  | 4692.6 | 5044.7541 | 5410.656
72 | 72 | 3326.4 | 3643.2 | 3960 | 594 | 571.4047 | 560.2949 |  | 3920.4 | 4214.6047 | 4520.2949
73 | 73 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
74 | 74 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
75 | 75 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
76 | 76 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
77 | 77 | 2520 | 2760 | 3000 | 450 | 432.8823 | 424.4658 |  | 2970 | 3192.8823 | 3424.4658
78 | 78 | 2688 | 2944 | 3200 | 480 | 461.7411 | 452.7636 |  | 3168 | 3405.7411 | 3652.7636
79 | 79 | 2856 | 3128 | 3400 | 510 | 490.6 | 481.0613 |  | 3366 | 3618.6 | 3881.0613
80 | 80 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
81 | 81 | 3192 | 3496 | 3800 | 570 | 548.3176 | 537.6567 |  | 3762 | 4044.3176 | 4337.6567
82 | 82 | 3360 | 3680 | 4000 | 600 | 577.1764 | 565.9544 |  | 3960 | 4257.1764 | 4565.9544
83 | 83 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
84 | 84 | 3696 | 4048 | 4400 | 660 | 634.8941 | 622.5499 |  | 4356 | 4682.8941 | 5022.5499
85 | 85 | 3864 | 4232 | 4600 | 690 | 663.7529 | 650.8476 |  | 4554 | 4895.7529 | 5250.8476
86 | 86 | 4032 | 4416 | 4800 | 720 | 692.6117 | 679.1453 |  | 4752 | 5108.6117 | 5479.1453
87 | 87 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
88 | 88 | 4200 | 4600 | 5000 | 750 | 721.4705 | 707.4431 |  | 4950 | 5321.4705 | 5707.4431
89 | 89 | 4494 | 4922 | 5350 | 802.5 | 771.9735 | 756.9641 |  | 5296.5 | 5693.9735 | 6106.9641
90 | 90 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
91 | 91 | 4441.5 | 4864.5 | 5287.5 | 793.125 | 762.9551 | 748.121 |  | 5234.625 | 5627.4551 | 6035.621
92 | 92 | 4095 | 4485 | 4875 | 731.25 | 703.4338 | 689.757 |  | 4826.25 | 5188.4338 | 5564.757
93 | 93 | 3748.5 | 4105.5 | 4462.5 | 669.375 | 643.9125 | 631.3929 |  | 4417.875 | 4749.4125 | 5093.8929
94 | 94 | 3402 | 3726 | 4050 | 607.5 | 584.3911 | 573.0289 |  | 4009.5 | 4310.3911 | 4623.0289
95 | 95 | 3055.5 | 3346.5 | 3637.5 | 545.625 | 524.8698 | 514.6648 |  | 3601.125 | 3871.3698 | 4152.1648
96 | 96 | 2520 | 2760 | 3000 | 450 | 432.8823 | 424.4658 |  | 2970 | 3192.8823 | 3424.4658
97 | 97 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
98 | 98 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
99 | 99 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
100 | 100 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
101 | 101 | 2497.0909 | 2734.9091 | 2972.7273 | 445.9091 | 428.947 | 420.6071 |  | 2943 | 3163.8561 | 3393.3343
102 | 102 | 2657.4545 | 2910.5455 | 3163.6364 | 474.5455 | 456.4941 | 447.6185 |  | 3132 | 3367.0395 | 3611.2549
103 | 103 | 2817.8182 | 3086.1818 | 3354.5455 | 503.1818 | 484.0411 | 474.63 |  | 3321 | 3570.223 | 3829.1754
104 | 104 | 2978.1818 | 3261.8182 | 3545.4545 | 531.8182 | 511.5882 | 501.6414 |  | 3510 | 3773.4064 | 4047.096
105 | 105 | 3138.5455 | 3437.4545 | 3736.3636 | 560.4545 | 539.1353 | 528.6529 |  | 3699 | 3976.5898 | 4265.0165
106 | 106 | 3298.9091 | 3613.0909 | 3927.2727 | 589.0909 | 566.6823 | 555.6644 |  | 3888 | 4179.7732 | 4482.9371
107 | 107 | 3459.2727 | 3788.7273 | 4118.1818 | 617.7273 | 594.2294 | 582.6758 |  | 4077 | 4382.9566 | 4700.8576
108 | 108 | 3619.6364 | 3964.3636 | 4309.0909 | 646.3636 | 621.7764 | 609.6873 |  | 4266 | 4586.1401 | 4918.7782
109 | 109 | 3780 | 4140 | 4500 | 675 | 649.3235 | 636.6987 |  | 4455 | 4789.3235 | 5136.6987
110 | 110 | 3708 | 4061.1429 | 4414.2857 | 662.1429 | 636.9554 | 624.5712 |  | 4370.1429 | 4698.0983 | 5038.8569
111 | 111 | 3636 | 3982.2857 | 4328.5714 | 649.2857 | 624.5874 | 612.4436 |  | 4285.2857 | 4606.8731 | 4941.015
112 | 112 | 3564 | 3903.4286 | 4242.8571 | 636.4286 | 612.2193 | 600.316 |  | 4200.4286 | 4515.6479 | 4843.1731
113 | 113 | 3492 | 3824.5714 | 4157.1429 | 623.5714 | 599.8512 | 588.1884 |  | 4115.5714 | 4424.4227 | 4745.3312
114 | 114 | 3420 | 3745.7143 | 4071.4286 | 610.7143 | 587.4832 | 576.0608 |  | 4030.7143 | 4333.1974 | 4647.4893
115 | 115 | 3348 | 3666.8571 | 3985.7143 | 597.8571 | 575.1151 | 563.9332 |  | 3945.8571 | 4241.9722 | 4549.6475
116 | 116 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
117 | 117 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
118 | 118 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
119 | 119 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
120 | 120 | 2394 | 2622 | 2850 | 427.5 | 411.2382 | 403.2425 |  | 2821.5 | 3033.2382 | 3253.2425
121 | 121 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
122 | 122 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
123 | 123 | 2160 | 2365.7143 | 2571.4286 | 385.7143 | 371.042 | 363.8279 |  | 2545.7143 | 2736.7563 | 2935.2564
124 | 124 | 2304 | 2523.4286 | 2742.8571 | 411.4286 | 395.7781 | 388.083 |  | 2715.4286 | 2919.2067 | 3130.9402
125 | 125 | 2448 | 2681.1429 | 2914.2857 | 437.1429 | 420.5143 | 412.3382 |  | 2885.1429 | 3101.6571 | 3326.624
126 | 126 | 2592 | 2838.8571 | 3085.7143 | 462.8571 | 445.2504 | 436.5934 |  | 3054.8571 | 3284.1075 | 3522.3077
127 | 127 | 2736 | 2996.5714 | 3257.1429 | 488.5714 | 469.9865 | 460.8486 |  | 3224.5714 | 3466.558 | 3717.9915
128 | 128 | 2880 | 3154.2857 | 3428.5714 | 514.2857 | 494.7227 | 485.1038 |  | 3394.2857 | 3649.0084 | 3913.6752
129 | 129 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
130 | 130 | 3168 | 3469.7143 | 3771.4286 | 565.7143 | 544.1949 | 533.6142 |  | 3733.7143 | 4013.9092 | 4305.0428
131 | 131 | 3312 | 3627.4286 | 3942.8571 | 591.4286 | 568.9311 | 557.8694 |  | 3903.4286 | 4196.3596 | 4500.7265
132 | 132 | 3456 | 3785.1429 | 4114.2857 | 617.1429 | 593.6672 | 582.1246 |  | 4073.1429 | 4378.81 | 4696.4103
133 | 133 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
134 | 134 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
135 | 135 | 3888 | 4258.2857 | 4628.5714 | 694.2857 | 667.8756 | 654.8901 |  | 4582.2857 | 4926.1613 | 5283.4616
136 | 136 | 4032 | 4416 | 4800 | 720 | 692.6117 | 679.1453 |  | 4752 | 5108.6117 | 5479.1453
137 | 137 | 3830.4 | 4195.2 | 4560 | 684 | 657.9811 | 645.1881 |  | 4514.4 | 4853.1811 | 5205.1881
138 | 138 | 3628.8 | 3974.4 | 4320 | 648 | 623.3506 | 611.2308 |  | 4276.8 | 4597.7506 | 4931.2308
139 | 139 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
140 | 140 | 3225.6 | 3532.8 | 3840 | 576 | 554.0894 | 543.3163 |  | 3801.6 | 4086.8894 | 4383.3163
141 | 141 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
142 | 142 | 2822.4 | 3091.2 | 3360 | 504 | 484.8282 | 475.4017 |  | 3326.4 | 3576.0282 | 3835.4017
143 | 143 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
144 | 144 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
145 | 145 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
146 | 146 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
147 | 147 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
148 | 148 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
149 | 149 | 2394 | 2622 | 2850 | 427.5 | 411.2382 | 403.2425 |  | 2821.5 | 3033.2382 | 3253.2425
150 | 150 | 2520 | 2760 | 3000 | 450 | 432.8823 | 424.4658 |  | 2970 | 3192.8823 | 3424.4658
151 | 151 | 2646 | 2898 | 3150 | 472.5 | 454.5264 | 445.6891 |  | 3118.5 | 3352.5264 | 3595.6891
152 | 152 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
153 | 153 | 2898 | 3174 | 3450 | 517.5 | 497.8147 | 488.1357 |  | 3415.5 | 3671.8147 | 3938.1357
154 | 154 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
155 | 155 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
156 | 156 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
157 | 157 | 3402 | 3726 | 4050 | 607.5 | 584.3911 | 573.0289 |  | 4009.5 | 4310.3911 | 4623.0289
158 | 158 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
159 | 159 | 3402 | 3726 | 4050 | 607.5 | 584.3911 | 573.0289 |  | 4009.5 | 4310.3911 | 4623.0289
160 | 160 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
161 | 161 | 4032 | 4416 | 4800 | 720 | 692.6117 | 679.1453 |  | 4752 | 5108.6117 | 5479.1453
162 | 162 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
163 | 163 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
164 | 164 | 3880.8 | 4250.4 | 4620 | 693 | 666.6388 | 653.6774 |  | 4573.8 | 4917.0388 | 5273.6774
165 | 165 | 3603.6 | 3946.8 | 4290 | 643.5 | 619.0217 | 606.9861 |  | 4247.1 | 4565.8217 | 4896.9861
166 | 166 | 3326.4 | 3643.2 | 3960 | 594 | 571.4047 | 560.2949 |  | 3920.4 | 4214.6047 | 4520.2949
167 | 167 | 3049.2 | 3339.6 | 3630 | 544.5 | 523.7876 | 513.6037 |  | 3593.7 | 3863.3876 | 4143.6037
168 | 168 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
1 | 169 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
2 | 170 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
3 | 171 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
4 | 172 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
5 | 173 | 2583 | 2829 | 3075 | 461.25 | 443.7044 | 435.0775 |  | 3044.25 | 3272.7044 | 3510.0775
6 | 174 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
7 | 175 | 2961 | 3243 | 3525 | 528.75 | 508.6367 | 498.7474 |  | 3489.75 | 3751.6367 | 4023.7474
8 | 176 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
9 | 177 | 3339 | 3657 | 3975 | 596.25 | 573.5691 | 562.4172 |  | 3935.25 | 4230.5691 | 4537.4172
10 | 178 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
11 | 179 | 3717 | 4071 | 4425 | 663.75 | 638.5014 | 626.0871 |  | 4380.75 | 4709.5014 | 5051.0871
12 | 180 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
13 | 181 | 4095 | 4485 | 4875 | 731.25 | 703.4338 | 689.757 |  | 4826.25 | 5188.4338 | 5564.757
14 | 182 | 4284 | 4692 | 5100 | 765 | 735.9 | 721.5919 |  | 5049 | 5427.9 | 5821.5919
15 | 183 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
16 | 184 | 4326 | 4738 | 5150 | 772.5 | 743.1147 | 728.6663 |  | 5098.5 | 5481.1147 | 5878.6663
17 | 185 | 4914 | 5382 | 5850 | 877.5 | 844.1205 | 827.7084 |  | 5791.5 | 6226.1205 | 6677.7084
18 | 186 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
19 | 187 | 5040 | 5520 | 6000 | 900 | 865.7647 | 848.9317 |  | 5940 | 6385.7647 | 6848.9317
20 | 188 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
21 | 189 | 5166 | 5658 | 6150 | 922.5 | 887.4088 | 870.155 |  | 6088.5 | 6545.4088 | 7020.155
22 | 190 | 4536 | 4968 | 5400 | 810 | 779.1882 | 764.0385 |  | 5346 | 5747.1882 | 6164.0385
23 | 191 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
24 | 192 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
25 | 193 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
26 | 194 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
27 | 195 | 2167.2 | 2373.6 | 2580 | 387 | 372.2788 | 365.0406 |  | 2554.2 | 2745.8788 | 2945.0406
28 | 196 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
29 | 197 | 2502 | 2740.2857 | 2978.5714 | 446.7857 | 429.7903 | 421.4339 |  | 2948.7857 | 3170.076 | 3400.0054
30 | 198 | 2664 | 2917.7143 | 3171.4286 | 475.7143 | 457.6185 | 448.721 |  | 3139.7143 | 3375.3327 | 3620.1496
31 | 199 | 2826 | 3095.1429 | 3364.2857 | 504.6429 | 485.4466 | 476.0081 |  | 3330.6429 | 3580.5895 | 3840.2938
32 | 200 | 2988 | 3272.5714 | 3557.1429 | 533.5714 | 513.2748 | 503.2952 |  | 3521.5714 | 3785.8462 | 4060.4381
33 | 201 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
34 | 202 | 3312 | 3627.4286 | 3942.8571 | 591.4286 | 568.9311 | 557.8694 |  | 3903.4286 | 4196.3596 | 4500.7265
35 | 203 | 3474 | 3804.8571 | 4135.7143 | 620.3571 | 596.7592 | 585.1565 |  | 4094.3571 | 4401.6164 | 4720.8708
36 | 204 | 3636 | 3982.2857 | 4328.5714 | 649.2857 | 624.5874 | 612.4436 |  | 4285.2857 | 4606.8731 | 4941.015
37 | 205 | 3798 | 4159.7143 | 4521.4286 | 678.2143 | 652.4155 | 639.7306 |  | 4476.2143 | 4812.1298 | 5161.1592
38 | 206 | 3960 | 4337.1429 | 4714.2857 | 707.1429 | 680.2437 | 667.0177 |  | 4667.1429 | 5017.3865 | 5381.3035
39 | 207 | 4122 | 4514.5714 | 4907.1429 | 736.0714 | 708.0718 | 694.3048 |  | 4858.0714 | 5222.6432 | 5601.4477
40 | 208 | 4284 | 4692 | 5100 | 765 | 735.9 | 721.5919 |  | 5049 | 5427.9 | 5821.5919
41 | 209 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
42 | 210 | 4410 | 4830 | 5250 | 787.5 | 757.5441 | 742.8152 |  | 5197.5 | 5587.5441 | 5992.8152
43 | 211 | 4662 | 5106 | 5550 | 832.5 | 800.8323 | 785.2618 |  | 5494.5 | 5906.8323 | 6335.2618
44 | 212 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
45 | 213 | 5166 | 5658 | 6150 | 922.5 | 887.4088 | 870.155 |  | 6088.5 | 6545.4088 | 7020.155
46 | 214 | 4536 | 4968 | 5400 | 810 | 779.1882 | 764.0385 |  | 5346 | 5747.1882 | 6164.0385
47 | 215 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
48 | 216 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
49 | 217 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
50 | 218 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
51 | 219 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
52 | 220 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
53 | 221 | 2539.3846 | 2781.2308 | 3023.0769 | 453.4615 | 436.2122 | 427.731 |  | 2992.8462 | 3217.443 | 3450.8079
54 | 222 | 2713.8462 | 2972.3077 | 3230.7692 | 484.6154 | 466.181 | 457.1171 |  | 3198.4615 | 3438.4887 | 3687.8863
55 | 223 | 2888.3077 | 3163.3846 | 3438.4615 | 515.7692 | 496.1497 | 486.5031 |  | 3404.0769 | 3659.5344 | 3924.9647
56 | 224 | 3062.7692 | 3354.4615 | 3646.1538 | 546.9231 | 526.1185 | 515.8892 |  | 3609.6923 | 3880.5801 | 4162.0431
57 | 225 | 3237.2308 | 3545.5385 | 3853.8462 | 578.0769 | 556.0873 | 545.2753 |  | 3815.3077 | 4101.6258 | 4399.1215
58 | 226 | 3411.6923 | 3736.6154 | 4061.5385 | 609.2308 | 586.0561 | 574.6614 |  | 4020.9231 | 4322.6715 | 4636.1999
59 | 227 | 3586.1538 | 3927.6923 | 4269.2308 | 640.3846 | 616.0249 | 604.0475 |  | 4226.5385 | 4543.7172 | 4873.2783
60 | 228 | 3760.6154 | 4118.7692 | 4476.9231 | 671.5385 | 645.9936 | 633.4336 |  | 4432.1538 | 4764.7629 | 5110.3567
61 | 229 | 3935.0769 | 4309.8462 | 4684.6154 | 702.6923 | 675.9624 | 662.8197 |  | 4637.7692 | 4985.8086 | 5347.4351
62 | 230 | 4109.5385 | 4500.9231 | 4892.3077 | 733.8462 | 705.9312 | 692.2058 |  | 4843.3846 | 5206.8543 | 5584.5135
63 | 231 | 4284 | 4692 | 5100 | 765 | 735.9 | 721.5919 |  | 5049 | 5427.9 | 5821.5919
64 | 232 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
65 | 233 | 4384.8 | 4802.4 | 5220 | 783 | 753.2152 | 738.5705 |  | 5167.8 | 5555.6152 | 5958.5705
66 | 234 | 4611.6 | 5050.8 | 5490 | 823.5 | 792.1747 | 776.7725 |  | 5435.1 | 5842.9747 | 6266.7725
67 | 235 | 5040 | 5520 | 6000 | 900 | 865.7647 | 848.9317 |  | 5940 | 6385.7647 | 6848.9317
68 | 236 | 5040 | 5520 | 6000 | 900 | 865.7647 | 848.9317 |  | 5940 | 6385.7647 | 6848.9317
69 | 237 | 5292 | 5796 | 6300 | 945 | 909.0529 | 891.3782 |  | 6237 | 6705.0529 | 7191.3782
70 | 238 | 4636.8 | 5078.4 | 5520 | 828 | 796.5035 | 781.0171 |  | 5464.8 | 5874.9035 | 6301.0171
71 | 239 | 3981.6 | 4360.8 | 4740 | 711 | 683.9541 | 670.656 |  | 4692.6 | 5044.7541 | 5410.656
72 | 240 | 3326.4 | 3643.2 | 3960 | 594 | 571.4047 | 560.2949 |  | 3920.4 | 4214.6047 | 4520.2949
73 | 241 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
74 | 242 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
75 | 243 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
76 | 244 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
77 | 245 | 2520 | 2760 | 3000 | 450 | 432.8823 | 424.4658 |  | 2970 | 3192.8823 | 3424.4658
78 | 246 | 2688 | 2944 | 3200 | 480 | 461.7411 | 452.7636 |  | 3168 | 3405.7411 | 3652.7636
79 | 247 | 2856 | 3128 | 3400 | 510 | 490.6 | 481.0613 |  | 3366 | 3618.6 | 3881.0613
80 | 248 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
81 | 249 | 3192 | 3496 | 3800 | 570 | 548.3176 | 537.6567 |  | 3762 | 4044.3176 | 4337.6567
82 | 250 | 3360 | 3680 | 4000 | 600 | 577.1764 | 565.9544 |  | 3960 | 4257.1764 | 4565.9544
83 | 251 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
84 | 252 | 3696 | 4048 | 4400 | 660 | 634.8941 | 622.5499 |  | 4356 | 4682.8941 | 5022.5499
85 | 253 | 3864 | 4232 | 4600 | 690 | 663.7529 | 650.8476 |  | 4554 | 4895.7529 | 5250.8476
86 | 254 | 4032 | 4416 | 4800 | 720 | 692.6117 | 679.1453 |  | 4752 | 5108.6117 | 5479.1453
87 | 255 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
88 | 256 | 4200 | 4600 | 5000 | 750 | 721.4705 | 707.4431 |  | 4950 | 5321.4705 | 5707.4431
89 | 257 | 4494 | 4922 | 5350 | 802.5 | 771.9735 | 756.9641 |  | 5296.5 | 5693.9735 | 6106.9641
90 | 258 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
91 | 259 | 4441.5 | 4864.5 | 5287.5 | 793.125 | 762.9551 | 748.121 |  | 5234.625 | 5627.4551 | 6035.621
92 | 260 | 4095 | 4485 | 4875 | 731.25 | 703.4338 | 689.757 |  | 4826.25 | 5188.4338 | 5564.757
93 | 261 | 3748.5 | 4105.5 | 4462.5 | 669.375 | 643.9125 | 631.3929 |  | 4417.875 | 4749.4125 | 5093.8929
94 | 262 | 3402 | 3726 | 4050 | 607.5 | 584.3911 | 573.0289 |  | 4009.5 | 4310.3911 | 4623.0289
95 | 263 | 3055.5 | 3346.5 | 3637.5 | 545.625 | 524.8698 | 514.6648 |  | 3601.125 | 3871.3698 | 4152.1648
96 | 264 | 2520 | 2760 | 3000 | 450 | 432.8823 | 424.4658 |  | 2970 | 3192.8823 | 3424.4658
97 | 265 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
98 | 266 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
99 | 267 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
100 | 268 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
101 | 269 | 2497.0909 | 2734.9091 | 2972.7273 | 445.9091 | 428.947 | 420.6071 |  | 2943 | 3163.8561 | 3393.3343
102 | 270 | 2657.4545 | 2910.5455 | 3163.6364 | 474.5455 | 456.4941 | 447.6185 |  | 3132 | 3367.0395 | 3611.2549
103 | 271 | 2817.8182 | 3086.1818 | 3354.5455 | 503.1818 | 484.0411 | 474.63 |  | 3321 | 3570.223 | 3829.1754
104 | 272 | 2978.1818 | 3261.8182 | 3545.4545 | 531.8182 | 511.5882 | 501.6414 |  | 3510 | 3773.4064 | 4047.096
105 | 273 | 3138.5455 | 3437.4545 | 3736.3636 | 560.4545 | 539.1353 | 528.6529 |  | 3699 | 3976.5898 | 4265.0165
106 | 274 | 3298.9091 | 3613.0909 | 3927.2727 | 589.0909 | 566.6823 | 555.6644 |  | 3888 | 4179.7732 | 4482.9371
107 | 275 | 3459.2727 | 3788.7273 | 4118.1818 | 617.7273 | 594.2294 | 582.6758 |  | 4077 | 4382.9566 | 4700.8576
108 | 276 | 3619.6364 | 3964.3636 | 4309.0909 | 646.3636 | 621.7764 | 609.6873 |  | 4266 | 4586.1401 | 4918.7782
109 | 277 | 3780 | 4140 | 4500 | 675 | 649.3235 | 636.6987 |  | 4455 | 4789.3235 | 5136.6987
110 | 278 | 3708 | 4061.1429 | 4414.2857 | 662.1429 | 636.9554 | 624.5712 |  | 4370.1429 | 4698.0983 | 5038.8569
111 | 279 | 3636 | 3982.2857 | 4328.5714 | 649.2857 | 624.5874 | 612.4436 |  | 4285.2857 | 4606.8731 | 4941.015
112 | 280 | 3564 | 3903.4286 | 4242.8571 | 636.4286 | 612.2193 | 600.316 |  | 4200.4286 | 4515.6479 | 4843.1731
113 | 281 | 3492 | 3824.5714 | 4157.1429 | 623.5714 | 599.8512 | 588.1884 |  | 4115.5714 | 4424.4227 | 4745.3312
114 | 282 | 3420 | 3745.7143 | 4071.4286 | 610.7143 | 587.4832 | 576.0608 |  | 4030.7143 | 4333.1974 | 4647.4893
115 | 283 | 3348 | 3666.8571 | 3985.7143 | 597.8571 | 575.1151 | 563.9332 |  | 3945.8571 | 4241.9722 | 4549.6475
116 | 284 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
117 | 285 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
118 | 286 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
119 | 287 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
120 | 288 | 2394 | 2622 | 2850 | 427.5 | 411.2382 | 403.2425 |  | 2821.5 | 3033.2382 | 3253.2425
121 | 289 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
122 | 290 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
123 | 291 | 2160 | 2365.7143 | 2571.4286 | 385.7143 | 371.042 | 363.8279 |  | 2545.7143 | 2736.7563 | 2935.2564
124 | 292 | 2304 | 2523.4286 | 2742.8571 | 411.4286 | 395.7781 | 388.083 |  | 2715.4286 | 2919.2067 | 3130.9402
125 | 293 | 2448 | 2681.1429 | 2914.2857 | 437.1429 | 420.5143 | 412.3382 |  | 2885.1429 | 3101.6571 | 3326.624
126 | 294 | 2592 | 2838.8571 | 3085.7143 | 462.8571 | 445.2504 | 436.5934 |  | 3054.8571 | 3284.1075 | 3522.3077
127 | 295 | 2736 | 2996.5714 | 3257.1429 | 488.5714 | 469.9865 | 460.8486 |  | 3224.5714 | 3466.558 | 3717.9915
128 | 296 | 2880 | 3154.2857 | 3428.5714 | 514.2857 | 494.7227 | 485.1038 |  | 3394.2857 | 3649.0084 | 3913.6752
129 | 297 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
130 | 298 | 3168 | 3469.7143 | 3771.4286 | 565.7143 | 544.1949 | 533.6142 |  | 3733.7143 | 4013.9092 | 4305.0428
131 | 299 | 3312 | 3627.4286 | 3942.8571 | 591.4286 | 568.9311 | 557.8694 |  | 3903.4286 | 4196.3596 | 4500.7265
132 | 300 | 3456 | 3785.1429 | 4114.2857 | 617.1429 | 593.6672 | 582.1246 |  | 4073.1429 | 4378.81 | 4696.4103
133 | 301 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
134 | 302 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
135 | 303 | 3888 | 4258.2857 | 4628.5714 | 694.2857 | 667.8756 | 654.8901 |  | 4582.2857 | 4926.1613 | 5283.4616
136 | 304 | 4032 | 4416 | 4800 | 720 | 692.6117 | 679.1453 |  | 4752 | 5108.6117 | 5479.1453
137 | 305 | 3830.4 | 4195.2 | 4560 | 684 | 657.9811 | 645.1881 |  | 4514.4 | 4853.1811 | 5205.1881
138 | 306 | 3628.8 | 3974.4 | 4320 | 648 | 623.3506 | 611.2308 |  | 4276.8 | 4597.7506 | 4931.2308
139 | 307 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
140 | 308 | 3225.6 | 3532.8 | 3840 | 576 | 554.0894 | 543.3163 |  | 3801.6 | 4086.8894 | 4383.3163
141 | 309 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
142 | 310 | 2822.4 | 3091.2 | 3360 | 504 | 484.8282 | 475.4017 |  | 3326.4 | 3576.0282 | 3835.4017
143 | 311 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
144 | 312 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
145 | 313 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
146 | 314 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
147 | 315 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
148 | 316 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
149 | 317 | 2394 | 2622 | 2850 | 427.5 | 411.2382 | 403.2425 |  | 2821.5 | 3033.2382 | 3253.2425
150 | 318 | 2520 | 2760 | 3000 | 450 | 432.8823 | 424.4658 |  | 2970 | 3192.8823 | 3424.4658
151 | 319 | 2646 | 2898 | 3150 | 472.5 | 454.5264 | 445.6891 |  | 3118.5 | 3352.5264 | 3595.6891
152 | 320 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
153 | 321 | 2898 | 3174 | 3450 | 517.5 | 497.8147 | 488.1357 |  | 3415.5 | 3671.8147 | 3938.1357
154 | 322 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
155 | 323 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
156 | 324 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
157 | 325 | 3402 | 3726 | 4050 | 607.5 | 584.3911 | 573.0289 |  | 4009.5 | 4310.3911 | 4623.0289
158 | 326 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
159 | 327 | 3402 | 3726 | 4050 | 607.5 | 584.3911 | 573.0289 |  | 4009.5 | 4310.3911 | 4623.0289
160 | 328 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
161 | 329 | 4032 | 4416 | 4800 | 720 | 692.6117 | 679.1453 |  | 4752 | 5108.6117 | 5479.1453
162 | 330 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
163 | 331 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
164 | 332 | 3880.8 | 4250.4 | 4620 | 693 | 666.6388 | 653.6774 |  | 4573.8 | 4917.0388 | 5273.6774
165 | 333 | 3603.6 | 3946.8 | 4290 | 643.5 | 619.0217 | 606.9861 |  | 4247.1 | 4565.8217 | 4896.9861
166 | 334 | 3326.4 | 3643.2 | 3960 | 594 | 571.4047 | 560.2949 |  | 3920.4 | 4214.6047 | 4520.2949
167 | 335 | 3049.2 | 3339.6 | 3630 | 544.5 | 523.7876 | 513.6037 |  | 3593.7 | 3863.3876 | 4143.6037
168 | 336 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
1 | 337 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
2 | 338 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
3 | 339 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
4 | 340 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
5 | 341 | 2583 | 2829 | 3075 | 461.25 | 443.7044 | 435.0775 |  | 3044.25 | 3272.7044 | 3510.0775
6 | 342 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
7 | 343 | 2961 | 3243 | 3525 | 528.75 | 508.6367 | 498.7474 |  | 3489.75 | 3751.6367 | 4023.7474
8 | 344 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
9 | 345 | 3339 | 3657 | 3975 | 596.25 | 573.5691 | 562.4172 |  | 3935.25 | 4230.5691 | 4537.4172
10 | 346 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
11 | 347 | 3717 | 4071 | 4425 | 663.75 | 638.5014 | 626.0871 |  | 4380.75 | 4709.5014 | 5051.0871
12 | 348 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
13 | 349 | 4095 | 4485 | 4875 | 731.25 | 703.4338 | 689.757 |  | 4826.25 | 5188.4338 | 5564.757
14 | 350 | 4284 | 4692 | 5100 | 765 | 735.9 | 721.5919 |  | 5049 | 5427.9 | 5821.5919
15 | 351 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
16 | 352 | 4326 | 4738 | 5150 | 772.5 | 743.1147 | 728.6663 |  | 5098.5 | 5481.1147 | 5878.6663
17 | 353 | 4914 | 5382 | 5850 | 877.5 | 844.1205 | 827.7084 |  | 5791.5 | 6226.1205 | 6677.7084
18 | 354 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
19 | 355 | 5040 | 5520 | 6000 | 900 | 865.7647 | 848.9317 |  | 5940 | 6385.7647 | 6848.9317
20 | 356 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
21 | 357 | 5166 | 5658 | 6150 | 922.5 | 887.4088 | 870.155 |  | 6088.5 | 6545.4088 | 7020.155
22 | 358 | 4536 | 4968 | 5400 | 810 | 779.1882 | 764.0385 |  | 5346 | 5747.1882 | 6164.0385
23 | 359 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
24 | 360 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
25 | 361 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
26 | 362 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
27 | 363 | 2167.2 | 2373.6 | 2580 | 387 | 372.2788 | 365.0406 |  | 2554.2 | 2745.8788 | 2945.0406
28 | 364 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
29 | 365 | 2502 | 2740.2857 | 2978.5714 | 446.7857 | 429.7903 | 421.4339 |  | 2948.7857 | 3170.076 | 3400.0054
30 | 366 | 2664 | 2917.7143 | 3171.4286 | 475.7143 | 457.6185 | 448.721 |  | 3139.7143 | 3375.3327 | 3620.1496
31 | 367 | 2826 | 3095.1429 | 3364.2857 | 504.6429 | 485.4466 | 476.0081 |  | 3330.6429 | 3580.5895 | 3840.2938
32 | 368 | 2988 | 3272.5714 | 3557.1429 | 533.5714 | 513.2748 | 503.2952 |  | 3521.5714 | 3785.8462 | 4060.4381
33 | 369 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
34 | 370 | 3312 | 3627.4286 | 3942.8571 | 591.4286 | 568.9311 | 557.8694 |  | 3903.4286 | 4196.3596 | 4500.7265
35 | 371 | 3474 | 3804.8571 | 4135.7143 | 620.3571 | 596.7592 | 585.1565 |  | 4094.3571 | 4401.6164 | 4720.8708
36 | 372 | 3636 | 3982.2857 | 4328.5714 | 649.2857 | 624.5874 | 612.4436 |  | 4285.2857 | 4606.8731 | 4941.015
37 | 373 | 3798 | 4159.7143 | 4521.4286 | 678.2143 | 652.4155 | 639.7306 |  | 4476.2143 | 4812.1298 | 5161.1592
38 | 374 | 3960 | 4337.1429 | 4714.2857 | 707.1429 | 680.2437 | 667.0177 |  | 4667.1429 | 5017.3865 | 5381.3035
39 | 375 | 4122 | 4514.5714 | 4907.1429 | 736.0714 | 708.0718 | 694.3048 |  | 4858.0714 | 5222.6432 | 5601.4477
40 | 376 | 4284 | 4692 | 5100 | 765 | 735.9 | 721.5919 |  | 5049 | 5427.9 | 5821.5919
41 | 377 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
42 | 378 | 4410 | 4830 | 5250 | 787.5 | 757.5441 | 742.8152 |  | 5197.5 | 5587.5441 | 5992.8152
43 | 379 | 4662 | 5106 | 5550 | 832.5 | 800.8323 | 785.2618 |  | 5494.5 | 5906.8323 | 6335.2618
44 | 380 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
45 | 381 | 5166 | 5658 | 6150 | 922.5 | 887.4088 | 870.155 |  | 6088.5 | 6545.4088 | 7020.155
46 | 382 | 4536 | 4968 | 5400 | 810 | 779.1882 | 764.0385 |  | 5346 | 5747.1882 | 6164.0385
47 | 383 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
48 | 384 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
49 | 385 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
50 | 386 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
51 | 387 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
52 | 388 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
53 | 389 | 2539.3846 | 2781.2308 | 3023.0769 | 453.4615 | 436.2122 | 427.731 |  | 2992.8462 | 3217.443 | 3450.8079
54 | 390 | 2713.8462 | 2972.3077 | 3230.7692 | 484.6154 | 466.181 | 457.1171 |  | 3198.4615 | 3438.4887 | 3687.8863
55 | 391 | 2888.3077 | 3163.3846 | 3438.4615 | 515.7692 | 496.1497 | 486.5031 |  | 3404.0769 | 3659.5344 | 3924.9647
56 | 392 | 3062.7692 | 3354.4615 | 3646.1538 | 546.9231 | 526.1185 | 515.8892 |  | 3609.6923 | 3880.5801 | 4162.0431
57 | 393 | 3237.2308 | 3545.5385 | 3853.8462 | 578.0769 | 556.0873 | 545.2753 |  | 3815.3077 | 4101.6258 | 4399.1215
58 | 394 | 3411.6923 | 3736.6154 | 4061.5385 | 609.2308 | 586.0561 | 574.6614 |  | 4020.9231 | 4322.6715 | 4636.1999
59 | 395 | 3586.1538 | 3927.6923 | 4269.2308 | 640.3846 | 616.0249 | 604.0475 |  | 4226.5385 | 4543.7172 | 4873.2783
60 | 396 | 3760.6154 | 4118.7692 | 4476.9231 | 671.5385 | 645.9936 | 633.4336 |  | 4432.1538 | 4764.7629 | 5110.3567
61 | 397 | 3935.0769 | 4309.8462 | 4684.6154 | 702.6923 | 675.9624 | 662.8197 |  | 4637.7692 | 4985.8086 | 5347.4351
62 | 398 | 4109.5385 | 4500.9231 | 4892.3077 | 733.8462 | 705.9312 | 692.2058 |  | 4843.3846 | 5206.8543 | 5584.5135
63 | 399 | 4284 | 4692 | 5100 | 765 | 735.9 | 721.5919 |  | 5049 | 5427.9 | 5821.5919
64 | 400 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
65 | 401 | 4384.8 | 4802.4 | 5220 | 783 | 753.2152 | 738.5705 |  | 5167.8 | 5555.6152 | 5958.5705
66 | 402 | 4611.6 | 5050.8 | 5490 | 823.5 | 792.1747 | 776.7725 |  | 5435.1 | 5842.9747 | 6266.7725
67 | 403 | 5040 | 5520 | 6000 | 900 | 865.7647 | 848.9317 |  | 5940 | 6385.7647 | 6848.9317
68 | 404 | 5040 | 5520 | 6000 | 900 | 865.7647 | 848.9317 |  | 5940 | 6385.7647 | 6848.9317
69 | 405 | 5292 | 5796 | 6300 | 945 | 909.0529 | 891.3782 |  | 6237 | 6705.0529 | 7191.3782
70 | 406 | 4636.8 | 5078.4 | 5520 | 828 | 796.5035 | 781.0171 |  | 5464.8 | 5874.9035 | 6301.0171
71 | 407 | 3981.6 | 4360.8 | 4740 | 711 | 683.9541 | 670.656 |  | 4692.6 | 5044.7541 | 5410.656
72 | 408 | 3326.4 | 3643.2 | 3960 | 594 | 571.4047 | 560.2949 |  | 3920.4 | 4214.6047 | 4520.2949
73 | 409 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
74 | 410 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
75 | 411 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
76 | 412 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
77 | 413 | 2520 | 2760 | 3000 | 450 | 432.8823 | 424.4658 |  | 2970 | 3192.8823 | 3424.4658
78 | 414 | 2688 | 2944 | 3200 | 480 | 461.7411 | 452.7636 |  | 3168 | 3405.7411 | 3652.7636
79 | 415 | 2856 | 3128 | 3400 | 510 | 490.6 | 481.0613 |  | 3366 | 3618.6 | 3881.0613
80 | 416 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
81 | 417 | 3192 | 3496 | 3800 | 570 | 548.3176 | 537.6567 |  | 3762 | 4044.3176 | 4337.6567
82 | 418 | 3360 | 3680 | 4000 | 600 | 577.1764 | 565.9544 |  | 3960 | 4257.1764 | 4565.9544
83 | 419 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
84 | 420 | 3696 | 4048 | 4400 | 660 | 634.8941 | 622.5499 |  | 4356 | 4682.8941 | 5022.5499
85 | 421 | 3864 | 4232 | 4600 | 690 | 663.7529 | 650.8476 |  | 4554 | 4895.7529 | 5250.8476
86 | 422 | 4032 | 4416 | 4800 | 720 | 692.6117 | 679.1453 |  | 4752 | 5108.6117 | 5479.1453
87 | 423 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
88 | 424 | 4200 | 4600 | 5000 | 750 | 721.4705 | 707.4431 |  | 4950 | 5321.4705 | 5707.4431
89 | 425 | 4494 | 4922 | 5350 | 802.5 | 771.9735 | 756.9641 |  | 5296.5 | 5693.9735 | 6106.9641
90 | 426 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
91 | 427 | 4441.5 | 4864.5 | 5287.5 | 793.125 | 762.9551 | 748.121 |  | 5234.625 | 5627.4551 | 6035.621
92 | 428 | 4095 | 4485 | 4875 | 731.25 | 703.4338 | 689.757 |  | 4826.25 | 5188.4338 | 5564.757
93 | 429 | 3748.5 | 4105.5 | 4462.5 | 669.375 | 643.9125 | 631.3929 |  | 4417.875 | 4749.4125 | 5093.8929
94 | 430 | 3402 | 3726 | 4050 | 607.5 | 584.3911 | 573.0289 |  | 4009.5 | 4310.3911 | 4623.0289
95 | 431 | 3055.5 | 3346.5 | 3637.5 | 545.625 | 524.8698 | 514.6648 |  | 3601.125 | 3871.3698 | 4152.1648
96 | 432 | 2520 | 2760 | 3000 | 450 | 432.8823 | 424.4658 |  | 2970 | 3192.8823 | 3424.4658
97 | 433 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
98 | 434 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
99 | 435 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
100 | 436 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
101 | 437 | 2497.0909 | 2734.9091 | 2972.7273 | 445.9091 | 428.947 | 420.6071 |  | 2943 | 3163.8561 | 3393.3343
102 | 438 | 2657.4545 | 2910.5455 | 3163.6364 | 474.5455 | 456.4941 | 447.6185 |  | 3132 | 3367.0395 | 3611.2549
103 | 439 | 2817.8182 | 3086.1818 | 3354.5455 | 503.1818 | 484.0411 | 474.63 |  | 3321 | 3570.223 | 3829.1754
104 | 440 | 2978.1818 | 3261.8182 | 3545.4545 | 531.8182 | 511.5882 | 501.6414 |  | 3510 | 3773.4064 | 4047.096
105 | 441 | 3138.5455 | 3437.4545 | 3736.3636 | 560.4545 | 539.1353 | 528.6529 |  | 3699 | 3976.5898 | 4265.0165
106 | 442 | 3298.9091 | 3613.0909 | 3927.2727 | 589.0909 | 566.6823 | 555.6644 |  | 3888 | 4179.7732 | 4482.9371
107 | 443 | 3459.2727 | 3788.7273 | 4118.1818 | 617.7273 | 594.2294 | 582.6758 |  | 4077 | 4382.9566 | 4700.8576
108 | 444 | 3619.6364 | 3964.3636 | 4309.0909 | 646.3636 | 621.7764 | 609.6873 |  | 4266 | 4586.1401 | 4918.7782
109 | 445 | 3780 | 4140 | 4500 | 675 | 649.3235 | 636.6987 |  | 4455 | 4789.3235 | 5136.6987
110 | 446 | 3708 | 4061.1429 | 4414.2857 | 662.1429 | 636.9554 | 624.5712 |  | 4370.1429 | 4698.0983 | 5038.8569
111 | 447 | 3636 | 3982.2857 | 4328.5714 | 649.2857 | 624.5874 | 612.4436 |  | 4285.2857 | 4606.8731 | 4941.015
112 | 448 | 3564 | 3903.4286 | 4242.8571 | 636.4286 | 612.2193 | 600.316 |  | 4200.4286 | 4515.6479 | 4843.1731
113 | 449 | 3492 | 3824.5714 | 4157.1429 | 623.5714 | 599.8512 | 588.1884 |  | 4115.5714 | 4424.4227 | 4745.3312
114 | 450 | 3420 | 3745.7143 | 4071.4286 | 610.7143 | 587.4832 | 576.0608 |  | 4030.7143 | 4333.1974 | 4647.4893
115 | 451 | 3348 | 3666.8571 | 3985.7143 | 597.8571 | 575.1151 | 563.9332 |  | 3945.8571 | 4241.9722 | 4549.6475
116 | 452 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
117 | 453 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
118 | 454 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
119 | 455 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
120 | 456 | 2394 | 2622 | 2850 | 427.5 | 411.2382 | 403.2425 |  | 2821.5 | 3033.2382 | 3253.2425
121 | 457 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
122 | 458 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
123 | 459 | 2160 | 2365.7143 | 2571.4286 | 385.7143 | 371.042 | 363.8279 |  | 2545.7143 | 2736.7563 | 2935.2564
124 | 460 | 2304 | 2523.4286 | 2742.8571 | 411.4286 | 395.7781 | 388.083 |  | 2715.4286 | 2919.2067 | 3130.9402
125 | 461 | 2448 | 2681.1429 | 2914.2857 | 437.1429 | 420.5143 | 412.3382 |  | 2885.1429 | 3101.6571 | 3326.624
126 | 462 | 2592 | 2838.8571 | 3085.7143 | 462.8571 | 445.2504 | 436.5934 |  | 3054.8571 | 3284.1075 | 3522.3077
127 | 463 | 2736 | 2996.5714 | 3257.1429 | 488.5714 | 469.9865 | 460.8486 |  | 3224.5714 | 3466.558 | 3717.9915
128 | 464 | 2880 | 3154.2857 | 3428.5714 | 514.2857 | 494.7227 | 485.1038 |  | 3394.2857 | 3649.0084 | 3913.6752
129 | 465 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
130 | 466 | 3168 | 3469.7143 | 3771.4286 | 565.7143 | 544.1949 | 533.6142 |  | 3733.7143 | 4013.9092 | 4305.0428
131 | 467 | 3312 | 3627.4286 | 3942.8571 | 591.4286 | 568.9311 | 557.8694 |  | 3903.4286 | 4196.3596 | 4500.7265
132 | 468 | 3456 | 3785.1429 | 4114.2857 | 617.1429 | 593.6672 | 582.1246 |  | 4073.1429 | 4378.81 | 4696.4103
133 | 469 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
134 | 470 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
135 | 471 | 3888 | 4258.2857 | 4628.5714 | 694.2857 | 667.8756 | 654.8901 |  | 4582.2857 | 4926.1613 | 5283.4616
136 | 472 | 4032 | 4416 | 4800 | 720 | 692.6117 | 679.1453 |  | 4752 | 5108.6117 | 5479.1453
137 | 473 | 3830.4 | 4195.2 | 4560 | 684 | 657.9811 | 645.1881 |  | 4514.4 | 4853.1811 | 5205.1881
138 | 474 | 3628.8 | 3974.4 | 4320 | 648 | 623.3506 | 611.2308 |  | 4276.8 | 4597.7506 | 4931.2308
139 | 475 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
140 | 476 | 3225.6 | 3532.8 | 3840 | 576 | 554.0894 | 543.3163 |  | 3801.6 | 4086.8894 | 4383.3163
141 | 477 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
142 | 478 | 2822.4 | 3091.2 | 3360 | 504 | 484.8282 | 475.4017 |  | 3326.4 | 3576.0282 | 3835.4017
143 | 479 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
144 | 480 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
145 | 481 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
146 | 482 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
147 | 483 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
148 | 484 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
149 | 485 | 2394 | 2622 | 2850 | 427.5 | 411.2382 | 403.2425 |  | 2821.5 | 3033.2382 | 3253.2425
150 | 486 | 2520 | 2760 | 3000 | 450 | 432.8823 | 424.4658 |  | 2970 | 3192.8823 | 3424.4658
151 | 487 | 2646 | 2898 | 3150 | 472.5 | 454.5264 | 445.6891 |  | 3118.5 | 3352.5264 | 3595.6891
152 | 488 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
153 | 489 | 2898 | 3174 | 3450 | 517.5 | 497.8147 | 488.1357 |  | 3415.5 | 3671.8147 | 3938.1357
154 | 490 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
155 | 491 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
156 | 492 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
157 | 493 | 3402 | 3726 | 4050 | 607.5 | 584.3911 | 573.0289 |  | 4009.5 | 4310.3911 | 4623.0289
158 | 494 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
159 | 495 | 3402 | 3726 | 4050 | 607.5 | 584.3911 | 573.0289 |  | 4009.5 | 4310.3911 | 4623.0289
160 | 496 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
161 | 497 | 4032 | 4416 | 4800 | 720 | 692.6117 | 679.1453 |  | 4752 | 5108.6117 | 5479.1453
162 | 498 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
163 | 499 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
164 | 500 | 3880.8 | 4250.4 | 4620 | 693 | 666.6388 | 653.6774 |  | 4573.8 | 4917.0388 | 5273.6774
165 | 501 | 3603.6 | 3946.8 | 4290 | 643.5 | 619.0217 | 606.9861 |  | 4247.1 | 4565.8217 | 4896.9861
166 | 502 | 3326.4 | 3643.2 | 3960 | 594 | 571.4047 | 560.2949 |  | 3920.4 | 4214.6047 | 4520.2949
167 | 503 | 3049.2 | 3339.6 | 3630 | 544.5 | 523.7876 | 513.6037 |  | 3593.7 | 3863.3876 | 4143.6037
168 | 504 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
1 | 505 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
2 | 506 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
3 | 507 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
4 | 508 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
5 | 509 | 2583 | 2829 | 3075 | 461.25 | 443.7044 | 435.0775 |  | 3044.25 | 3272.7044 | 3510.0775
6 | 510 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
7 | 511 | 2961 | 3243 | 3525 | 528.75 | 508.6367 | 498.7474 |  | 3489.75 | 3751.6367 | 4023.7474
8 | 512 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
9 | 513 | 3339 | 3657 | 3975 | 596.25 | 573.5691 | 562.4172 |  | 3935.25 | 4230.5691 | 4537.4172
10 | 514 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
11 | 515 | 3717 | 4071 | 4425 | 663.75 | 638.5014 | 626.0871 |  | 4380.75 | 4709.5014 | 5051.0871
12 | 516 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
13 | 517 | 4095 | 4485 | 4875 | 731.25 | 703.4338 | 689.757 |  | 4826.25 | 5188.4338 | 5564.757
14 | 518 | 4284 | 4692 | 5100 | 765 | 735.9 | 721.5919 |  | 5049 | 5427.9 | 5821.5919
15 | 519 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
16 | 520 | 4326 | 4738 | 5150 | 772.5 | 743.1147 | 728.6663 |  | 5098.5 | 5481.1147 | 5878.6663
17 | 521 | 4914 | 5382 | 5850 | 877.5 | 844.1205 | 827.7084 |  | 5791.5 | 6226.1205 | 6677.7084
18 | 522 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
19 | 523 | 5040 | 5520 | 6000 | 900 | 865.7647 | 848.9317 |  | 5940 | 6385.7647 | 6848.9317
20 | 524 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
21 | 525 | 5166 | 5658 | 6150 | 922.5 | 887.4088 | 870.155 |  | 6088.5 | 6545.4088 | 7020.155
22 | 526 | 4536 | 4968 | 5400 | 810 | 779.1882 | 764.0385 |  | 5346 | 5747.1882 | 6164.0385
23 | 527 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
24 | 528 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
25 | 529 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
26 | 530 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
27 | 531 | 2167.2 | 2373.6 | 2580 | 387 | 372.2788 | 365.0406 |  | 2554.2 | 2745.8788 | 2945.0406
28 | 532 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
29 | 533 | 2502 | 2740.2857 | 2978.5714 | 446.7857 | 429.7903 | 421.4339 |  | 2948.7857 | 3170.076 | 3400.0054
30 | 534 | 2664 | 2917.7143 | 3171.4286 | 475.7143 | 457.6185 | 448.721 |  | 3139.7143 | 3375.3327 | 3620.1496
31 | 535 | 2826 | 3095.1429 | 3364.2857 | 504.6429 | 485.4466 | 476.0081 |  | 3330.6429 | 3580.5895 | 3840.2938
32 | 536 | 2988 | 3272.5714 | 3557.1429 | 533.5714 | 513.2748 | 503.2952 |  | 3521.5714 | 3785.8462 | 4060.4381
33 | 537 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
34 | 538 | 3312 | 3627.4286 | 3942.8571 | 591.4286 | 568.9311 | 557.8694 |  | 3903.4286 | 4196.3596 | 4500.7265
35 | 539 | 3474 | 3804.8571 | 4135.7143 | 620.3571 | 596.7592 | 585.1565 |  | 4094.3571 | 4401.6164 | 4720.8708
36 | 540 | 3636 | 3982.2857 | 4328.5714 | 649.2857 | 624.5874 | 612.4436 |  | 4285.2857 | 4606.8731 | 4941.015
37 | 541 | 3798 | 4159.7143 | 4521.4286 | 678.2143 | 652.4155 | 639.7306 |  | 4476.2143 | 4812.1298 | 5161.1592
38 | 542 | 3960 | 4337.1429 | 4714.2857 | 707.1429 | 680.2437 | 667.0177 |  | 4667.1429 | 5017.3865 | 5381.3035
39 | 543 | 4122 | 4514.5714 | 4907.1429 | 736.0714 | 708.0718 | 694.3048 |  | 4858.0714 | 5222.6432 | 5601.4477
40 | 544 | 4284 | 4692 | 5100 | 765 | 735.9 | 721.5919 |  | 5049 | 5427.9 | 5821.5919
41 | 545 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
42 | 546 | 4410 | 4830 | 5250 | 787.5 | 757.5441 | 742.8152 |  | 5197.5 | 5587.5441 | 5992.8152
43 | 547 | 4662 | 5106 | 5550 | 832.5 | 800.8323 | 785.2618 |  | 5494.5 | 5906.8323 | 6335.2618
44 | 548 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
45 | 549 | 5166 | 5658 | 6150 | 922.5 | 887.4088 | 870.155 |  | 6088.5 | 6545.4088 | 7020.155
46 | 550 | 4536 | 4968 | 5400 | 810 | 779.1882 | 764.0385 |  | 5346 | 5747.1882 | 6164.0385
47 | 551 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
48 | 552 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
49 | 553 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
50 | 554 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
51 | 555 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
52 | 556 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
53 | 557 | 2539.3846 | 2781.2308 | 3023.0769 | 453.4615 | 436.2122 | 427.731 |  | 2992.8462 | 3217.443 | 3450.8079
54 | 558 | 2713.8462 | 2972.3077 | 3230.7692 | 484.6154 | 466.181 | 457.1171 |  | 3198.4615 | 3438.4887 | 3687.8863
55 | 559 | 2888.3077 | 3163.3846 | 3438.4615 | 515.7692 | 496.1497 | 486.5031 |  | 3404.0769 | 3659.5344 | 3924.9647
56 | 560 | 3062.7692 | 3354.4615 | 3646.1538 | 546.9231 | 526.1185 | 515.8892 |  | 3609.6923 | 3880.5801 | 4162.0431
57 | 561 | 3237.2308 | 3545.5385 | 3853.8462 | 578.0769 | 556.0873 | 545.2753 |  | 3815.3077 | 4101.6258 | 4399.1215
58 | 562 | 3411.6923 | 3736.6154 | 4061.5385 | 609.2308 | 586.0561 | 574.6614 |  | 4020.9231 | 4322.6715 | 4636.1999
59 | 563 | 3586.1538 | 3927.6923 | 4269.2308 | 640.3846 | 616.0249 | 604.0475 |  | 4226.5385 | 4543.7172 | 4873.2783
60 | 564 | 3760.6154 | 4118.7692 | 4476.9231 | 671.5385 | 645.9936 | 633.4336 |  | 4432.1538 | 4764.7629 | 5110.3567
61 | 565 | 3935.0769 | 4309.8462 | 4684.6154 | 702.6923 | 675.9624 | 662.8197 |  | 4637.7692 | 4985.8086 | 5347.4351
62 | 566 | 4109.5385 | 4500.9231 | 4892.3077 | 733.8462 | 705.9312 | 692.2058 |  | 4843.3846 | 5206.8543 | 5584.5135
63 | 567 | 4284 | 4692 | 5100 | 765 | 735.9 | 721.5919 |  | 5049 | 5427.9 | 5821.5919
64 | 568 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
65 | 569 | 4384.8 | 4802.4 | 5220 | 783 | 753.2152 | 738.5705 |  | 5167.8 | 5555.6152 | 5958.5705
66 | 570 | 4611.6 | 5050.8 | 5490 | 823.5 | 792.1747 | 776.7725 |  | 5435.1 | 5842.9747 | 6266.7725
67 | 571 | 5040 | 5520 | 6000 | 900 | 865.7647 | 848.9317 |  | 5940 | 6385.7647 | 6848.9317
68 | 572 | 5040 | 5520 | 6000 | 900 | 865.7647 | 848.9317 |  | 5940 | 6385.7647 | 6848.9317
69 | 573 | 5292 | 5796 | 6300 | 945 | 909.0529 | 891.3782 |  | 6237 | 6705.0529 | 7191.3782
70 | 574 | 4636.8 | 5078.4 | 5520 | 828 | 796.5035 | 781.0171 |  | 5464.8 | 5874.9035 | 6301.0171
71 | 575 | 3981.6 | 4360.8 | 4740 | 711 | 683.9541 | 670.656 |  | 4692.6 | 5044.7541 | 5410.656
72 | 576 | 3326.4 | 3643.2 | 3960 | 594 | 571.4047 | 560.2949 |  | 3920.4 | 4214.6047 | 4520.2949
73 | 577 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
74 | 578 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
75 | 579 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
76 | 580 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
77 | 581 | 2520 | 2760 | 3000 | 450 | 432.8823 | 424.4658 |  | 2970 | 3192.8823 | 3424.4658
78 | 582 | 2688 | 2944 | 3200 | 480 | 461.7411 | 452.7636 |  | 3168 | 3405.7411 | 3652.7636
79 | 583 | 2856 | 3128 | 3400 | 510 | 490.6 | 481.0613 |  | 3366 | 3618.6 | 3881.0613
80 | 584 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
81 | 585 | 3192 | 3496 | 3800 | 570 | 548.3176 | 537.6567 |  | 3762 | 4044.3176 | 4337.6567
82 | 586 | 3360 | 3680 | 4000 | 600 | 577.1764 | 565.9544 |  | 3960 | 4257.1764 | 4565.9544
83 | 587 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
84 | 588 | 3696 | 4048 | 4400 | 660 | 634.8941 | 622.5499 |  | 4356 | 4682.8941 | 5022.5499
85 | 589 | 3864 | 4232 | 4600 | 690 | 663.7529 | 650.8476 |  | 4554 | 4895.7529 | 5250.8476
86 | 590 | 4032 | 4416 | 4800 | 720 | 692.6117 | 679.1453 |  | 4752 | 5108.6117 | 5479.1453
87 | 591 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
88 | 592 | 4200 | 4600 | 5000 | 750 | 721.4705 | 707.4431 |  | 4950 | 5321.4705 | 5707.4431
89 | 593 | 4494 | 4922 | 5350 | 802.5 | 771.9735 | 756.9641 |  | 5296.5 | 5693.9735 | 6106.9641
90 | 594 | 4788 | 5244 | 5700 | 855 | 822.4764 | 806.4851 |  | 5643 | 6066.4764 | 6506.4851
91 | 595 | 4441.5 | 4864.5 | 5287.5 | 793.125 | 762.9551 | 748.121 |  | 5234.625 | 5627.4551 | 6035.621
92 | 596 | 4095 | 4485 | 4875 | 731.25 | 703.4338 | 689.757 |  | 4826.25 | 5188.4338 | 5564.757
93 | 597 | 3748.5 | 4105.5 | 4462.5 | 669.375 | 643.9125 | 631.3929 |  | 4417.875 | 4749.4125 | 5093.8929
94 | 598 | 3402 | 3726 | 4050 | 607.5 | 584.3911 | 573.0289 |  | 4009.5 | 4310.3911 | 4623.0289
95 | 599 | 3055.5 | 3346.5 | 3637.5 | 545.625 | 524.8698 | 514.6648 |  | 3601.125 | 3871.3698 | 4152.1648
96 | 600 | 2520 | 2760 | 3000 | 450 | 432.8823 | 424.4658 |  | 2970 | 3192.8823 | 3424.4658
97 | 601 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
98 | 602 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
99 | 603 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
100 | 604 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
101 | 605 | 2497.0909 | 2734.9091 | 2972.7273 | 445.9091 | 428.947 | 420.6071 |  | 2943 | 3163.8561 | 3393.3343
102 | 606 | 2657.4545 | 2910.5455 | 3163.6364 | 474.5455 | 456.4941 | 447.6185 |  | 3132 | 3367.0395 | 3611.2549
103 | 607 | 2817.8182 | 3086.1818 | 3354.5455 | 503.1818 | 484.0411 | 474.63 |  | 3321 | 3570.223 | 3829.1754
104 | 608 | 2978.1818 | 3261.8182 | 3545.4545 | 531.8182 | 511.5882 | 501.6414 |  | 3510 | 3773.4064 | 4047.096
105 | 609 | 3138.5455 | 3437.4545 | 3736.3636 | 560.4545 | 539.1353 | 528.6529 |  | 3699 | 3976.5898 | 4265.0165
106 | 610 | 3298.9091 | 3613.0909 | 3927.2727 | 589.0909 | 566.6823 | 555.6644 |  | 3888 | 4179.7732 | 4482.9371
107 | 611 | 3459.2727 | 3788.7273 | 4118.1818 | 617.7273 | 594.2294 | 582.6758 |  | 4077 | 4382.9566 | 4700.8576
108 | 612 | 3619.6364 | 3964.3636 | 4309.0909 | 646.3636 | 621.7764 | 609.6873 |  | 4266 | 4586.1401 | 4918.7782
109 | 613 | 3780 | 4140 | 4500 | 675 | 649.3235 | 636.6987 |  | 4455 | 4789.3235 | 5136.6987
110 | 614 | 3708 | 4061.1429 | 4414.2857 | 662.1429 | 636.9554 | 624.5712 |  | 4370.1429 | 4698.0983 | 5038.8569
111 | 615 | 3636 | 3982.2857 | 4328.5714 | 649.2857 | 624.5874 | 612.4436 |  | 4285.2857 | 4606.8731 | 4941.015
112 | 616 | 3564 | 3903.4286 | 4242.8571 | 636.4286 | 612.2193 | 600.316 |  | 4200.4286 | 4515.6479 | 4843.1731
113 | 617 | 3492 | 3824.5714 | 4157.1429 | 623.5714 | 599.8512 | 588.1884 |  | 4115.5714 | 4424.4227 | 4745.3312
114 | 618 | 3420 | 3745.7143 | 4071.4286 | 610.7143 | 587.4832 | 576.0608 |  | 4030.7143 | 4333.1974 | 4647.4893
115 | 619 | 3348 | 3666.8571 | 3985.7143 | 597.8571 | 575.1151 | 563.9332 |  | 3945.8571 | 4241.9722 | 4549.6475
116 | 620 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
117 | 621 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
118 | 622 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
119 | 623 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
120 | 624 | 2394 | 2622 | 2850 | 427.5 | 411.2382 | 403.2425 |  | 2821.5 | 3033.2382 | 3253.2425
121 | 625 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
122 | 626 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
123 | 627 | 2160 | 2365.7143 | 2571.4286 | 385.7143 | 371.042 | 363.8279 |  | 2545.7143 | 2736.7563 | 2935.2564
124 | 628 | 2304 | 2523.4286 | 2742.8571 | 411.4286 | 395.7781 | 388.083 |  | 2715.4286 | 2919.2067 | 3130.9402
125 | 629 | 2448 | 2681.1429 | 2914.2857 | 437.1429 | 420.5143 | 412.3382 |  | 2885.1429 | 3101.6571 | 3326.624
126 | 630 | 2592 | 2838.8571 | 3085.7143 | 462.8571 | 445.2504 | 436.5934 |  | 3054.8571 | 3284.1075 | 3522.3077
127 | 631 | 2736 | 2996.5714 | 3257.1429 | 488.5714 | 469.9865 | 460.8486 |  | 3224.5714 | 3466.558 | 3717.9915
128 | 632 | 2880 | 3154.2857 | 3428.5714 | 514.2857 | 494.7227 | 485.1038 |  | 3394.2857 | 3649.0084 | 3913.6752
129 | 633 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
130 | 634 | 3168 | 3469.7143 | 3771.4286 | 565.7143 | 544.1949 | 533.6142 |  | 3733.7143 | 4013.9092 | 4305.0428
131 | 635 | 3312 | 3627.4286 | 3942.8571 | 591.4286 | 568.9311 | 557.8694 |  | 3903.4286 | 4196.3596 | 4500.7265
132 | 636 | 3456 | 3785.1429 | 4114.2857 | 617.1429 | 593.6672 | 582.1246 |  | 4073.1429 | 4378.81 | 4696.4103
133 | 637 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
134 | 638 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
135 | 639 | 3888 | 4258.2857 | 4628.5714 | 694.2857 | 667.8756 | 654.8901 |  | 4582.2857 | 4926.1613 | 5283.4616
136 | 640 | 4032 | 4416 | 4800 | 720 | 692.6117 | 679.1453 |  | 4752 | 5108.6117 | 5479.1453
137 | 641 | 3830.4 | 4195.2 | 4560 | 684 | 657.9811 | 645.1881 |  | 4514.4 | 4853.1811 | 5205.1881
138 | 642 | 3628.8 | 3974.4 | 4320 | 648 | 623.3506 | 611.2308 |  | 4276.8 | 4597.7506 | 4931.2308
139 | 643 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
140 | 644 | 3225.6 | 3532.8 | 3840 | 576 | 554.0894 | 543.3163 |  | 3801.6 | 4086.8894 | 4383.3163
141 | 645 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
142 | 646 | 2822.4 | 3091.2 | 3360 | 504 | 484.8282 | 475.4017 |  | 3326.4 | 3576.0282 | 3835.4017
143 | 647 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
144 | 648 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
145 | 649 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
146 | 650 | 2016 | 2208 | 2400 | 360 | 346.3059 | 339.5727 |  | 2376 | 2554.3059 | 2739.5727
147 | 651 | 2142 | 2346 | 2550 | 382.5 | 367.95 | 360.796 |  | 2524.5 | 2713.95 | 2910.796
148 | 652 | 2268 | 2484 | 2700 | 405 | 389.5941 | 382.0192 |  | 2673 | 2873.5941 | 3082.0192
149 | 653 | 2394 | 2622 | 2850 | 427.5 | 411.2382 | 403.2425 |  | 2821.5 | 3033.2382 | 3253.2425
150 | 654 | 2520 | 2760 | 3000 | 450 | 432.8823 | 424.4658 |  | 2970 | 3192.8823 | 3424.4658
151 | 655 | 2646 | 2898 | 3150 | 472.5 | 454.5264 | 445.6891 |  | 3118.5 | 3352.5264 | 3595.6891
152 | 656 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
153 | 657 | 2898 | 3174 | 3450 | 517.5 | 497.8147 | 488.1357 |  | 3415.5 | 3671.8147 | 3938.1357
154 | 658 | 3024 | 3312 | 3600 | 540 | 519.4588 | 509.359 |  | 3564 | 3831.4588 | 4109.359
155 | 659 | 3150 | 3450 | 3750 | 562.5 | 541.1029 | 530.5823 |  | 3712.5 | 3991.1029 | 4280.5823
156 | 660 | 3276 | 3588 | 3900 | 585 | 562.747 | 551.8056 |  | 3861 | 4150.747 | 4451.8056
157 | 661 | 3402 | 3726 | 4050 | 607.5 | 584.3911 | 573.0289 |  | 4009.5 | 4310.3911 | 4623.0289
158 | 662 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
159 | 663 | 3402 | 3726 | 4050 | 607.5 | 584.3911 | 573.0289 |  | 4009.5 | 4310.3911 | 4623.0289
160 | 664 | 3528 | 3864 | 4200 | 630 | 606.0353 | 594.2522 |  | 4158 | 4470.0353 | 4794.2522
161 | 665 | 4032 | 4416 | 4800 | 720 | 692.6117 | 679.1453 |  | 4752 | 5108.6117 | 5479.1453
162 | 666 | 3906 | 4278 | 4650 | 697.5 | 670.9676 | 657.922 |  | 4603.5 | 4948.9676 | 5307.922
163 | 667 | 4158 | 4554 | 4950 | 742.5 | 714.2558 | 700.3686 |  | 4900.5 | 5268.2558 | 5650.3686
164 | 668 | 3880.8 | 4250.4 | 4620 | 693 | 666.6388 | 653.6774 |  | 4573.8 | 4917.0388 | 5273.6774
165 | 669 | 3603.6 | 3946.8 | 4290 | 643.5 | 619.0217 | 606.9861 |  | 4247.1 | 4565.8217 | 4896.9861
166 | 670 | 3326.4 | 3643.2 | 3960 | 594 | 571.4047 | 560.2949 |  | 3920.4 | 4214.6047 | 4520.2949
167 | 671 | 3049.2 | 3339.6 | 3630 | 544.5 | 523.7876 | 513.6037 |  | 3593.7 | 3863.3876 | 4143.6037
168 | 672 | 2772 | 3036 | 3300 | 495 | 476.1706 | 466.9124 |  | 3267 | 3512.1706 | 3766.9124
| Sum | 2227714.5 | 2439877.8 | 2652041.1 | 397806.2 | 382673.9 | 375233.6
| Check Sum | 2227714.5 | 2439877.8 | 2652041.1 | 397806.2 | 382673.9 | 375233.6
|  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE

## Split Condenser
Condenser
Total Heat Released | Qactual | kW | 5900
Total Mass Flow Rate |  | kg/s | 141.01
Water Specific Heat | cp, cwater | kJ/kg·K | 4.181
Overall Heat Transfer Coefficient | U | kW/m2·K | 1
Primary Side Condenser Inlet Temperature |  | °C | 30
|  |  | First Stage | Second Stage | Initial Value
Secondary Side Mass Flow Rate |  | kg/s | 94 | 38.4394 | 47.01
Secondary Side Stage Inlet Temperature |  | °C | 20 | 10
Heat Transfer Area | A | m2 | 500 | 500
Minimum Heat Capacity Rate | Cmin | kJ/s·K | 393.014 | 160.7153
Number of Transfer Units | UA/Cmin | NTU | 1.2722 | 3.1111
Effectiveness | Ɛ |  | 0.71979 | 0.95545
ƐCmin |  |  | 282.8879 | 153.555
Qc actual |  | kW | 2828.8792 | 3071.1005 | 3071.1208
|  |  | Check Sum | 5899.9796

## Split Evaporator
Evaporator | [5 empty] | Side Calculation
Total Heat Released | Qactual | kW | 7200 |  |  | Heat Released | 2733704 | TRUE
Total Mass Flow Rate |  | kg/s | 141.01 |  |  | Heat to Hot Sink | 2113975 | 77.33%
Water Specific Heat | cp, cwater | kJ/kg·K | 4.181 |  |  | Heat to Cold Sink | 619729 | 22.67%
Overall Heat Transfer Coefficient | U | kW/m2·K | 1
Primary Side Evaporator Inlet Temperature |  | °C | 5 |  |  | HP Heat Demand | 2412546 | TRUE
[6 empty] | HP Hot Sink Supply | 380256 | 15.76%
|  |  | First Stage | Second Stage | Initial Value | HP Cold Sink Supply | 2032290 | 84.24%
Secondary Side Mass Flow Rate |  | kg/s | 40 | 369.0087 | 101.01
Secondary Side Stage Inlet Temperature |  | °C | 10 | 20
Heat Transfer Area | A | m2 | 500 | 500
Minimum Heat Capacity Rate | Cmin | kJ/s·K | 167.24 | 1542.8254
Number of Transfer Units | UA/Cmin | NTU | 2.9897 | 0.32408
Effectiveness | Ɛ |  | 0.9497 | 0.27681
ƐCmin |  |  | 158.8275 | 427.0666
Qc actual |  | kW | 794.1377 | 6405.9997 | 6405.8623
|  |  | Check Sum | 7200.1374

## NTU Calcs
Tc, in
| Condenser overall heat transfer coefficient | U | W/m2.k | 1400
(kJ/s°K) | Heat exchanger heat transfer area | A | m2 | 1500
| Secondary-side water mass flow rate | ṁ | kg/s | 146.1
| Water specific heat capcity | cp | KJ/kg.K | 4.181
| Hot network temperature rise | K | °K | 10
Calculations
| Water heat capacity rate | Cmin | KJ/s∙K | 610.8441
| NTU | NTU |  | 3.4379
| Effectiveness | Ɛ |  | 0.96787
| Heat transfer | Qch actual | MW | 5.9122
6.1084

## Calcs Cold Sink Secondary Sid
[12 empty] | 138156.6994 | 138160 | 138160 | 138156
0
HP Evaporator Secondary Side Flow Rate (kg/s)
| Qc Qh | 10 |  | 20 |  | 30 |  | 40 |  | 50 |  | 7.2195e-08
Condenser Secondary Side Flow Rate (kg/s) | 10 | 0 | 151941 | 3202 | 131849 | 0 | 138157 | 2118 | 116497 | 81892 | 94124 | 4.3317e-07
| 20 | 0 | 266189 | 0 | 248263 | 0 | 246159 | 0 | 187778 | 0 | 144666 | 2.238e-06
| 30 | 0 | 351049 | 0 | 330097 | 0 | 298086 | 0 | 276411 | 0 | 320885 | 1.1262e-05
0.0014099
0.0070464
|  | HP Evaporator Secondary Side Flow Rate (kg/s) | [9 empty] | 0.035156
| Qc Qh | 10 | 20 | 30 | 40 | 50 | [5 empty] | 0.099222
Condenser Secondary Side Flow Rate (kg/s) | 10 | 151941 | 135051 | 138157 | 118615 | 176016 | [5 empty] | 0.19684
| 20 | 266189 | 248263 | 246159 | 187778 | 144666 | [5 empty] | 0.29277
| 30 | 351049 | 330097 | 298086 | 276411 | 320885 | [5 empty] | 0.38693
0.6581
0.74446
0.82868
0.91069
0.99041
1.0678
1.1427
1.2151
1.285
1.3522
1.4167
1.4785
1.5373
1.5933
1.6463
1.6962
1.7429
1.7864
1.8265
1.8633
1.8965
1.9261
1.952
1.9741
1.9924
2.0066
2.0168
2.0229
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0247
2.0651
2.2695
2.6464
3.1957
3.9174
4.8113
5.8775
7.1157
8.526
10.1081
11.8621
13.7878
15.8852
18.1541
20.5944
23.2061
25.9891
28.9432
32.0684
35.3646
38.8316
42.4695
46.2779
50.257
54.4065
58.7264
63.2166
67.8769
72.7072
77.7074
82.8774
88.2171
93.7263
99.405
105.2529
111.2701
117.4563
123.8115
130.3356
137.0283
143.8897
150.9195
158.1177
165.4841
173.0187
180.7213
188.5924
196.6323
204.8415
213.2203
221.7693
230.4888
239.3795
248.4418
257.6762
267.0829
276.6621
286.4138
296.3381
306.4352
316.7051
327.148
337.764
348.5532
359.5156
370.6515
381.9608
393.4437
405.1003
416.9307
428.9351
441.1134
453.4658
465.9924
478.6932
491.5685
504.6182
517.8426
531.2415
544.8153
558.5639
572.4874
586.586
600.8597
615.3086
629.9328
644.7324
659.7074
674.858
690.1843
705.6862
721.364
737.2177
753.2473
769.453
785.8348
802.3929
819.1272
836.0379
853.125
870.3886
887.8288
905.4457
923.2393
941.2098
959.3571
977.6813
996.1826
1014.861
1033.7165
1052.7492
1071.9593
1091.3467
1110.9115
1130.6538
1150.5736
1170.6711
1190.9462
1211.3991
1232.0297
1252.8382
1273.8246
1294.989
1316.3314
1337.8519
1359.5506
1381.4274
1403.4826
1425.7162
1448.1283
1470.7189
1493.4882
1516.4362
1539.563
1562.8687
1586.3533
1610.0169
1633.8595
1657.8812
1682.082
1706.462
1731.0212
1755.7597
1780.6774
1805.7744
1831.0508
1856.5067
1882.1419
1907.9566
1933.9508
1960.1244
1986.4777
2013.0105
2039.7229
2066.6149
2093.6866
2120.938
2148.369
2175.9797
2203.7701
2231.7403
2259.8902
2288.2199
2316.7293
2345.4185
2374.2876
2403.3366
2432.5655
2461.9744
2491.5635
2521.3327
2551.2821
2581.4118
2611.7219
2642.2125
2672.8835
2703.7351
2734.7675
2765.9805
2797.3744
2828.9492
2860.705
2892.6419
2924.7599
2957.0592
2989.5399
3022.202
3055.0456
3088.0708
3121.2777
3154.6665
3188.2371
3221.9898
3255.9246
3290.0416
3324.3409
3358.8227
3393.487
3428.3339
3463.3636
3498.5761
3533.9717
3569.5503
3605.3121
3641.2572
3677.3853
3713.6959
3750.1887
3786.8633
3823.7192
3860.756
3897.973
3935.3699
3972.9461
4010.7012
4048.6353
4086.7482
4125.0399
4163.5102
4202.1591
4240.9865
4279.9922
4319.1763
4358.5387
4398.0792
4437.7978
4477.6944
4517.7689
4558.0212
4598.4513
4639.0591
4679.8445
4720.8075
4761.9479
4803.2657
4844.7608
4886.4331
4928.2825
4970.309
5012.5124
5054.8928
5097.4498
5140.1836
5183.094
5226.181
5269.4443
5312.884
5356.4998
5400.2918
5444.2598
5488.4037
5532.7234
5577.2187
5621.8896
5666.736
5711.7577
5756.9547
5802.3268
5847.8739
5893.5959
5939.4927
5985.5641
6031.8102
6078.2306
6124.8254
6171.5944
6218.5375
6265.6545
6312.9454
6360.4099
6408.048
6455.8595
6503.8444
6552.0023
6600.3334
6648.8373
6697.514
6746.3633
6795.3851
6844.5793
6893.9458
6943.4843
6993.1948
7043.0771
7093.1312
7143.3569
7193.7546
7244.3247
7295.0675
7345.9836
7397.0732
7448.337
7499.7753
7551.3888
7603.1778
7655.1425
7707.2831
7759.5997
7812.0923
7864.761
7917.606
7970.6273
8023.825
8077.1992
8130.75
8184.4775
8238.3818
8292.463
8346.7211
8401.1563
8455.7687
8510.5582
8565.5251
8620.6694
8675.9911
8731.4904
8787.1674
8843.0221
8899.0546
8955.265
9011.6533
9068.2197
9124.9643
9181.887
9238.988
9296.2674
9353.7252
9411.3615
9469.1763
9527.1698
9585.3421
9643.6931
9702.223
9760.9318
9819.8196
9878.8865
9938.1325
9997.5578
10057.1622
10116.946
10176.9092
10237.0519
10297.3741
10357.8758
10418.5572
10479.4183
10540.4591
10601.6798
10663.0803
10724.6608
10786.4212
10848.3617
10910.4823
10972.7831
11035.264
11097.9252
11160.7668
11223.7887
11286.9912
11350.3742
11413.9378
11477.6822
11541.6073
11605.7132
11670.0001
11734.468
11799.1169
11863.947
11928.9583
11994.1508
12059.5248
12125.0801
12190.817
12256.7355
12322.8356
12389.1175
12455.5811
12522.2267
12589.0542
12656.0638
12723.2555
12790.6294
12858.1856
12925.9241
12993.845
13061.9485
13130.2345
13198.7032
13267.3547
13336.189
13405.2061
13474.4063
13543.7895
13613.3559
13683.1055
13753.0384
13823.1547
13893.4545
13963.9378
14034.6047
14105.4554
14176.4898
14247.7082
14319.1105
14390.6968
14462.4673
14534.422
14606.5609
14678.8843
14751.3921
14824.0845
14896.9615
14970.0233
15043.2698
15116.7012
15190.3176
15264.1191
15338.1057
15412.2776
15486.6348
15561.1774
15635.9055
15710.8192
15785.9185
15861.2037
15936.6746
16012.3314
16088.1742
16164.203
16240.4179
16316.8189
16393.406
16470.1794
16547.1391
16624.2851
16701.6176
16779.1366
16856.8422
16934.7346
17012.8139
17091.0801
17169.5334
17248.1739
17327.0017
17406.0168
17485.219
17564.6079
17644.1831
17723.9441
17803.8906
17884.0219
17964.3377
18044.8373
18125.5203
18206.3864
18287.4355
18368.6674
18450.0822
18531.6796
18613.4596
18695.422
18777.5668
18859.8938
18942.403
19025.0943
19107.9675
19191.0226
19274.2595
19357.6781
19441.2782
19525.0599
19609.0231
19693.1675
19777.4932
19862.0002
19946.6881
20031.5571
20116.6069
20201.8374
20287.2486
20372.8403
20458.6125
20544.5649
20630.6975
20717.0103
20803.503
20890.1755
20977.0278
21064.0596
21151.271
21238.6616
21326.2316
21413.9806
21501.9086
21590.0154
21678.3009
21766.765
21855.4076
21944.2285
22033.2276
22122.4048
22211.7599
22301.2928
22391.0034
22480.8914
22570.9569
22661.1996
22751.6195
22842.2163
22932.99
23023.9404
23115.0673
23206.3706
23297.8503
23389.5061
23481.3378
23573.3455
23665.5288
23757.8877
23850.422
23943.1316
24036.0164
24129.076
24222.3106
24315.7198
24409.3037
24503.0625
24596.9967
24691.1066
24785.3926
24879.8551
24974.4947
25069.3117
25164.3068
25259.4803
25354.8324
25450.3632
25546.0728
25641.9612
25738.0287
25834.2751
25930.7007
26027.3056
26124.0897
26221.0531
26318.1955
26415.5164
26513.0155
26610.6923
26708.5461
26806.5766
26904.7832
27003.1652
27101.7221
27200.4537
27299.3596
27398.4398
27497.6941
27597.1223
27696.7242
27796.4996
27896.4485
27996.5705
28096.8656
28197.3335
28297.9741
28398.7871
28499.7725
28600.93
28702.2595
28803.7607
28905.4335
29007.2778
29109.2932
29211.4797
29313.837
29416.3649
29519.0634
29621.9321
29724.971
29828.1797
29931.5582
30035.1062
30138.8235
30242.71
30346.7654
30450.9896
30555.3824
30659.9436
30764.673
30869.5704
30974.6357
31079.8686
31185.269
31290.8366
31396.5713
31502.4728
31608.5411
31714.776
31821.1771
31927.7444
32034.4777
32141.3767
32248.4414
32355.6715
32463.0667
32570.627
32678.352
32786.2415
32894.2954
33002.5133
33110.8952
33219.4407
33328.1496
33437.0217
33546.057
33655.2555
33764.6178
33874.144
33983.8345
34093.6896
34203.7098
34313.8955
34424.2472
34534.7651
34645.4495
34756.3004
34867.3179
34978.5019
35089.8526
35201.37
35313.0542
35424.9053
35536.9232
35649.1081
35761.46
35873.9789
35986.665
36099.5183
36212.5388
36325.7266
36439.0819
36552.6046
36666.2948
36780.1526
36894.1781
37008.3712
37122.7322
37237.2609
37351.9576
37466.8222
37581.8549
37697.0556
37812.4245
37927.9616
38043.6669
38159.5407
38275.5829
38391.7937
38508.173
38624.7211
38741.438
38858.3238
38975.3786
39092.6025
39209.9955
39327.5578
39445.2894
39563.1904
39681.2609
39799.5011
39917.9109
40036.4905
40155.24
40274.1595
40393.249
40512.5087
40631.9387
40751.5389
40871.3097
40991.251
41111.3629
41231.6456
41352.0992
41472.7236
41593.5186
41714.4838
41835.619
41956.9235
42078.397
42200.0391
42321.8492
42443.8269
42565.9716
42688.2831
42810.7613
42933.406
43056.2172
43179.1947
43302.3384
43425.6481
43549.1238
43672.7654
43796.5726
43920.5454
44044.6837
44168.9874
44293.4562
44418.0902
44542.8892
44667.8531
44792.9817
44918.275
45043.7328
45169.3551
45295.1416
45421.0923
45547.2071
45673.4857
45799.9282
45926.5344
46053.3041
46180.2372
46307.3336
46434.5932
46562.0159
46689.6014
46817.3498
46945.2607
47073.3342
47201.57
47329.968
47458.5281
47587.2502
47716.134
47845.1796
47974.3866
48103.755
48233.2846
48362.9754
48492.827
48622.8395
48753.0126
48883.3463
49013.8403
49144.4945
49275.3088
49406.283
49537.4169
49668.7105
49800.1636
49931.776
50063.5475
50195.4781
50327.5675
50459.8156
50592.2223
50724.7873
50857.5107
50990.3921
51123.4314
51256.6285
51389.9832
51523.4954
51657.1649
51790.9916
51924.9759
52059.1182
52193.4186
52327.8778
52462.4961
52597.2739
52732.2117
52867.31
53002.5693
53137.9897
53273.5713
53409.3141
53545.2183
53681.284
53817.5111
53953.8998
54090.4502
54227.1622
54364.036
54501.0712
54638.2673
54775.624
54913.1407
55050.8169
55188.6521
55326.6457
55464.7971
55603.1058
55741.5714
55880.1938
56018.9727
56157.9081
56296.9996
56436.2472
56575.6507
56715.2098
56854.9244
56994.7943
57134.8194
57274.9993
57415.334
57555.8233
57696.467
57837.2649
57978.2167
58119.3224
58260.5817
58401.9944
58543.5604
58685.2794
58827.1513
58969.1759
59111.3529
59253.6822
59396.1636
59538.7969
59681.5819
59824.5184
59967.6062
60110.8452
60254.235
60397.7755
60541.4666
60685.308
60829.2995
60965.2476
61100.8858
61236.2138
61371.2313
61505.9383
61640.3345
61774.4198
61908.1938
62041.6565
62174.8075
62307.6468
62440.1742
62572.3893
62704.2921
62835.8823
62967.1597
63098.1242
63228.7757
63359.1138
63489.1385
63618.8496
63748.2468
63877.3301
64006.0992
64134.554
64262.6949
64390.5221
64518.036
64645.2369
64772.1253
64898.7015
65024.9659
65150.9191
65276.5614
65401.893
65526.9138
65651.6239
65776.0232
65900.1119
66023.8898
66147.357
66270.5134
66393.3592
66515.8943
66638.1186
66760.0324
66881.6355
67002.9281
67123.9102
67244.5819
67364.9431
67484.994
67604.7346
67724.1649
67843.285
67962.0949
68080.5946
68198.7841
68316.6634
68434.2326
68551.4917
68668.4406
68785.0795
68901.4082
69017.4269
69133.1356
69248.5343
69363.6232
69478.4023
69592.8716
69707.0312
69820.8812
69934.4215
70047.6524
70160.5738
70273.1859
70385.4886
70497.4821
70609.1665
70720.5417
70831.6079
70942.3652
71052.8136
71162.9533
71272.7842
71382.3065
71491.5202
71600.4255
71709.0224
71817.311
71925.2914
72032.9637
72140.328
72247.3843
72354.1322
72460.5715
72566.7016
72672.5221
72778.0325
72883.2323
72988.1211
73092.6981
73196.963
73300.9153
73404.5551
73507.882
73610.8961
73713.5972
73815.9851
73918.0597
74019.8209
74121.2685
74222.4025
74323.2227
74423.729
74523.9213
74623.7995
74723.3636
74822.6134
74921.5489
75020.17
75118.4766
75216.4686
75314.1461
75411.5088
75508.5567
75605.2896
75701.7075
75797.8103
75893.5978
75989.0699
76084.2266
76179.0678
76273.5933
76367.803
76461.6968
76555.2747
76648.5363
76741.4818
76834.1108
76926.4234
77018.4193
77110.0985
77201.4608
77292.5061
77383.2343
77473.6452
77563.7388
77653.5149
77742.9734
77832.1141
77920.9369
78009.4418
78097.6284
78185.4969
78273.0469
78360.2783
78447.191
78533.7848
78620.0597
78706.0153
78791.6516
78876.9685
78961.9657
79046.6432
79131.0007
79215.0382
79298.7554
79382.1523
79465.2286
79547.9843
79630.4191
79712.533
79794.3257
79875.7973
79956.948
80037.7781
80118.2882
80198.4785
80278.3495
80357.9016
80437.1353
80516.0512
80594.6496
80672.9308
80750.8947
80828.5416
80905.8714
80982.8843
81059.5803
81135.9595
81212.022
81287.7678
81363.1971
81438.3093
81513.1042
81587.5812
81661.74
81735.5799
81809.1004
81882.301
81955.1812
82027.7402
82099.9779
82171.894
82243.4883
82314.7608
82385.7111
82456.3392
82526.6448
82596.6278
82666.288
82735.6251
82804.6391
82873.3297
82941.6968
83009.7401
83077.4595
83144.8549
83211.9259
83278.6724
83345.0943
83411.1913
83476.9633
83542.41
83607.5313
83672.3269
83736.7968
83800.9406
83864.7583
83928.2495
83991.4142
84054.252
84116.7629
84178.9466
84240.8029
84302.3316
84363.5325
84424.4054
84484.9502
84545.1665
84605.0543
84664.6133
84723.8433
84782.744
84841.3154
84899.5571
84957.469
85015.0508
85072.3025
85129.2236
85185.8141
85242.0737
85298.0023
85353.5995
85408.8653
85463.7995
85518.4018
85572.6721
85626.6102
85680.2159
85733.4891
85786.4295
85839.0369
85891.3114
85943.2531
85994.8623
86046.1393
86097.0846
86147.6985
86197.9813
86247.9335
86297.5556
86346.848
86395.8107
86444.4438
86492.7472
86540.7209
86588.3649
86635.6793
86682.6639
86729.3188
86775.6439
86821.6393
86867.305
86912.6409
86957.6472
87002.3238
87046.6708
87090.6882
87134.3762
87177.7346
87220.7635
87263.463
87305.8331
87347.8738
87389.5851
87430.967
87472.0195
87512.7426
87553.1363
87593.2007
87632.9356
87672.3412
87711.4174
87750.1643
87788.582
87826.6704
87864.4296
87901.8597
87938.9608
87975.7327
88012.1757
88048.2897
88084.0748
88119.531
88154.6582
88189.4564
88223.9257
88258.066
88291.8774
88325.3597
88358.5131
88391.3375
88423.8329
88455.9995
88487.8372
88519.3463
88550.5267
88581.3785
88611.9018
88642.0967
88671.9633
88701.5016
88730.7114
88759.5921
88788.1434
88816.3648
88844.2559
88871.8161
88899.045
88925.942
88952.5066
88978.7385
89004.6376
89030.2038
89055.4369
89080.337
89104.9038
89129.1372
89153.0372
89176.6037
89199.8365
89222.7356
89245.301
89267.5325
89289.4301
89310.9939
89332.2237
89353.1195
89373.6815
89393.9094
89413.8033
89433.3633
89452.5892
89471.4809
89490.0384
89508.2617
89526.1505
89543.705
89560.9249
89577.8102
89594.3608
89610.5768
89626.4579
89642.004
89657.2152
89672.0913
89686.6321
89700.8377
89714.7079
89728.2426
89741.4416
89754.305
89766.8327
89779.0244
89790.8802
89802.3999
89813.5835
89824.4307
89834.9417
89845.1162
89854.9541
89864.4554
89873.6199
89882.4476
89890.9383
89899.0919
89906.9083
89914.3874
89921.5291
89928.3332
89934.7997
89940.9284
89946.7193
89952.1721
89957.2868
89962.0633
89966.5015
89970.6012
89974.3623
89977.7848
89980.8684
89983.6132
89986.019
89988.0862
89989.8152
89991.2065
89992.2603
89992.9773
89993.3579
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4252
89993.4712
89993.6909
89994.0913
89994.6725
89995.4344
89996.3768
89997.4998
89998.8032
90000.2869
90001.951
90003.7952
90005.8197
90008.0242
90010.4088
90012.9733
90015.7177
90018.642
90021.746
90025.0298
90028.4931
90032.1361
90035.9585
90039.9604
90044.1418
90048.5024
90053.0423
90057.7613
90062.6594
90067.7366
90072.9927
90078.4277
90084.0414
90089.834
90095.8051
90101.9548
90108.283
90114.7895
90121.4744
90128.3374
90135.3785
90142.5976
90149.9945
90157.5693
90165.3218
90173.2519
90181.3595
90189.6446
90198.1069
90206.7465
90215.5631
90224.5568
90233.7274
90243.0748
90252.5989
90262.2995
90272.1767
90282.2302
90292.4599
90302.8658
90313.4476
90324.2054
90335.1389
90346.2481
90357.5328
90368.9929
90380.6283
90392.4388
90404.4245
90416.585
90428.9204
90441.4304
90454.1151
90466.9741
90480.0077
90493.216
90506.5994
90520.1585
90533.8935
90547.805
90561.8935
90576.1594
90590.6033
90605.2256
90620.0266
90635.0063
90650.1649
90665.5026
90681.0193
90696.7152
90712.5904
90728.645
90744.8792
90761.2929
90777.8865
90794.6598
90811.6131
90828.7465
90846.06
90863.5537
90881.2278
90899.0823
90917.1174
90935.3331
90953.7296
90972.3068
90991.0651
91010.0043
91029.1247
91048.4263
91067.9092
91087.5734
91107.4192
91127.4466
91147.6556
91168.0463
91188.6189
91209.3735
91230.31
91251.4287
91272.7295
91294.2126
91315.8781
91337.726
91359.7564
91381.9693
91404.365
91426.9434
91449.7047
91472.6488
91495.776
91519.0862
91542.5795
91566.2561
91590.1159
91614.1591
91638.3857
91662.7958
91687.3895
91712.1668
91737.1278
91762.2726
91787.6013
91813.1138
91838.8104
91864.691
91890.7558
91917.0048
91943.4381
91970.0559
91996.8582
92023.8451
92051.0166
92078.3729
92105.914
92133.6401
92161.5512
92189.6474
92217.9288
92246.3955
92275.0476
92303.8851
92332.9082
92362.1169
92391.5114
92421.0916
92450.8578
92480.81
92510.9482
92541.2727
92571.7834
92602.4805
92633.364
92664.434
92695.6908
92727.1342
92758.7644
92790.5816
92822.5858
92854.777
92887.1555
92919.7212
92952.4744
92985.415
93018.5431
93051.859
93085.3626
93119.054
93152.9334
93187.0008
93221.2564
93255.7002
93290.3324
93325.153
93360.1621
93395.3598
93430.7463
93466.3215
93502.0857
93538.0389
93574.1812
93610.5128
93647.0336
93683.7439
93720.6437
93757.733
93795.0121
93832.481
93870.1399
93907.9887
93946.0276
93984.2568
94022.6763
94061.2862
94100.0866
94139.0775
94178.2591
94217.6315
94257.1946
94296.9485
94336.8934
94377.0293
94417.3563
94457.8743
94498.5837
94539.4844
94580.5765
94621.8603
94663.3357
94705.0031
94746.8623
94788.9137
94831.1573
94873.5931
94916.221
94959.0405
95002.0512
95045.2528
95088.6447
95132.2266
95175.9979
95219.9581
95264.1068
95308.4436
95352.9684
95397.6812
95442.5819
95487.6704
95532.9465
95578.4103
95624.0615
95669.9002
95715.9262
95762.1395
95808.5399
95855.1274
95901.9019
95948.8634
95996.0117
96043.3468
96090.8687
96138.5771
96186.4722
96234.5537
96282.8216
96331.2759
96379.9164
96428.743
96477.7556
96526.9542
96576.3386
96625.9087
96675.6645
96725.6058
96775.7326
96826.0447
96876.542
96927.2244
96978.0918
97029.1441
97080.3812
97131.8029
97183.4092
97235.1999
97287.1749
97339.3341
97391.6774
97444.2047
97496.9158
97549.8107
97602.8892
97656.1511
97709.5965
97763.225
97817.0368
97871.0315
97925.209
97979.5694
98034.1124
98088.8378
98143.7457
98198.8358
98254.108
98309.5622
98365.1983
98421.0161
98477.0155
98533.1964
98589.5586
98646.102
98702.8265
98759.7319
98816.8182
98874.0851
98931.5326
98989.1612
99046.9711
99104.9628
99163.1366
99221.4931
99280.0326
99338.7557
99397.6629
99456.7547
99516.0312
99575.4926
99635.1389
99694.9703
99754.9868
99815.1886
99875.5757
99936.1483
99996.9064
100057.8501
100118.979
100180.2927
100241.7909
100303.473
100365.3386
100427.3871
100489.618
100552.0308
100614.6249
100677.3999
100740.3558
100803.4923
100866.8093
100930.3066
100993.9841
101057.8417
101121.8791
101186.0962
101250.4928
101315.0688
101379.8239
101444.7581
101509.8712
101575.163
101640.6333
101706.2819
101772.1088
101838.1136
101904.2963
101970.6567
102037.1946
102103.9099
102170.8023
102237.8716
102305.1178
102372.5406
102440.1399
102507.9155
102575.8671
102643.9947
102712.298
102780.7769
102849.4312
102918.2608
102987.2654
103056.4448
103125.799
103195.3276
103265.0307
103334.9079
103404.959
103475.1841
103545.5827
103616.1549
103686.9003
103757.8189
103828.9105
103900.1748
103971.6118
104043.2212
104115.0029
104186.9566
104259.0821
104331.3793
104403.8479
104476.4877
104549.2985
104622.2801
104695.4323
104768.7548
104842.2477
104915.9111
104989.7453
105063.7507
105137.9277
105212.2766
105286.7978
105361.4917
105436.3589
105511.3997
105586.6142
105662.0026
105737.5649
105813.3011
105889.2113
105965.2957
106041.5542
106117.9869
106194.594
106271.3754
106348.3313
106425.4617
106502.7667
106580.2464
106657.9009
106735.7302
106813.7344
106891.9135
106970.2678
107048.7972
107127.5018
107206.3817
107285.437
107364.6678
107444.074
107523.6559
107603.4135
107683.3467
107763.4559
107843.7409
107924.2019
108004.839
108085.6523
108166.6419
108247.8079
108329.1504
108410.6694
108492.3652
108574.2377
108656.2871
108738.5136
108820.9171
108903.4979
108986.2559
109069.1913
109152.3043
109235.5948
109319.0631
109402.7091
109486.5331
109570.5352
109654.7153
109739.0737
109823.6105
109908.3258
109993.2196
110078.2921
110163.5434
110248.9736
110334.5828
110420.3707
110506.337
110592.4812
110678.803
110765.3019
110851.9775
110938.8294
111025.8569
111113.0598
111200.4376
111287.9903
111375.7178
111463.62
111551.6968
111639.948
111728.3736
111816.9735
111905.7474
111994.6954
112083.8174
112173.1131
112262.5826
112352.2256
112442.0422
112532.0322
112622.1954
112712.5319
112803.0414
112893.7239
112984.5793
113075.6075
113166.8083
113258.1817
113349.7276
113441.4457
113533.3361
113625.3985
113717.633
113810.0393
113902.6174
113995.3671
114088.2884
114181.381
114274.6449
114368.08
114461.6861
114555.4631
114649.4109
114743.5293
114837.8182
114932.2775
115026.9071
115121.7068
115216.6765
115311.8161
115407.1254
115502.6043
115598.2527
115694.0704
115790.0573
115886.2133
115982.5382
116079.0319
116175.6943
116272.5252
116369.5245
116466.692
116564.0276
116661.5312
116759.2027
116857.0418
116955.0484
117053.2225
117151.5638
117250.0723
117348.7477
117447.5899
117546.5988
117645.7743
117745.1162
117844.6244
117944.2993
118044.1412
118144.1506
118244.3278
118344.6733
118445.1875
118545.8709
118646.724
118747.7473
118848.941
118950.3051
119051.8397
119153.545
119255.4209
119357.4677
119459.6854
119562.074
119664.6337
119767.3644
119870.2659
119973.3377
120076.5795
120179.9906
120283.5707
120387.3192
120491.2356
120595.3192
120699.5696
120803.9864
120908.5694
121013.3184
121118.2334
121223.3141
121328.5604
121433.9721
121539.549
121645.291
121751.1979
121857.2695
121963.5056
122069.9061
122176.4708
122283.1995
122390.092
122497.1483
122604.368
122711.7511
122819.2973
122927.0064
123034.8783
123142.9129
123251.1099
123359.4691
123467.9904
123576.6735
123685.5184
123794.5248
123903.6925
124013.0214
124122.5112
124232.1618
124341.973
124451.9446
124562.0764
124672.3683
124782.8199
124893.4313
125004.2021
125115.1322
125226.2213
125337.4694
125448.8761
125560.4413
125672.1649
125784.0466
125896.0862
126008.2835
126120.6383
126233.1505
126345.8198
126458.6461
126571.6292
126684.769
126798.0651
126911.5176
127025.1262
127138.8907
127252.8109
127366.8867
127481.1181
127595.5052
127710.0484
127824.7481
127939.6045
128054.6181
128169.7894
128285.1186
128400.6064
128516.2531
128632.0588
128748.0235
128864.1472
128980.43
129096.8718
129213.4727
129330.2327
129447.1517
129564.2298
129681.4669
129798.8631
129916.4184
130034.1329
130152.0067
130270.0397
130388.232
130506.5837
130625.0947
130743.7653
130862.5953
130981.5848
131100.7339
131220.0426
131339.5107
131459.1385
131578.9259
131698.8728
131818.9794
131939.2456
132059.6714
132180.2569
132301.0021
132421.9071
132542.9719
132664.1965
132785.5811
132907.1257
133028.8304
133150.6951
133272.72
133394.9052
133517.2506
133639.7563
133762.4225
133885.2491
134008.2363
134131.384
134254.6925
134378.1617
134501.7917
134625.5826
134749.5344
134873.6473
134997.9213
135122.3565
135246.953
135371.7108
135496.63
135621.7107
135746.953
135872.3564
135997.9206
136123.6452
136249.5297
136375.5735
136501.7762
136628.1373
136754.6561
136881.3322
137008.1651
137135.1549
137262.3013
137389.6041
137517.0633
137644.6787
137772.4502
137900.3775
138028.4607
138156.6994