## Large ASHP
Refrigerant |  | R32
Data source |  | tlk-energy.de pressure-enthalpy
T0 | K | 273
|  | Hot Sink ASHP |  |  | Cold Sink ASHP
|  | Winter | Spring/Autumn | Summer | Winter | Spring/Autumn | Summer
Rating condition |  | A7W20 | A15.3W20 | A23W20* | A7W10 | A15.3W10* | A23W10*
Compressor Efficiency |  | 80% | 80% | 80% | 80% | 80% | 80% | Add source
Superheating | K | 6 | 6 | 6 | 6 | 6 | 6
Subcooling | K | 5 | 5 | 5 | 5 | 5 | 5
CoP |  | 6.4 | 8 | 9.6* | 7.2 | 8.9* | 10.7*
COPcarnot |  | 14.1905 | 23.4646 | 59.6
* Ambient temp > sink temp. HP operation replaced with heat exchanger
Sink demand | kW
Compressor Power 1-2 | kW
Condenser temp | ºC | 25 | 25 | 25 | 15 | 15 | 15
Evaporator temp | ºC | 4 | 12.3 | 20 | 4 | 12.3 | 20
h1 | kJ/kg | 523.4 | 524.9 | 525.6 | 523.4 | 524.9 | Air temperature higher than condenser temperature
h2,act | kJ/kg | 553.9 | 542.3 | 532.1 | 539.6 | 528.6
h2 | kJ/kg
h3 | kJ/kg | 236.1 | 236.1 | 236.1 | 217.1 | 217.1
h4 | kJ/kg | 236.1 | 236.1 | 236.1 | 217.7 | 217.7
s1 | J/kg.K | 2166.6 | 2138.2 | 2112.3 | 2166.6 | 2138.2
s2,act | J/kg.K | 2185.4 | 2149.2 | 2116.5 | 2177.2 | 2140.7
s2 | J/kg.K
s3 | J/kg.K | 1124.3 | 1124.3 | 1124.3 | 1062.1 | 1062.1
s4 | J/kg.K | 1129.9 | 1126.7 | 1125.1 | 1063.8 | 1062.5
Refrigerant mass flow | kg/s | 0 | 0 | 0
Exergy Destruction over 4-week (672 h) period
Expansion Valve | kWh | 104.8727 | 0 |  | 274.7886
Compressor | kWh | 352.0728 | 0 |  | 1713.3877 |  |  |  | ›
Condenser | kWh | 100.0589 | -17.7514 |  | 758.3626
Evaporator | kWh | 0 | 0 |  | 0 | Air term ignored
Total | kWh | 557.0044 | -17.7514 |  | 2746.5389
| Winter |  | Spring/autumn
| Hot | Cold | Hot | Cold
Expansion Valve | 18.83% | 10% | 0 | 10%
Compressor | 63.21% | 62.38% | 0 | 62.38%
Condenser | 17.96% | 27.61% | 0 | 27.61%
| 100% | 100% | 0% | 100%

## Refrig Mass Flow & Cond kW
|  | Winter |  |  |  | Spring/Autumn |  |  |  | Summer
|  | Hot Sink ASHP |  | Cold Sink ASHP |  | Hot Sink ASHP |  | Cold Sink ASHP |  | Hot Sink ASHP |  | Cold Sink ASHP
| Rating Condition | A7W20 |  | A7W10 |  | A15.3W20 |  | A15.3W10* |  | A23W20* |  | A23W10*
h2 | kJ/kg |  | 553.9 |  | 539.6 |  | 542.3
h3 | kJ/kg |  | 236.1 |  | 217.1 |  | 236.1
|  | Qcond, h | mrefrig, hot | Qcond, c | mrefrig, cold | Qcond, h | mrefrig, hot | Qcond, c | mrefrig, cold | Qcond, h | mrefrig, hot | Qcond, c | mrefrig, cold
| Total (kWh/kgs) | 21800.4679 | 68.5981 | 190948.7608 | 592.0892 | 0 | 0 | 112313.7666 | 0 | 0 | 0 | 23697.0215 | 0
| Hours | kW | kg/s | kW | kg/s | kW | kg/s | kW | kg/s | kW | kg/s | kW | kg/s
| 1 | 0 | 0 | 0.9998 | 0.0031001 | 0 | 0 | 0.9998 |  | 0 |  | 0.9998
| 2 | 0 | 0 | 0.9995 | 0.0030992 | 0 | 0 | 0.9995 |  | 0 |  | 0.9995
| 3 | 0 | 0 | 0.99911 | 0.003098 | 0 | 0 | 0.99911 |  | 0 |  | 0.99911
| 4 | 0 | 0 | 0.99863 | 0.0030965 | 0 | 0 | 0.99863 |  | 0 |  | 0.99863
| 5 | 0 | 0 | 0.99806 | 0.0030948 | 0 | 0 | 0.99806 |  | 0 |  | 0.99806
| 6 | 0 | 0 | 0.9974 | 0.0030927 | 0 | 0 | 0.9974 |  | 0 |  | 0.99674
| 7 | 0 | 0 | 1.206 | 0.0037397 | 0 | 0 | 1.1882 |  | 0 |  | 1.0256
| 8 | 0 | 0 | 1.531 | 0.0047473 | 0 | 0 | 1.4768 |  | 0 |  | 1.0899
| 9 | 0 | 0 | 1.9276 | 0.0059771 | 0 | 0 | 1.7779 |  | 0 |  | 1.0575
| 10 | 0 | 0 | 2.1486 | 0.0066624 | 0 | 0 | 1.8772 |  | 0 |  | 0.86266
| 11 | 0 | 0 | 2.2934 | 0.0071114 | 0 | 0 | 1.867 |  | 0 |  | 0.52476
| 12 | 0 | 0 | 2.341 | 0.007259 | 0 | 0 | 1.7248 |  | 0 |  | 0.019681
| 13 | 0 | 0 | 2.2704 | 0.00704 | 0 | 0 | 1.4279 |  | 0 |  | 0
| 14 | 0 | 0 | 2.0606 | 0.0063894 | 0 | 0 | 0.95389 |  | 0 |  | 0
| 15 | 0 | 0 | 1.7258 | 0.0053513 | 0 | 0 | 0.31791 |  | 0 |  | 0
| 16 | 0 | 0 | 1.4802 | 0.0045898 | 0 | 0 | 0 |  | 0 |  | 0
| 17 | 0 | 0 | 1.1457 | 0.0035525 | 0 | 0 | 0 |  | 0 |  | 0
| 18 | 0 | 0 | 0.69436 | 0.002153 | 0 | 0 | 0 |  | 0 |  | 0
| 19 | 0 | 0 | 0.15245 | 0.00047271 | 0 | 0 | 0 |  | 0 |  | 0
| 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 112 | 239.9188 | 0.75494 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 113 | 246.1993 | 0.7747 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 114 | 252.4716 | 0.79444 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 115 | 258.736 | 0.81415 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 116 | 264.9926 | 0.83383 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 117 | 271.2415 | 0.8535 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 118 | 277.5179 | 0.87325 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 119 | 276.1567 | 0.86896 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 120 | 269.6083 | 0.84836 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 121 | 264.0994 | 0.83102 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 122 | 259.1079 | 0.81532 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 123 | 253.9123 | 0.79897 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 124 | 248.3137 | 0.78135 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 125 | 242.3117 | 0.76247 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 126 | 235.9065 | 0.74231 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 127 | 235.336 | 0.74052 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 128 | 242.768 | 0.7639 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 129 | 241.4058 | 0.75962 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 130 | 233.3957 | 0.73441 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 131 | 225.1078 | 0.70833 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 132 | 609.0746 | 1.9165 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 133 | 600.9451 | 1.891 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 134 | 592.8301 | 1.8654 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 135 | 584.7295 | 1.8399 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 143 | 0 | 0 | 14.1068 | 0.043742 | 0 | 0 | 0 |  | 0 |  | 0
| 144 | 0 | 0 | 33.3296 | 0.10335 | 0 | 0 | 0 |  | 0 |  | 0
| 145 | 0 | 0 | 52.5462 | 0.16293 | 0 | 0 | 0 |  | 0 |  | 0
| 146 | 0 | 0 | 71.755 | 0.2225 | 0 | 0 | 0 |  | 0 |  | 0
| 147 | 0 | 0 | 90.9542 | 0.28203 | 0 | 0 | 0 |  | 0 |  | 0
| 148 | 0 | 0 | 110.142 | 0.34153 | 0 | 0 | 0 |  | 0 |  | 0
| 149 | 0 | 0 | 129.3166 | 0.40098 | 0 | 0 | 0 |  | 0 |  | 0
| 150 | 0 | 0 | 148.4763 | 0.46039 | 0 | 0 | 0 |  | 0 |  | 0
| 151 | 0 | 0 | 167.8192 | 0.52037 | 0 | 0 | 0 |  | 0 |  | 0
| 152 | 0 | 0 | 187.2537 | 0.58063 | 0 | 0 | 0 |  | 0 |  | 0
| 153 | 0 | 0 | 206.753 | 0.64109 | 0 | 0 | 0 |  | 0 |  | 0
| 154 | 0 | 0 | 226.1151 | 0.70113 | 0 | 0 | 0 |  | 0 |  | 0
| 155 | 0 | 0 | 245.4534 | 0.7611 | 0 | 0 | 0 |  | 0 |  | 0
| 156 | 0 | 0 | 264.7579 | 0.82095 | 0 | 0 | 0 |  | 0 |  | 0
| 157 | 0 | 0 | 284.0002 | 0.88062 | 0 | 0 | 0 |  | 0 |  | 0
| 158 | 0 | 0 | 303.1638 | 0.94004 | 0 | 0 | 0 |  | 0 |  | 0
| 159 | 0 | 0 | 322.261 | 0.99926 | 0 | 0 | 0 |  | 0 |  | 0
| 160 | 0 | 0 | 341.494 | 1.0589 | 0 | 0 | 0 |  | 0 |  | 0
| 161 | 0 | 0 | 360.6984 | 1.1184 | 0 | 0 | 0 |  | 0 |  | 0
| 162 | 0 | 0 | 379.8487 | 1.1778 | 0 | 0 | 0 |  | 0 |  | 0
| 163 | 0 | 0 | 398.9629 | 1.2371 | 0 | 0 | 0 |  | 0 |  | 0
| 164 | 0 | 0 | 418.0434 | 1.2963 | 0 | 0 | 0 |  | 0 |  | 0
| 165 | 168.0988 | 0.52895 | 437.1591 | 1.3555 | 0 | 0 | 0 |  | 0 |  | 0
| 166 | 174.593 | 0.54938 | 456.3383 | 1.415 | 0 | 0 | 0 |  | 0 |  | 0
| 167 | 172.7885 | 0.5437 | 475.5881 | 1.4747 | 0 | 0 | 0 |  | 0 |  | 0
| 168 | 165.4039 | 0.52047 | 494.681 | 1.5339 | 0 | 0 | 0 |  | 0 |  | 0
| 169 | 159.268 | 0.50116 | 513.7254 | 1.5929 | 0 | 0 | 0.90806 |  | 0 |  | 0
| 170 | 154.1722 | 0.48512 | 532.7198 | 1.6518 | 0 | 0 | 21.6204 |  | 0 |  | 0
| 171 | 149.0719 | 0.46907 | 551.6623 | 1.7106 | 0 | 0 | 42.3275 |  | 0 |  | 0
| 172 | 143.6187 | 0.45192 | 570.5513 | 1.7692 | 0 | 0 | 63.0274 |  | 0 |  | 0
| 173 | 137.5513 | 0.43282 | 589.3849 | 1.8276 | 0 | 0 | 83.7183 |  | 0 |  | 0
| 174 | 0 | 0 | 608.1616 | 1.8858 | 0 | 0 | 104.3832 |  | 0 |  | 0
| 175 | 0 | 0 | 627.0802 | 1.9444 | 0 | 0 | 125.1602 |  | 0 |  | 0
| 176 | 0 | 0 | 646.0491 | 2.0033 | 0 | 0 | 145.9613 |  | 0 |  | 0
| 177 | 0 | 0 | 665.0232 | 2.0621 | 0 | 0 | 166.7189 |  | 0 |  | 0
| 178 | 0 | 0 | 683.7623 | 2.1202 | 0 | 0 | 187.2274 |  | 0 |  | 0
| 179 | 0 | 0 | 702.3591 | 2.1779 | 0 | 0 | 207.5704 |  | 0 |  | 0
| 180 | 0 | 0 | 720.7909 | 2.235 | 0 | 0 | 227.7238 |  | 0 |  | 0
| 181 | 0 | 0 | 739.0349 | 2.2916 | 0 | 0 | 247.6633 |  | 0 |  | 0
| 182 | 0 | 0 | 757.0685 | 2.3475 | 0 | 0 | 267.3648 |  | 0 |  | 0
| 183 | 0 | 0 | 774.9042 | 2.4028 | 0 | 0 | 286.8419 |  | 0 |  | 0
| 184 | 0 | 0 | 792.7474 | 2.4581 | 0 | 0 | 306.2808 |  | 0 |  | 0
| 185 | 0 | 0 | 810.4207 | 2.5129 | 0 | 0 | 325.5227 |  | 0 |  | 0
| 186 | 0 | 0 | 827.8957 | 2.5671 | 0 | 0 | 344.5283 |  | 0 |  | 0
| 187 | 0 | 0 | 845.197 | 2.6208 | 0 | 0 | 363.3237 |  | 0 |  | 0
| 188 | 0 | 0 | 862.3245 | 2.6739 | 0 | 0 | 381.9082 |  | 0 |  | 0
| 189 | 0 | 0 | 879.2725 | 2.7264 | 0 | 0 | 400.2752 |  | 0 |  | 0
| 190 | 0 | 0 | 896.0645 | 2.7785 | 0 | 0 | 418.4494 |  | 0 |  | 0
| 191 | 0 | 0 | 912.8298 | 2.8305 | 0 | 0 | 436.5595 |  | 0 |  | 0
| 192 | 0 | 0 | 929.4269 | 2.8819 | 0 | 0 | 454.49 |  | 0 |  | 0
| 193 | 0 | 0 | 945.9973 | 2.9333 | 0 | 0 | 472.464 |  | 0 |  | 0
| 194 | 0 | 0 | 962.4796 | 2.9844 | 0 | 0 | 490.4281 |  | 0 |  | 0
| 195 | 0 | 0 | 978.871 | 3.0353 | 0 | 0 | 508.3445 |  | 0 |  | 0
| 196 | 0 | 0 | 995.17 | 3.0858 | 0 | 0 | 526.2114 |  | 0 |  | 0
| 197 | 0 | 0 | 1011.3753 | 3.136 | 0 | 0 | 544.0272 |  | 0 |  | 0
| 198 | 0 | 0 | 1027.4853 | 3.186 | 0 | 0 | 561.7857 |  | 0 |  | 0
| 199 | 0 | 0 | 1043.7057 | 3.2363 | 0 | 0 | 579.6376 |  | 0 |  | 0
| 200 | 0 | 0 | 1059.9433 | 3.2866 | 0 | 0 | 597.495 |  | 0 |  | 0
| 201 | 0 | 0 | 1076.1694 | 3.337 | 0 | 0 | 615.2899 |  | 0 |  | 0
| 202 | 0 | 0 | 1092.1552 | 3.3865 | 0 | 0 | 632.8141 |  | 0 |  | 0
| 203 | 0 | 0 | 1107.9889 | 3.4356 | 0 | 0 | 650.1588 |  | 0 |  | 0
| 204 | 0 | 0 | 1123.6509 | 3.4842 | 0 | 0 | 667.303 |  | 0 |  | 0
| 205 | 0 | 0 | 1139.1219 | 3.5322 | 0 | 0 | 684.2262 |  | 0 |  | 0
| 206 | 0 | 0 | 1154.3823 | 3.5795 | 0 | 0 | 700.9076 |  | 0 |  | 0
| 207 | 0 | 0 | 1080.5863 | 3.3507 | 0 | 0 | 717.3265 |  | 0 |  | 0
| 208 | 0 | 0 | 1049.6245 | 3.2546 | 0 | 0 | 733.652 |  | 0 |  | 0
| 209 | 0 | 0 | 1018.5653 | 3.1583 | 0 | 0 | 749.8346 |  | 0 |  | 0
| 210 | 0 | 0 | 987.3924 | 3.0617 | 0 | 0 | 765.843 |  | 0 |  | 0
| 211 | 0 | 0 | 956.0538 | 2.9645 | 0 | 0 | 781.6163 |  | 0 |  | 0
| 212 | 0 | 0 | 924.5401 | 2.8668 | 0 | 0 | 797.1395 |  | 0 |  | 0
| 213 | 0 | 0 | 892.823 | 2.7684 | 0 | 0 | 812.377 |  | 0 |  | 0
| 214 | 0 | 0 | 860.9588 | 2.6696 | 0 | 0 | 827.3847 |  | 0 |  | 0
| 215 | 0 | 0 | 829.0804 | 2.5708 | 0 | 0 | 842.2893 |  | 0 |  | 0
| 216 | 0 | 0 | 797.0439 | 2.4715 | 0 | 0 | 856.9696 |  | 0 |  | 0
| 217 | 0 | 0 | 765.0016 | 2.3721 | 0 | 0 | 871.6561 |  | 0 |  | 0
| 218 | 0 | 0 | 732.8956 | 2.2725 | 0 | 0 | 886.3001 |  | 0 |  | 0
| 219 | 0 | 0 | 700.7276 | 2.1728 | 0 | 0 | 900.8605 |  | 0 |  | 0
| 220 | 0 | 0 | 668.5005 | 2.0729 | 0 | 0 | 915.3361 |  | 0 |  | 0
| 221 | 0 | 0 | 636.2172 | 1.9728 | 0 | 0 | 929.7255 |  | 0 |  | 0
| 222 | 0 | 0 | 603.8808 | 1.8725 | 0 | 0 | 944.0088 |  | 0 |  | 0
| 223 | 0 | 0 | 571.7073 | 1.7727 | 0 | 0 | 958.3423 |  | 0 |  | 0
| 224 | 0 | 0 | 539.6061 | 1.6732 | 0 | 0 | 972.6406 |  | 0 |  | 0
| 225 | 0 | 0 | 507.5443 | 1.5738 | 0 | 0 | 986.8298 |  | 0 |  | 0
| 226 | 0 | 0 | 475.2749 | 1.4737 | 0 | 0 | 1000.6939 |  | 0 |  | 0
| 227 | 0 | 0 | 442.9023 | 1.3733 | 0 | 0 | 1014.3276 |  | 0 |  | 1.2624
| 228 | 0 | 0 | 410.4101 | 1.2726 | 0 | 0 | 925.0949 |  | 0 |  | 20.7473
| 229 | 0 | 0 | 377.7818 | 1.1714 | 0 | 0 | 892.255 |  | 0 |  | 39.9873
| 230 | 0 | 0 | 345.001 | 1.0698 | 0 | 0 | 859.1402 |  | 0 |  | 58.9588
| 231 | 0 | 0 | 312.0513 | 0.9676 | 0 | 0 | 825.7328 |  | 0 |  | 77.6383
| 232 | 0 | 0 | 279.1648 | 0.86563 | 0 | 0 | 792.2486 |  | 0 |  | 96.1053
| 233 | 0 | 0 | 246.2491 | 0.76356 | 0 | 0 | 758.6239 |  | 0 |  | 114.3962
| 234 | 0 | 0 | 213.2432 | 0.66122 | 0 | 0 | 724.7819 |  | 0 |  | 132.4066
| 235 | 0 | 0 | 180.104 | 0.55846 | 0 | 0 | 690.6756 |  | 0 |  | 150.0807
| 236 | 0 | 0 | 146.8218 | 0.45526 | 0 | 0 | 656.2941 |  | 0 |  | 167.4009
| 237 | 0 | 0 | 113.4049 | 0.35164 | 0 | 0 | 621.6458 |  | 0 |  | 184.3706
| 238 | 0 | 0 | 79.9121 | 0.24779 | 0 | 0 | 586.7935 |  | 0 |  | 201.0515
| 239 | 0 | 0 | 46.4708 | 0.1441 | 0 | 0 | 551.8604 |  | 0 |  | 217.5383
| 240 | 0 | 0 | 12.9363 | 0.040112 | 0 | 0 | 516.7252 |  | 0 |  | 233.8694
| 241 | 0 | 0 | 0 | 0 | 0 | 0 | 481.6372 |  | 0 |  | 250.2366
| 242 | 0 | 0 | 0 | 0 | 0 | 0 | 446.5572 |  | 0 |  | 266.6832
| 243 | 0 | 0 | 0 | 0 | 0 | 0 | 411.4418 |  | 0 |  | 283.1028
| 244 | 0 | 0 | 0 | 0 | 0 | 0 | 376.2943 |  | 0 |  | 299.4729
| 245 | 0 | 0 | 0 | 0 | 0 | 0 | 341.1179 |  | 0 |  | 315.7514
| 246 | 0 | 0 | 0 | 0 | 0 | 0 | 305.8958 |  | 0 |  | 331.9051
| 247 | 0 | 0 | 0 | 0 | 0 | 0 | 270.7984 |  | 0 |  | 347.9832
| 248 | 0 | 0 | 0 | 0 | 0 | 0 | 235.7453 |  | 0 |  | 364.0047
| 249 | 0 | 0 | 0 | 0 | 0 | 0 | 200.6936 |  | 0 |  | 379.9034
| 250 | 0 | 0 | 0 | 0 | 0 | 0 | 165.6272 |  | 0 |  | 395.6569
| 251 | 0 | 0 | 0 | 0 | 0 | 0 | 130.5302 |  | 0 |  | 411.2426
| 252 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3865 |  | 0 |  | 426.6381
| 253 | 0 | 0 | 0 | 0 | 0 | 0 | 60.1802 |  | 0 |  | 441.821
| 254 | 0 | 0 | 0 | 0 | 0 | 0 | 24.8953 |  | 0 |  | 363.3463
| 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 332.1235
| 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 300.6869
| 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 268.9661
| 258 | 28.0569 | 0.088285 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 236.9273
| 259 | 34.6867 | 0.10915 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 204.619
| 260 | 41.3045 | 0.12997 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 172.1431
| 261 | 47.9115 | 0.15076 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 139.5456
| 262 | 54.5094 | 0.17152 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 106.8725
| 263 | 52.8258 | 0.16622 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 74.1056
| 264 | 46.1092 | 0.14509 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 41.2734
| 265 | 40.6501 | 0.12791 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 8.4855
| 266 | 35.8828 | 0.11291 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 267 | 31.111 | 0.097895 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 268 | 25.9863 | 0.081769 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 269 | 20.3662 | 0.064085 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 270 | 14.2029 | 0.044691 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 271 | 13.7175 | 0.043164 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 272 | 21.1715 | 0.066619 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 273 | 28.1889 | 0.0887 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 274 | 34.8843 | 0.10977 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 275 | 41.5573 | 0.13077 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 276 | 48.2229 | 0.15174 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 277 | 54.8805 | 0.17269 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 278 | 61.5295 | 0.19361 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 279 | 68.1702 | 0.21451 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 280 | 74.8027 | 0.23538 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 281 | 81.4273 | 0.25622 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 282 | 88.0441 | 0.27704 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 283 | 94.6535 | 0.29784 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 284 | 101.2557 | 0.31861 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 285 | 107.8506 | 0.33937 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 286 | 114.4666 | 0.36018 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 287 | 113.4287 | 0.35692 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 288 | 107.229 | 0.33741 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 289 | 102.069 | 0.32117 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 290 | 97.4265 | 0.30657 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 291 | 92.5802 | 0.29132 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 292 | 87.331 | 0.2748 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 293 | 81.6787 | 0.25701 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 294 | 75.6234 | 0.23796 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 295 | 75.3861 | 0.23721 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 296 | 83.1495 | 0.26164 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 297 | 82.1226 | 0.25841 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 298 | 74.4631 | 0.23431 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 299 | 458.7763 | 1.4436 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 300 | 450.9998 | 1.4191 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 301 | 443.237 | 1.3947 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 302 | 435.488 | 1.3703 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 310 | 73.2256 | 0.23041 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 311 | 73.3408 | 0.23078 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 312 | 68.1344 | 0.21439 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 313 | 63.2716 | 0.19909 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 314 | 58.5784 | 0.18432 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 315 | 53.7067 | 0.169 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 316 | 48.4823 | 0.15256 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 317 | 42.9049 | 0.13501 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 330 | 0 | 0 | 14.2967 | 0.044331 | 0 | 0 | 0 |  | 0 |  | 0
| 331 | 0 | 0 | 34.0781 | 0.10567 | 0 | 0 | 0 |  | 0 |  | 0
| 332 | 0 | 0 | 53.8551 | 0.16699 | 0 | 0 | 0 |  | 0 |  | 0
| 333 | 0 | 0 | 73.6965 | 0.22852 | 0 | 0 | 0 |  | 0 |  | 0
| 334 | 0 | 0 | 93.6309 | 0.29033 | 0 | 0 | 0 |  | 0 |  | 0
| 335 | 0 | 0 | 113.6682 | 0.35246 | 0 | 0 | 0 |  | 0 |  | 0
| 336 | 0 | 0 | 133.5849 | 0.41422 | 0 | 0 | 0 |  | 0 |  | 0
| 337 | 0 | 0 | 153.4862 | 0.47593 | 0 | 0 | 0 |  | 0 |  | 0
| 338 | 0 | 0 | 173.3702 | 0.53758 | 0 | 0 | 0 |  | 0 |  | 0
| 339 | 0 | 0 | 193.2352 | 0.59918 | 0 | 0 | 0 |  | 0 |  | 0
| 340 | 0 | 0 | 213.0793 | 0.66071 | 0 | 0 | 0 |  | 0 |  | 0
| 341 | 0 | 0 | 232.9008 | 0.72217 | 0 | 0 | 0 |  | 0 |  | 0
| 342 | 0 | 0 | 252.6977 | 0.78356 | 0 | 0 | 0 |  | 0 |  | 0
| 343 | 0 | 0 | 272.6666 | 0.84548 | 0 | 0 | 0 |  | 0 |  | 0
| 344 | 0 | 0 | 292.7163 | 0.90765 | 0 | 0 | 0 |  | 0 |  | 0
| 345 | 0 | 0 | 312.7995 | 0.96992 | 0 | 0 | 0 |  | 0 |  | 0
| 346 | 0 | 0 | 332.68 | 1.0316 | 0 | 0 | 0 |  | 0 |  | 0
| 347 | 0 | 0 | 352.449 | 1.0929 | 0 | 0 | 0 |  | 0 |  | 0
| 348 | 0 | 0 | 372.0836 | 1.1537 | 0 | 0 | 0 |  | 0 |  | 0
| 349 | 0 | 0 | 391.5611 | 1.2141 | 0 | 0 | 0 |  | 0 |  | 0
| 350 | 0 | 0 | 410.8587 | 1.274 | 0 | 0 | 0 |  | 0 |  | 0
| 351 | 0 | 0 | 429.9889 | 1.3333 | 0 | 0 | 0 |  | 0 |  | 0
| 352 | 0 | 0 | 449.1536 | 1.3927 | 0 | 0 | 0 |  | 0 |  | 0
| 353 | 0 | 0 | 468.1766 | 1.4517 | 0 | 0 | 0 |  | 0 |  | 0
| 354 | 0 | 0 | 487.0295 | 1.5102 | 0 | 0 | 0 |  | 0 |  | 0
| 355 | 0 | 0 | 505.737 | 1.5682 | 0 | 0 | 0 |  | 0 |  | 0
| 356 | 0 | 0 | 524.2987 | 1.6257 | 0 | 0 | 0 |  | 0 |  | 0
| 357 | 0 | 0 | 542.7088 | 1.6828 | 0 | 0 | 0 |  | 0 |  | 0
| 358 | 0 | 0 | 560.9906 | 1.7395 | 0 | 0 | 0 |  | 0 |  | 0
| 359 | 0 | 0 | 579.2736 | 1.7962 | 0 | 0 | 0 |  | 0 |  | 0
| 360 | 0 | 0 | 597.4201 | 1.8525 | 0 | 0 | 0 |  | 0 |  | 0
| 361 | 0 | 0 | 615.5709 | 1.9087 | 0 | 0 | 0 |  | 0 |  | 0
| 362 | 0 | 0 | 633.6637 | 1.9648 | 0 | 0 | 0 |  | 0 |  | 0
| 363 | 0 | 0 | 651.6956 | 2.0208 | 0 | 0 | 0 |  | 0 |  | 0
| 364 | 0 | 0 | 669.6649 | 2.0765 | 0 | 0 | 0 |  | 0 |  | 0
| 365 | 0 | 0 | 687.57 | 2.132 | 0 | 0 | 0 |  | 0 |  | 0
| 366 | 0 | 0 | 705.4092 | 2.1873 | 0 | 0 | 0 |  | 0 |  | 0
| 367 | 0 | 0 | 723.3838 | 2.2431 | 0 | 0 | 0 |  | 0 |  | 0
| 368 | 0 | 0 | 741.4018 | 2.2989 | 0 | 0 | 0 |  | 0 |  | 0
| 369 | 0 | 0 | 759.4352 | 2.3548 | 0 | 0 | 0 |  | 0 |  | 0
| 370 | 0 | 0 | 777.2564 | 2.4101 | 0 | 0 | 0 |  | 0 |  | 0
| 371 | 0 | 0 | 794.9524 | 2.465 | 0 | 0 | 0 |  | 0 |  | 0
| 372 | 0 | 0 | 812.5035 | 2.5194 | 0 | 0 | 0 |  | 0 |  | 0
| 373 | 0 | 0 | 829.89 | 2.5733 | 0 | 0 | 0 |  | 0 |  | 0
| 374 | 0 | 0 | 847.0924 | 2.6266 | 0 | 0 | 0 |  | 0 |  | 0
| 375 | 0 | 0 | 864.0908 | 2.6794 | 0 | 0 | 0 |  | 0 |  | 0
| 376 | 0 | 0 | 881.071 | 2.732 | 0 | 0 | 0 |  | 0 |  | 0
| 377 | 0 | 0 | 897.9568 | 2.7844 | 0 | 0 | 0 |  | 0 |  | 0
| 378 | 0 | 0 | 914.7282 | 2.8364 | 0 | 0 | 0 |  | 0 |  | 0
| 379 | 0 | 0 | 931.3288 | 2.8878 | 0 | 0 | 0 |  | 0 |  | 0
| 380 | 0 | 0 | 947.745 | 2.9387 | 0 | 0 | 0 |  | 0 |  | 0
| 381 | 0 | 0 | 963.9439 | 2.989 | 0 | 0 | 0 |  | 0 |  | 0
| 382 | 0 | 0 | 979.9777 | 3.0387 | 0 | 0 | 0 |  | 0 |  | 0
| 383 | 0 | 0 | 995.9755 | 3.0883 | 0 | 0 | 0 |  | 0 |  | 0
| 384 | 0 | 0 | 1011.7939 | 3.1373 | 0 | 0 | 0 |  | 0 |  | 0
| 385 | 0 | 0 | 1027.5806 | 3.1863 | 0 | 0 | 0 |  | 0 |  | 0
| 386 | 0 | 0 | 1043.2722 | 3.235 | 0 | 0 | 0 |  | 0 |  | 0
| 387 | 0 | 0 | 1058.8656 | 3.2833 | 0 | 0 | 0 |  | 0 |  | 0
| 388 | 0 | 0 | 1074.3596 | 3.3313 | 0 | 0 | 0 |  | 0 |  | 0
| 389 | 0 | 0 | 1089.7526 | 3.3791 | 0 | 0 | 0 |  | 0 |  | 0
| 390 | 0 | 0 | 1105.0433 | 3.4265 | 0 | 0 | 0 |  | 0 |  | 0
| 391 | 0 | 0 | 1120.4394 | 3.4742 | 0 | 0 | 0 |  | 0 |  | 0
| 392 | 0 | 0 | 1135.8472 | 3.522 | 0 | 0 | 0 |  | 0 |  | 0
| 393 | 0 | 0 | 1151.2293 | 3.5697 | 0 | 0 | 0 |  | 0 |  | 0
| 394 | 0 | 0 | 1166.3381 | 3.6166 | 0 | 0 | 0 |  | 0 |  | 0
| 395 | 0 | 0 | 1181.2717 | 3.6629 | 0 | 0 | 0 |  | 0 |  | 0
| 396 | 0 | 0 | 1196.0096 | 3.7086 | 0 | 0 | 0 |  | 0 |  | 0
| 397 | 0 | 0 | 1210.531 | 3.7536 | 0 | 0 | 0 |  | 0 |  | 0
| 398 | 0 | 0 | 1224.8152 | 3.7979 | 0 | 0 | 0 |  | 0 |  | 0
| 399 | 0 | 0 | 1238.8414 | 3.8414 | 0 | 0 | 0 |  | 0 |  | 0
| 400 | 0 | 0 | 1252.835 | 3.8848 | 0 | 0 | 0 |  | 0 |  | 0
| 401 | 0 | 0 | 1266.7002 | 3.9278 | 0 | 0 | 0 |  | 0 |  | 0
| 402 | 0 | 0 | 1280.3721 | 3.9701 | 0 | 0 | 0 |  | 0 |  | 0
| 403 | 0 | 0 | 1186.594 | 3.6794 | 0 | 0 | 0 |  | 0 |  | 0
| 404 | 0 | 0 | 1153.8257 | 3.5778 | 0 | 0 | 0 |  | 0 |  | 0
| 405 | 0 | 0 | 1120.8284 | 3.4754 | 0 | 0 | 0 |  | 0 |  | 0
| 406 | 0 | 0 | 1087.6611 | 3.3726 | 0 | 0 | 0 |  | 0 |  | 0
| 407 | 0 | 0 | 1054.4514 | 3.2696 | 0 | 0 | 0 |  | 0 |  | 0
| 408 | 0 | 0 | 1021.0553 | 3.1661 | 0 | 0 | 0 |  | 0 |  | 0
| 409 | 0 | 0 | 987.6422 | 3.0625 | 0 | 0 | 0 |  | 0 |  | 0
| 410 | 0 | 0 | 954.147 | 2.9586 | 0 | 0 | 0 |  | 0 |  | 0
| 411 | 0 | 0 | 920.5696 | 2.8545 | 0 | 0 | 0 |  | 0 |  | 0
| 412 | 0 | 0 | 886.9132 | 2.7501 | 0 | 0 | 0 |  | 0 |  | 0
| 413 | 0 | 0 | 853.1809 | 2.6455 | 0 | 0 | 0 |  | 0 |  | 0
| 414 | 0 | 0 | 819.3758 | 2.5407 | 0 | 0 | 0 |  | 0 |  | 0
| 415 | 0 | 0 | 785.7177 | 2.4363 | 0 | 0 | 0 |  | 0 |  | 0
| 416 | 0 | 0 | 752.115 | 2.3321 | 0 | 0 | 0 |  | 0 |  | 0
| 417 | 0 | 0 | 718.553 | 2.2281 | 0 | 0 | 0 |  | 0 |  | 0
| 418 | 0 | 0 | 685.0046 | 2.124 | 0 | 0 | 0 |  | 0 |  | 0
| 419 | 0 | 0 | 651.4511 | 2.02 | 0 | 0 | 0 |  | 0 |  | 0
| 420 | 0 | 0 | 617.8783 | 1.9159 | 0 | 0 | 0 |  | 0 |  | 0
| 421 | 0 | 0 | 584.2719 | 1.8117 | 0 | 0 | 0 |  | 0 |  | 0
| 422 | 0 | 0 | 550.6177 | 1.7073 | 0 | 0 | 0 |  | 0 |  | 0
| 423 | 0 | 0 | 516.9342 | 1.6029 | 0 | 0 | 0 |  | 0 |  | 0
| 424 | 0 | 0 | 483.2142 | 1.4983 | 0 | 0 | 0 |  | 0 |  | 0
| 425 | 0 | 0 | 449.3983 | 1.3935 | 0 | 0 | 17.9717 |  | 0 |  | 0
| 426 | 0 | 0 | 415.4586 | 1.2882 | 0 | 0 | 37.549 |  | 0 |  | 0
| 427 | 0 | 0 | 381.439 | 1.1828 | 0 | 0 | 56.9836 |  | 0 |  | 0
| 428 | 0 | 0 | 347.4288 | 1.0773 | 0 | 0 | 76.3667 |  | 0 |  | 0
| 429 | 0 | 0 | 313.4689 | 0.972 | 0 | 0 | 95.737 |  | 0 |  | 0
| 430 | 0 | 0 | 279.6003 | 0.86698 | 0 | 0 | 115.1335 |  | 0 |  | 0
| 431 | 0 | 0 | 245.8411 | 0.7623 | 0 | 0 | 134.5707 |  | 0 |  | 0
| 432 | 0 | 0 | 211.9478 | 0.6572 | 0 | 0 | 153.9231 |  | 0 |  | 0
| 433 | 0 | 0 | 178.0405 | 0.55206 | 0 | 0 | 173.2873 |  | 0 |  | 0
| 434 | 0 | 0 | 144.1222 | 0.44689 | 0 | 0 | 192.6324 |  | 0 |  | 0
| 435 | 0 | 0 | 110.1961 | 0.34169 | 0 | 0 | 211.9569 |  | 0 |  | 0
| 436 | 0 | 0 | 76.2653 | 0.23648 | 0 | 0 | 231.2588 |  | 0 |  | 0
| 437 | 0 | 0 | 42.3329 | 0.13126 | 0 | 0 | 250.5365 |  | 0 |  | 0
| 438 | 0 | 0 | 8.402 | 0.026053 | 0 | 0 | 269.7874 |  | 0 |  | 0
| 439 | 0 | 0 | 0 | 0 | 0 | 0 | 289.1667 |  | 0 |  | 0
| 440 | 0 | 0 | 0 | 0 | 0 | 0 | 308.5817 |  | 0 |  | 0
| 441 | 0 | 0 | 0 | 0 | 0 | 0 | 327.991 |  | 0 |  | 0
| 442 | 0 | 0 | 0 | 0 | 0 | 0 | 347.3746 |  | 0 |  | 0
| 443 | 0 | 0 | 0 | 0 | 0 | 0 | 366.7126 |  | 0 |  | 0
| 444 | 0 | 0 | 0 | 0 | 0 | 0 | 385.9851 |  | 0 |  | 0
| 445 | 0 | 0 | 0 | 0 | 0 | 0 | 405.1722 |  | 0 |  | 0
| 446 | 0 | 0 | 0 | 0 | 0 | 0 | 424.2819 |  | 0 |  | 0
| 447 | 0 | 0 | 0 | 0 | 0 | 0 | 443.3402 |  | 0 |  | 0
| 448 | 0 | 0 | 0 | 0 | 0 | 0 | 462.3542 |  | 0 |  | 0
| 449 | 0 | 0 | 0 | 0 | 0 | 0 | 481.3309 |  | 0 |  | 0
| 450 | 0 | 0 | 0 | 0 | 0 | 0 | 500.2776 |  | 0 |  | 0
| 451 | 0 | 0 | 0 | 0 | 0 | 0 | 519.2012 |  | 0 |  | 0
| 452 | 0 | 0 | 0 | 0 | 0 | 0 | 538.1087 |  | 0 |  | 0
| 453 | 0 | 0 | 0 | 0 | 0 | 0 | 556.9685 |  | 0 |  | 0
| 454 | 5.7651 | 0.018141 | 0 | 0 | 0 | 0 | 575.7992 |  | 0 |  | 0
| 455 | 4.8796 | 0.015354 | 0 | 0 | 0 | 0 | 594.6699 |  | 0 |  | 0
| 456 | 0 | 0 | 0 | 0 | 0 | 0 | 613.4132 |  | 0 |  | 0
| 457 | 0 | 0 | 0 | 0 | 0 | 0 | 632.0995 |  | 0 |  | 0
| 458 | 0 | 0 | 0 | 0 | 0 | 0 | 650.725 |  | 0 |  | 0
| 459 | 0 | 0 | 0 | 0 | 0 | 0 | 669.2879 |  | 0 |  | 0
| 460 | 0 | 0 | 0 | 0 | 0 | 0 | 687.7865 |  | 0 |  | 0
| 461 | 0 | 0 | 0 | 0 | 0 | 0 | 706.2191 |  | 0 |  | 0
| 462 | 0 | 0 | 0 | 0 | 0 | 0 | 724.584 |  | 0 |  | 0
| 463 | 0 | 0 | 0 | 0 | 0 | 0 | 743.0622 |  | 0 |  | 0
| 464 | 0 | 0 | 0 | 0 | 0 | 0 | 761.5585 |  | 0 |  | 0
| 465 | 0 | 0 | 0 | 0 | 0 | 0 | 780.0043 |  | 0 |  | 0
| 466 | 0 | 0 | 0 | 0 | 0 | 0 | 798.1949 |  | 0 |  | 0
| 467 | 352.9206 | 1.1105 | 0 | 0 | 0 | 0 | 816.2227 |  | 0 |  | 0
| 468 | 345.3932 | 1.0868 | 0 | 0 | 0 | 0 | 834.0692 |  | 0 |  | 0
| 469 | 337.8791 | 1.0632 | 0 | 0 | 0 | 0 | 851.7245 |  | 0 |  | 0
| 470 | 330.3783 | 1.0396 | 0 | 0 | 0 | 0 | 869.1929 |  | 0 |  | 0
| 471 | 0 | 0 | 0 | 0 | 0 | 0 | 886.4355 |  | 0 |  | 0
| 472 | 0 | 0 | 0 | 0 | 0 | 0 | 903.5933 |  | 0 |  | 0
| 473 | 0 | 0 | 0 | 0 | 0 | 0 | 920.6438 |  | 0 |  | 0
| 474 | 0 | 0 | 0 | 0 | 0 | 0 | 937.6147 |  | 0 |  | 0
| 475 | 0 | 0 | 0 | 0 | 0 | 0 | 954.5164 |  | 0 |  | 0
| 476 | 0 | 0 | 0 | 0 | 0 | 0 | 971.3756 |  | 0 |  | 0
| 477 | 0 | 0 | 0 | 0 | 0 | 0 | 988.2304 |  | 0 |  | 0
| 478 | 0 | 0 | 0 | 0 | 0 | 0 | 1005.0951 |  | 0 |  | 0
| 479 | 0 | 0 | 0 | 0 | 0 | 0 | 1021.9715 |  | 0 |  | 0
| 480 | 0 | 0 | 0 | 0 | 0 | 0 | 1038.6415 |  | 0 |  | 0
| 481 | 0 | 0 | 0 | 0 | 0 | 0 | 1055.2137 |  | 0 |  | 0
| 482 | 0 | 0 | 0 | 0 | 0 | 0 | 1071.6866 |  | 0 |  | 0
| 483 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.0586 |  | 0 |  | 0
| 484 | 0 | 0 | 0 | 0 | 0 | 0 | 1104.3283 |  | 0 |  | 0
| 485 | 0 | 0 | 0 | 0 | 0 | 0 | 1120.4942 |  | 0 |  | 0
| 486 | 0 | 0 | 0 | 0 | 0 | 0 | 1136.5548 |  | 0 |  | 0
| 487 | 0 | 0 | 0 | 0 | 0 | 0 | 1152.6992 |  | 0 |  | 0
| 488 | 0 | 0 | 0 | 0 | 0 | 0 | 1168.8547 |  | 0 |  | 0
| 489 | 0 | 0 | 0 | 0 | 0 | 0 | 1184.9429 |  | 0 |  | 0
| 490 | 0 | 0 | 0 | 0 | 0 | 0 | 1200.7559 |  | 0 |  | 0
| 491 | 0 | 0 | 0 | 0 | 0 | 0 | 1216.3915 |  | 0 |  | 0
| 492 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.8335 |  | 0 |  | 0
| 493 | 0 | 0 | 0 | 0 | 0 | 0 | 1247.0657 |  | 0 |  | 0
| 494 | 0 | 0 | 0 | 0 | 0 | 0 | 1173.2455 |  | 0 |  | 0
| 495 | 0 | 0 | 0 | 0 | 0 | 0 | 1142.0873 |  | 0 |  | 0
| 496 | 0 | 0 | 0 | 0 | 0 | 0 | 1110.933 |  | 0 |  | 0
| 497 | 0 | 0 | 0 | 0 | 0 | 0 | 1079.6416 |  | 0 |  | 0
| 498 | 0 | 0 | 0 | 0 | 0 | 0 | 1048.1789 |  | 0 |  | 0
| 499 | 0 | 0 | 0 | 0 | 0 | 0 | 1016.5689 |  | 0 |  | 0
| 500 | 0 | 0 | 0 | 0 | 0 | 0 | 984.8185 |  | 0 |  | 0
| 501 | 0 | 0 | 0 | 0 | 0 | 0 | 953.0064 |  | 0 |  | 0
| 502 | 0 | 0 | 0 | 0 | 0 | 0 | 921.1683 |  | 0 |  | 0
| 503 | 0 | 0 | 0 | 0 | 0 | 0 | 889.3116 |  | 0 |  | 0
| 504 | 0 | 0 | 0 | 0 | 0 | 0 | 857.2767 |  | 0 |  | 0
| 505 | 0 | 0 | 0 | 0 | 0 | 0 | 825.1998 |  | 0 |  | 2.3206
| 506 | 0 | 0 | 0 | 0 | 0 | 0 | 793.0532 |  | 0 |  | 23.1207
| 507 | 0 | 0 | 0 | 0 | 0 | 0 | 760.8391 |  | 0 |  | 43.9153
| 508 | 0 | 0 | 0 | 0 | 0 | 0 | 728.5603 |  | 0 |  | 64.682
| 509 | 0 | 0 | 0 | 0 | 0 | 0 | 696.2199 |  | 0 |  | 85.3704
| 510 | 0 | 0 | 0 | 0 | 0 | 0 | 663.8175 |  | 0 |  | 105.9392
| 511 | 0 | 0 | 0 | 0 | 0 | 0 | 631.5136 |  | 0 |  | 126.4384
| 512 | 0 | 0 | 0 | 0 | 0 | 0 | 599.2194 |  | 0 |  | 146.8843
| 513 | 0 | 0 | 0 | 0 | 0 | 0 | 566.8631 |  | 0 |  | 167.1434
| 514 | 0 | 0 | 0 | 0 | 0 | 0 | 534.2299 |  | 0 |  | 187.1489
| 515 | 0 | 0 | 0 | 0 | 0 | 0 | 501.4183 |  | 0 |  | 206.9192
| 516 | 0 | 0 | 0 | 0 | 0 | 0 | 468.4091 |  | 0 |  | 226.429
| 517 | 0 | 0 | 0 | 0 | 0 | 0 | 435.1833 |  | 0 |  | 245.653
| 518 | 0 | 0 | 0 | 0 | 0 | 0 | 401.7218 |  | 0 |  | 264.5662
| 519 | 0 | 0 | 0 | 0 | 0 | 0 | 368.0434 |  | 0 |  | 283.1837
| 520 | 0 | 0 | 0 | 0 | 0 | 0 | 334.3539 |  | 0 |  | 301.5738
| 521 | 0 | 0 | 0 | 0 | 0 | 0 | 300.499 |  | 0 |  | 319.6759
| 522 | 0 | 0 | 0 | 0 | 0 | 0 | 266.4402 |  | 0 |  | 337.4269
| 523 | 0 | 0 | 0 | 0 | 0 | 0 | 232.2086 |  | 0 |  | 354.8544
| 524 | 0 | 0 | 0 | 0 | 0 | 0 | 197.8085 |  | 0 |  | 371.9576
| 525 | 0 | 0 | 0 | 0 | 0 | 0 | 163.2383 |  | 0 |  | 388.7292
| 526 | 0 | 0 | 0 | 0 | 0 | 0 | 128.5276 |  | 0 |  | 405.1955
| 527 | 0 | 0 | 0 | 0 | 0 | 0 | 93.8051 |  | 0 |  | 421.457
| 528 | 0 | 0 | 0 | 0 | 0 | 0 | 58.947 |  | 0 |  | 437.5492
| 529 | 0 | 0 | 4.6582 | 0.014444 | 0 | 0 | 24.179 |  | 0 |  | 453.6576
| 530 | 0 | 0 | 22.9085 | 0.071034 | 0 | 0 | 0 |  | 0 |  | 469.8215
| 531 | 0 | 0 | 41.1538 | 0.12761 | 0 | 0 | 0 |  | 0 |  | 485.9392
| 532 | 0 | 0 | 59.3924 | 0.18416 | 0 | 0 | 0 |  | 0 |  | 501.989
| 533 | 0 | 0 | 77.6227 | 0.24069 | 0 | 0 | 0 |  | 0 |  | 517.9354
| 534 | 0 | 0 | 95.843 | 0.29719 | 0 | 0 | 0 |  | 0 |  | 533.7454
| 535 | 0 | 0 | 114.2536 | 0.35427 | 0 | 0 | 0 |  | 0 |  | 549.4683
| 536 | 0 | 0 | 132.7626 | 0.41167 | 0 | 0 | 0 |  | 0 |  | 565.124
| 537 | 0 | 0 | 151.3424 | 0.46928 | 0 | 0 | 0 |  | 0 |  | 580.5831
| 538 | 0 | 0 | 169.7733 | 0.52643 | 0 | 0 | 0 |  | 0 |  | 595.7824
| 539 | 0 | 0 | 188.1379 | 0.58337 | 0 | 0 | 0 |  | 0 |  | 521.9177
| 540 | 0 | 0 | 206.4164 | 0.64005 | 0 | 0 | 0 |  | 0 |  | 490.6679
| 541 | 0 | 0 | 224.589 | 0.6964 | 0 | 0 | 0 |  | 0 |  | 459.1572
| 542 | 0 | 0 | 242.636 | 0.75236 | 0 | 0 | 0 |  | 0 |  | 427.3686
| 543 | 0 | 0 | 260.5378 | 0.80787 | 0 | 0 | 0 |  | 0 |  | 395.2849
| 544 | 0 | 0 | 278.4776 | 0.8635 | 0 | 0 | 0 |  | 0 |  | 362.9533
| 545 | 0 | 0 | 296.3798 | 0.91901 | 0 | 0 | 0 |  | 0 |  | 330.4354
| 546 | 0 | 0 | 314.2245 | 0.97434 | 0 | 0 | 0 |  | 0 |  | 297.6829
| 547 | 0 | 0 | 331.9552 | 1.0293 | 0 | 0 | 0 |  | 0 |  | 264.6344
| 548 | 0 | 0 | 349.5579 | 1.0839 | 0 | 0 | 0 |  | 0 |  | 231.2781
| 549 | 0 | 0 | 366.9998 | 1.138 | 0 | 0 | 0 |  | 0 |  | 197.5799
| 550 | 0 | 0 | 384.3328 | 1.1917 | 0 | 0 | 0 |  | 0 |  | 163.6036
| 551 | 0 | 0 | 401.6862 | 1.2455 | 0 | 0 | 0 |  | 0 |  | 129.4545
| 552 | 0 | 0 | 418.9199 | 1.299 | 0 | 0 | 0 |  | 0 |  | 95.1725
| 553 | 0 | 0 | 436.1726 | 1.3525 | 0 | 0 | 0 |  | 0 |  | 60.9479
| 554 | 0 | 0 | 453.3837 | 1.4058 | 0 | 0 | 0 |  | 0 |  | 26.8206
| 555 | 0 | 0 | 470.5504 | 1.4591 | 0 | 0 | 0 |  | 0 |  | 0
| 556 | 0 | 0 | 487.6713 | 1.5122 | 0 | 0 | 0 |  | 0 |  | 0
| 557 | 0 | 0 | 504.7448 | 1.5651 | 0 | 0 | 0 |  | 0 |  | 0
| 558 | 0 | 0 | 521.7693 | 1.6179 | 0 | 0 | 0 |  | 0 |  | 0
| 559 | 0 | 0 | 538.9482 | 1.6712 | 0 | 0 | 0 |  | 0 |  | 0
| 560 | 0 | 0 | 556.1888 | 1.7246 | 0 | 0 | 0 |  | 0 |  | 0
| 561 | 0 | 0 | 573.4588 | 1.7782 | 0 | 0 | 0 |  | 0 |  | 0
| 562 | 0 | 0 | 590.5167 | 1.8311 | 0 | 0 | 0 |  | 0 |  | 0
| 563 | 0 | 0 | 607.4557 | 1.8836 | 0 | 0 | 0 |  | 0 |  | 0
| 564 | 0 | 0 | 624.2547 | 1.9357 | 0 | 0 | 0 |  | 0 |  | 0
| 565 | 0 | 0 | 640.8929 | 1.9873 | 0 | 0 | 0 |  | 0 |  | 0
| 566 | 0 | 0 | 657.3494 | 2.0383 | 0 | 0 | 0 |  | 0 |  | 0
| 567 | 0 | 0 | 673.6033 | 2.0887 | 0 | 0 | 0 |  | 0 |  | 0
| 568 | 0 | 0 | 689.8742 | 2.1391 | 0 | 0 | 0 |  | 0 |  | 0
| 569 | 0 | 0 | 706.0679 | 2.1894 | 0 | 0 | 0 |  | 0 |  | 0
| 570 | 0 | 0 | 722.1197 | 2.2391 | 0 | 0 | 0 |  | 0 |  | 0
| 571 | 0 | 0 | 737.9823 | 2.2883 | 0 | 0 | 0 |  | 0 |  | 0
| 572 | 0 | 0 | 753.6414 | 2.3369 | 0 | 0 | 0 |  | 0 |  | 0
| 573 | 0 | 0 | 769.101 | 2.3848 | 0 | 0 | 0 |  | 0 |  | 0
| 574 | 0 | 0 | 784.4154 | 2.4323 | 0 | 0 | 0 |  | 0 |  | 0
| 575 | 0 | 0 | 799.7089 | 2.4797 | 0 | 0 | 0 |  | 0 |  | 0
| 576 | 0 | 0 | 814.8392 | 2.5266 | 0 | 0 | 0 |  | 0 |  | 0
| 577 | 0 | 0 | 829.9606 | 2.5735 | 0 | 0 | 0 |  | 0 |  | 0
| 578 | 0 | 0 | 845.0056 | 2.6202 | 0 | 0 | 0 |  | 0 |  | 0
| 579 | 0 | 0 | 859.9708 | 2.6666 | 0 | 0 | 0 |  | 0 |  | 0
| 580 | 0 | 0 | 874.8548 | 2.7127 | 0 | 0 | 0 |  | 0 |  | 0
| 581 | 0 | 0 | 889.6562 | 2.7586 | 0 | 0 | 0 |  | 0 |  | 0
| 582 | 0 | 0 | 904.3738 | 2.8043 | 0 | 0 | 0 |  | 0 |  | 0
| 583 | 0 | 0 | 919.2167 | 2.8503 | 0 | 0 | 0 |  | 0 |  | 0
| 584 | 0 | 0 | 934.0908 | 2.8964 | 0 | 0 | 0 |  | 0 |  | 0
| 585 | 0 | 0 | 948.9802 | 2.9426 | 0 | 0 | 0 |  | 0 |  | 0
| 586 | 0 | 0 | 963.8589 | 2.9887 | 0 | 0 | 0 |  | 0 |  | 0
| 587 | 0 | 0 | 978.6999 | 3.0347 | 0 | 0 | 0 |  | 0 |  | 0
| 588 | 0 | 0 | 993.4848 | 3.0806 | 0 | 0 | 0 |  | 0 |  | 0
| 589 | 0 | 0 | 1008.1948 | 3.1262 | 0 | 0 | 0 |  | 0 |  | 0
| 590 | 0 | 0 | 1022.8112 | 3.1715 | 0 | 0 | 0 |  | 0 |  | 0
| 591 | 0 | 0 | 1037.3481 | 3.2166 | 0 | 0 | 0 |  | 0 |  | 0
| 592 | 0 | 0 | 1051.7935 | 3.2614 | 0 | 0 | 0 |  | 0 |  | 0
| 593 | 0 | 0 | 1066.0833 | 3.3057 | 0 | 0 | 0 |  | 0 |  | 0
| 594 | 0 | 0 | 1080.1853 | 3.3494 | 0 | 0 | 0 |  | 0 |  | 0
| 595 | 0 | 0 | 1094.1386 | 3.3927 | 0 | 0 | 0 |  | 0 |  | 0
| 596 | 0 | 0 | 1108.0285 | 3.4357 | 0 | 0 | 0 |  | 0 |  | 0
| 597 | 0 | 0 | 1121.8918 | 3.4787 | 0 | 0 | 0 |  | 0 |  | 0
| 598 | 0 | 0 | 1135.765 | 3.5218 | 0 | 0 | 0 |  | 0 |  | 0
| 599 | 0 | 0 | 1149.6602 | 3.5648 | 0 | 0 | 0 |  | 0 |  | 0
| 600 | 0 | 0 | 1083.6975 | 3.3603 | 0 | 0 | 0 |  | 0 |  | 0
| 601 | 0 | 0 | 1051.3039 | 3.2599 | 0 | 0 | 0 |  | 0 |  | 0
| 602 | 0 | 0 | 1018.8191 | 3.1591 | 0 | 0 | 0 |  | 0 |  | 0
| 603 | 0 | 0 | 986.2461 | 3.0581 | 0 | 0 | 0 |  | 0 |  | 0
| 604 | 0 | 0 | 953.5879 | 2.9569 | 0 | 0 | 0 |  | 0 |  | 0
| 605 | 0 | 0 | 920.8474 | 2.8553 | 0 | 0 | 0 |  | 0 |  | 0
| 606 | 0 | 0 | 888.0278 | 2.7536 | 0 | 0 | 0 |  | 0 |  | 0
| 607 | 0 | 0 | 855.3463 | 2.6522 | 0 | 0 | 0 |  | 0 |  | 0
| 608 | 0 | 0 | 822.7121 | 2.551 | 0 | 0 | 0 |  | 0 |  | 0
| 609 | 0 | 0 | 790.1137 | 2.45 | 0 | 0 | 0 |  | 0 |  | 0
| 610 | 0 | 0 | 757.549 | 2.349 | 0 | 0 | 0 |  | 0 |  | 0
| 611 | 0 | 0 | 724.9901 | 2.248 | 0 | 0 | 0 |  | 0 |  | 0
| 612 | 0 | 0 | 692.4206 | 2.147 | 0 | 0 | 0 |  | 0 |  | 0
| 613 | 0 | 0 | 659.8267 | 2.046 | 0 | 0 | 0 |  | 0 |  | 0
| 614 | 0 | 0 | 627.2205 | 1.9449 | 0 | 0 | 0 |  | 0 |  | 0
| 615 | 0 | 0 | 594.631 | 1.8438 | 0 | 0 | 0 |  | 0 |  | 0
| 616 | 0 | 0 | 562.0692 | 1.7429 | 0 | 0 | 0 |  | 0 |  | 0
| 617 | 0 | 0 | 529.5464 | 1.642 | 0 | 0 | 0 |  | 0 |  | 0
| 618 | 0 | 0 | 497.0738 | 1.5413 | 0 | 0 | 0 |  | 0 |  | 0
| 619 | 0 | 0 | 464.6625 | 1.4408 | 0 | 0 | 0 |  | 0 |  | 0
| 620 | 0 | 0 | 432.3238 | 1.3405 | 0 | 0 | 0 |  | 0 |  | 0
| 621 | 0 | 0 | 400.0326 | 1.2404 | 0 | 0 | 0 |  | 0 |  | 0
| 622 | 0 | 0 | 367.8073 | 1.1405 | 0 | 0 | 0 |  | 0 |  | 0
| 623 | 0 | 0 | 335.6588 | 1.0408 | 0 | 0 | 0 |  | 0 |  | 0
| 624 | 0 | 0 | 303.3611 | 0.94065 | 0 | 0 | 0 |  | 0 |  | 0
| 625 | 0 | 0 | 271.0407 | 0.84044 | 0 | 0 | 0 |  | 0 |  | 0
| 626 | 0 | 0 | 238.7006 | 0.74016 | 0 | 0 | 0 |  | 0 |  | 0
| 627 | 0 | 0 | 206.3438 | 0.63983 | 0 | 0 | 0 |  | 0 |  | 0
| 628 | 0 | 0 | 173.9732 | 0.53945 | 0 | 0 | 0 |  | 0 |  | 0
| 629 | 0 | 0 | 141.5917 | 0.43904 | 0 | 0 | 0 |  | 0 |  | 0
| 630 | 0 | 0 | 109.2025 | 0.33861 | 0 | 0 | 0 |  | 0 |  | 0
| 631 | 0 | 0 | 77.0218 | 0.23883 | 0 | 0 | 0 |  | 0 |  | 0
| 632 | 0 | 0 | 44.9587 | 0.13941 | 0 | 0 | 0 |  | 0 |  | 0
| 633 | 0 | 0 | 12.987 | 0.04027 | 0 | 0 | 0 |  | 0 |  | 0
| 634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 635 | 288.665 | 0.90832 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 636 | 281.3051 | 0.88516 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 637 | 273.9581 | 0.86205 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 638 | 266.6241 | 0.83897 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 639 | 259.303 | 0.81593 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 640 | 258.0931 | 0.81212 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 641 | 265.2484 | 0.83464 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 642 | 272.3912 | 0.85712 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 643 | 279.5224 | 0.87955 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 644 | 286.6426 | 0.90196 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 645 | 293.9779 | 0.92504 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 646 | 301.8687 | 0.94987 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 647 | 302.4274 | 0.95163 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 648 | 297.7989 | 0.93706 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 649 | 293.5113 | 0.92357 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 650 | 289.3906 | 0.91061 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 651 | 285.0885 | 0.89707 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 652 | 280.4308 | 0.88241 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 653 | 275.4175 | 0.86664 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 654 | 270.0484 | 0.84974 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 655 | 270.4604 | 0.85104 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 656 | 278.9052 | 0.87761 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 657 | 278.6219 | 0.87672 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 658 | 271.8384 | 0.85538 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| Total | 21800.4679 | 68.5981 | 190948.7608 | 592.0892 | 0 | 0 | 112313.7666 | 0 | 0 | 0 | 23697.0215

## Winter
| T0 | 273 | K
Winter
|  | Hot Sink ASHP |  |  |  | Cold Sink ASHP
| Rating Condition | A7W20 |  |  |  | A7W10
Condenser Temp | ºC | 25 |  |  |  | 15
Evaporator Temp | ºC | 4 |  |  |  | 4
h1 | kJ/kg | 523.4 |  |  |  | 523.4
h2,act | kJ/kg | 553.9 |  |  |  | 539.6
h3 | kJ/kg | 236.1 |  |  |  | 217.1
h4 | kJ/kg | 236.1 |  |  |  | 217.7
s1 | J/kg.K | 2166.6 |  |  |  | 2166.6
s2,act | J/kg.K | 2185.4 |  |  |  | 2177.2
s3 | J/kg.K | 1124.3 |  |  |  | 1062.1
s4 | J/kg.K | 1129.9 |  |  |  | 1063.8
|  | Expansion Valve | Compressor | Condenser | Total | Expansion Valve | Compressor | Condenser | Total | Total
Total Exergy Destruction | kWh | 104.8727 | 352.0728 | 100.0589 | 557.0044 | 274.7886 | 1713.3877 | 758.3626 | 2746.5389 | 3303.5433 | kWh
|  | 18.83% | 63.21% | 17.96% | 100% | 10% | 62.38% | 27.61% | 100%
Hours
| 1 | 0 | 0 | 0 |  | 0.0014388 | 0.0089712 | 0.0039707
| 2 | 0 | 0 | 0 |  | 0.0014383 | 0.0089685 | 0.0039696
| 3 | 0 | 0 | 0 |  | 0.0014378 | 0.0089651 | 0.003968
| 4 | 0 | 0 | 0 |  | 0.0014371 | 0.0089608 | 0.0039661
| 5 | 0 | 0 | 0 |  | 0.0014363 | 0.0089556 | 0.0039639
| 6 | 0 | 0 | 0 |  | 0.0014353 | 0.0089497 | 0.0039612
| 7 | 0 | 0 | 0 |  | 0.0017356 | 0.010822 | 0.0047898
| 8 | 0 | 0 | 0 |  | 0.0022032 | 0.013738 | 0.0060805
| 9 | 0 | 0 | 0 |  | 0.002774 | 0.017297 | 0.0076557
| 10 | 0 | 0 | 0 |  | 0.003092 | 0.01928 | 0.0085334
| 11 | 0 | 0 | 0 |  | 0.0033004 | 0.020579 | 0.0091085
| 12 | 0 | 0 | 0 |  | 0.0033689 | 0.021006 | 0.0092975
| 13 | 0 | 0 | 0 |  | 0.0032673 | 0.020372 | 0.009017
| 14 | 0 | 0 | 0 |  | 0.0029653 | 0.01849 | 0.0081837
| 15 | 0 | 0 | 0 |  | 0.0024835 | 0.015486 | 0.0068541
| 16 | 0 | 0 | 0 |  | 0.0021301 | 0.013282 | 0.0058787
| 17 | 0 | 0 | 0 |  | 0.0016487 | 0.01028 | 0.0045502
| 18 | 0 | 0 | 0 |  | 0.00099923 | 0.0062305 | 0.0027577
| 19 | 0 | 0 | 0 |  | 0.00021939 | 0.0013679 | 0.00060546
| 20 | 0 | 0 | 0 |  | 0 | 0 | 0
| 21 | 0 | 0 | 0 |  | 0 | 0 | 0
| 22 | 0 | 0 | 0 |  | 0 | 0 | 0
| 23 | 0 | 0 | 0 |  | 0 | 0 | 0
| 24 | 0 | 0 | 0 |  | 0 | 0 | 0
| 25 | 0 | 0 | 0 |  | 0 | 0 | 0
| 26 | 0 | 0 | 0 |  | 0 | 0 | 0
| 27 | 0 | 0 | 0 |  | 0 | 0 | 0
| 28 | 0 | 0 | 0 |  | 0 | 0 | 0
| 29 | 0 | 0 | 0 |  | 0 | 0 | 0
| 30 | 0 | 0 | 0 |  | 0 | 0 | 0
| 31 | 0 | 0 | 0 |  | 0 | 0 | 0
| 32 | 0 | 0 | 0 |  | 0 | 0 | 0
| 33 | 0 | 0 | 0 |  | 0 | 0 | 0
| 34 | 0 | 0 | 0 |  | 0 | 0 | 0
| 35 | 0 | 0 | 0 |  | 0 | 0 | 0
| 36 | 0 | 0 | 0 |  | 0 | 0 | 0
| 37 | 0 | 0 | 0 |  | 0 | 0 | 0
| 38 | 0 | 0 | 0 |  | 0 | 0 | 0
| 39 | 0 | 0 | 0 |  | 0 | 0 | 0
| 40 | 0 | 0 | 0 |  | 0 | 0 | 0
| 41 | 0 | 0 | 0 |  | 0 | 0 | 0
| 42 | 0 | 0 | 0 |  | 0 | 0 | 0
| 43 | 0 | 0 | 0 |  | 0 | 0 | 0
| 44 | 0 | 0 | 0 |  | 0 | 0 | 0
| 45 | 0 | 0 | 0 |  | 0 | 0 | 0
| 46 | 0 | 0 | 0 |  | 0 | 0 | 0
| 47 | 0 | 0 | 0 |  | 0 | 0 | 0
| 48 | 0 | 0 | 0 |  | 0 | 0 | 0
| 49 | 0 | 0 | 0 |  | 0 | 0 | 0
| 50 | 0 | 0 | 0 |  | 0 | 0 | 0
| 51 | 0 | 0 | 0 |  | 0 | 0 | 0
| 52 | 0 | 0 | 0 |  | 0 | 0 | 0
| 53 | 0 | 0 | 0 |  | 0 | 0 | 0
| 54 | 0 | 0 | 0 |  | 0 | 0 | 0
| 55 | 0 | 0 | 0 |  | 0 | 0 | 0
| 56 | 0 | 0 | 0 |  | 0 | 0 | 0
| 57 | 0 | 0 | 0 |  | 0 | 0 | 0
| 58 | 0 | 0 | 0 |  | 0 | 0 | 0
| 59 | 0 | 0 | 0 |  | 0 | 0 | 0
| 60 | 0 | 0 | 0 |  | 0 | 0 | 0
| 61 | 0 | 0 | 0 |  | 0 | 0 | 0
| 62 | 0 | 0 | 0 |  | 0 | 0 | 0
| 63 | 0 | 0 | 0 |  | 0 | 0 | 0
| 64 | 0 | 0 | 0 |  | 0 | 0 | 0
| 65 | 0 | 0 | 0 |  | 0 | 0 | 0
| 66 | 0 | 0 | 0 |  | 0 | 0 | 0
| 67 | 0 | 0 | 0 |  | 0 | 0 | 0
| 68 | 0 | 0 | 0 |  | 0 | 0 | 0
| 69 | 0 | 0 | 0 |  | 0 | 0 | 0
| 70 | 0 | 0 | 0 |  | 0 | 0 | 0
| 71 | 0 | 0 | 0 |  | 0 | 0 | 0
| 72 | 0 | 0 | 0 |  | 0 | 0 | 0
| 73 | 0 | 0 | 0 |  | 0 | 0 | 0
| 74 | 0 | 0 | 0 |  | 0 | 0 | 0
| 75 | 0 | 0 | 0 |  | 0 | 0 | 0
| 76 | 0 | 0 | 0 |  | 0 | 0 | 0
| 77 | 0 | 0 | 0 |  | 0 | 0 | 0
| 78 | 0 | 0 | 0 |  | 0 | 0 | 0
| 79 | 0 | 0 | 0 |  | 0 | 0 | 0
| 80 | 0 | 0 | 0 |  | 0 | 0 | 0
| 81 | 0 | 0 | 0 |  | 0 | 0 | 0
| 82 | 0 | 0 | 0 |  | 0 | 0 | 0
| 83 | 0 | 0 | 0 |  | 0 | 0 | 0
| 84 | 0 | 0 | 0 |  | 0 | 0 | 0
| 85 | 0 | 0 | 0 |  | 0 | 0 | 0
| 86 | 0 | 0 | 0 |  | 0 | 0 | 0
| 87 | 0 | 0 | 0 |  | 0 | 0 | 0
| 88 | 0 | 0 | 0 |  | 0 | 0 | 0
| 89 | 0 | 0 | 0 |  | 0 | 0 | 0
| 90 | 0 | 0 | 0 |  | 0 | 0 | 0
| 91 | 0 | 0 | 0 |  | 0 | 0 | 0
| 92 | 0 | 0 | 0 |  | 0 | 0 | 0
| 93 | 0 | 0 | 0 |  | 0 | 0 | 0
| 94 | 0 | 0 | 0 |  | 0 | 0 | 0
| 95 | 0 | 0 | 0 |  | 0 | 0 | 0
| 96 | 0 | 0 | 0 |  | 0 | 0 | 0
| 97 | 0 | 0 | 0 |  | 0 | 0 | 0
| 98 | 0 | 0 | 0 |  | 0 | 0 | 0
| 99 | 0 | 0 | 0 |  | 0 | 0 | 0
| 100 | 0 | 0 | 0 |  | 0 | 0 | 0
| 101 | 0 | 0 | 0 |  | 0 | 0 | 0
| 102 | 0 | 0 | 0 |  | 0 | 0 | 0
| 103 | 0 | 0 | 0 |  | 0 | 0 | 0
| 104 | 0 | 0 | 0 |  | 0 | 0 | 0
| 105 | 0 | 0 | 0 |  | 0 | 0 | 0
| 106 | 0 | 0 | 0 |  | 0 | 0 | 0
| 107 | 0 | 0 | 0 |  | 0 | 0 | 0
| 108 | 0 | 0 | 0 |  | 0 | 0 | 0
| 109 | 0 | 0 | 0 |  | 0 | 0 | 0
| 110 | 0 | 0 | 0 |  | 0 | 0 | 0
| 111 | 0 | 0 | 0 |  | 0 | 0 | 0
| 112 | 1.1541 | 3.8746 | 1.1012 |  | 0 | 0 | 0
| 113 | 1.1844 | 3.9761 | 1.13 |  | 0 | 0 | 0
| 114 | 1.2145 | 4.0774 | 1.1588 |  | 0 | 0 | 0
| 115 | 1.2447 | 4.1785 | 1.1875 |  | 0 | 0 | 0
| 116 | 1.2748 | 4.2796 | 1.2163 |  | 0 | 0 | 0
| 117 | 1.3048 | 4.3805 | 1.2449 |  | 0 | 0 | 0
| 118 | 1.335 | 4.4819 | 1.2737 |  | 0 | 0 | 0
| 119 | 1.3285 | 4.4599 | 1.2675 |  | 0 | 0 | 0
| 120 | 1.297 | 4.3541 | 1.2374 |  | 0 | 0 | 0
| 121 | 1.2705 | 4.2651 | 1.2122 |  | 0 | 0 | 0
| 122 | 1.2465 | 4.1845 | 1.1892 |  | 0 | 0 | 0
| 123 | 1.2215 | 4.1006 | 1.1654 |  | 0 | 0 | 0
| 124 | 1.1945 | 4.0102 | 1.1397 |  | 0 | 0 | 0
| 125 | 1.1657 | 3.9133 | 1.1122 |  | 0 | 0 | 0
| 126 | 1.1348 | 3.8098 | 1.0828 |  | 0 | 0 | 0
| 127 | 1.1321 | 3.8006 | 1.0801 |  | 0 | 0 | 0
| 128 | 1.1679 | 3.9207 | 1.1142 |  | 0 | 0 | 0
| 129 | 1.1613 | 3.8987 | 1.108 |  | 0 | 0 | 0
| 130 | 1.1228 | 3.7693 | 1.0712 |  | 0 | 0 | 0
| 131 | 1.0829 | 3.6354 | 1.0332 |  | 0 | 0 | 0
| 132 | 2.93 | 9.8364 | 2.7955 |  | 0 | 0 | 0
| 133 | 2.8909 | 9.7051 | 2.7582 |  | 0 | 0 | 0
| 134 | 2.8519 | 9.5741 | 2.7209 |  | 0 | 0 | 0
| 135 | 2.8129 | 9.4433 | 2.6838 |  | 0 | 0 | 0
| 136 | 0 | 0 | 0 |  | 0 | 0 | 0
| 137 | 0 | 0 | 0 |  | 0 | 0 | 0
| 138 | 0 | 0 | 0 |  | 0 | 0 | 0
| 139 | 0 | 0 | 0 |  | 0 | 0 | 0
| 140 | 0 | 0 | 0 |  | 0 | 0 | 0
| 141 | 0 | 0 | 0 |  | 0 | 0 | 0
| 142 | 0 | 0 | 0 |  | 0 | 0 | 0
| 143 | 0 | 0 | 0 |  | 0.020301 | 0.12658 | 0.056026
| 144 | 0 | 0 | 0 |  | 0.047964 | 0.29907 | 0.13237
| 145 | 0 | 0 | 0 |  | 0.075618 | 0.4715 | 0.20869
| 146 | 0 | 0 | 0 |  | 0.10326 | 0.64386 | 0.28498
| 147 | 0 | 0 | 0 |  | 0.13089 | 0.81613 | 0.36123
| 148 | 0 | 0 | 0 |  | 0.1585 | 0.98831 | 0.43743
| 149 | 0 | 0 | 0 |  | 0.1861 | 1.1604 | 0.51359
| 150 | 0 | 0 | 0 |  | 0.21367 | 1.3323 | 0.58968
| 151 | 0 | 0 | 0 |  | 0.2415 | 1.5058 | 0.6665
| 152 | 0 | 0 | 0 |  | 0.26947 | 1.6802 | 0.74369
| 153 | 0 | 0 | 0 |  | 0.29753 | 1.8552 | 0.82113
| 154 | 0 | 0 | 0 |  | 0.3254 | 2.0289 | 0.89803
| 155 | 0 | 0 | 0 |  | 0.35322 | 2.2025 | 0.97483
| 156 | 0 | 0 | 0 |  | 0.38101 | 2.3757 | 1.0515
| 157 | 0 | 0 | 0 |  | 0.4087 | 2.5483 | 1.1279
| 158 | 0 | 0 | 0 |  | 0.43627 | 2.7203 | 1.204
| 159 | 0 | 0 | 0 |  | 0.46376 | 2.8917 | 1.2799
| 160 | 0 | 0 | 0 |  | 0.49143 | 3.0642 | 1.3563
| 161 | 0 | 0 | 0 |  | 0.51907 | 3.2366 | 1.4325
| 162 | 0 | 0 | 0 |  | 0.54663 | 3.4084 | 1.5086
| 163 | 0 | 0 | 0 |  | 0.57414 | 3.5799 | 1.5845
| 164 | 0 | 0 | 0 |  | 0.60159 | 3.7511 | 1.6603
| 165 | 0.80865 | 2.7148 | 0.77153 |  | 0.6291 | 3.9226 | 1.7362
| 166 | 0.83989 | 2.8196 | 0.80134 |  | 0.6567 | 4.0947 | 1.8124
| 167 | 0.83121 | 2.7905 | 0.79306 |  | 0.6844 | 4.2675 | 1.8888
| 168 | 0.79569 | 2.6712 | 0.75916 |  | 0.71188 | 4.4388 | 1.9647
| 169 | 0.76617 | 2.5721 | 0.731 |  | 0.73929 | 4.6097 | 2.0403
| 170 | 0.74166 | 2.4898 | 0.70761 |  | 0.76662 | 4.7801 | 2.1157
| 171 | 0.71712 | 2.4075 | 0.6842 |  | 0.79388 | 4.9501 | 2.191
| 172 | 0.69089 | 2.3194 | 0.65918 |  | 0.82106 | 5.1196 | 2.266
| 173 | 0.6617 | 2.2214 | 0.63133 |  | 0.84817 | 5.2886 | 2.3408
| 174 | 0 | 0 | 0 |  | 0.87519 | 5.457 | 2.4153
| 175 | 0 | 0 | 0 |  | 0.90241 | 5.6268 | 2.4905
| 176 | 0 | 0 | 0 |  | 0.92971 | 5.797 | 2.5658
| 177 | 0 | 0 | 0 |  | 0.95701 | 5.9673 | 2.6412
| 178 | 0 | 0 | 0 |  | 0.98398 | 6.1354 | 2.7156
| 179 | 0 | 0 | 0 |  | 1.0107 | 6.3023 | 2.7895
| 180 | 0 | 0 | 0 |  | 1.0373 | 6.4677 | 2.8627
| 181 | 0 | 0 | 0 |  | 1.0635 | 6.6314 | 2.9351
| 182 | 0 | 0 | 0 |  | 1.0895 | 6.7932 | 3.0067
| 183 | 0 | 0 | 0 |  | 1.1151 | 6.9532 | 3.0776
| 184 | 0 | 0 | 0 |  | 1.1408 | 7.1133 | 3.1484
| 185 | 0 | 0 | 0 |  | 1.1663 | 7.2719 | 3.2186
| 186 | 0 | 0 | 0 |  | 1.1914 | 7.4287 | 3.288
| 187 | 0 | 0 | 0 |  | 1.2163 | 7.584 | 3.3567
| 188 | 0 | 0 | 0 |  | 1.2409 | 7.7377 | 3.4248
| 189 | 0 | 0 | 0 |  | 1.2653 | 7.8897 | 3.4921
| 190 | 0 | 0 | 0 |  | 1.2895 | 8.0404 | 3.5588
| 191 | 0 | 0 | 0 |  | 1.3136 | 8.1908 | 3.6253
| 192 | 0 | 0 | 0 |  | 1.3375 | 8.3398 | 3.6913
| 193 | 0 | 0 | 0 |  | 1.3614 | 8.4885 | 3.7571
| 194 | 0 | 0 | 0 |  | 1.3851 | 8.6364 | 3.8225
| 195 | 0 | 0 | 0 |  | 1.4087 | 8.7834 | 3.8876
| 196 | 0 | 0 | 0 |  | 1.4321 | 8.9297 | 3.9524
| 197 | 0 | 0 | 0 |  | 1.4554 | 9.0751 | 4.0167
| 198 | 0 | 0 | 0 |  | 1.4786 | 9.2196 | 4.0807
| 199 | 0 | 0 | 0 |  | 1.502 | 9.3652 | 4.1451
| 200 | 0 | 0 | 0 |  | 1.5253 | 9.5109 | 4.2096
| 201 | 0 | 0 | 0 |  | 1.5487 | 9.6565 | 4.2741
| 202 | 0 | 0 | 0 |  | 1.5717 | 9.7999 | 4.3375
| 203 | 0 | 0 | 0 |  | 1.5945 | 9.942 | 4.4004
| 204 | 0 | 0 | 0 |  | 1.617 | 10.0825 | 4.4626
| 205 | 0 | 0 | 0 |  | 1.6393 | 10.2214 | 4.5241
| 206 | 0 | 0 | 0 |  | 1.6612 | 10.3583 | 4.5847
| 207 | 0 | 0 | 0 |  | 1.555 | 9.6961 | 4.2916
| 208 | 0 | 0 | 0 |  | 1.5105 | 9.4183 | 4.1686
| 209 | 0 | 0 | 0 |  | 1.4658 | 9.1396 | 4.0453
| 210 | 0 | 0 | 0 |  | 1.4209 | 8.8599 | 3.9215
| 211 | 0 | 0 | 0 |  | 1.3758 | 8.5787 | 3.797
| 212 | 0 | 0 | 0 |  | 1.3305 | 8.2959 | 3.6719
| 213 | 0 | 0 | 0 |  | 1.2848 | 8.0113 | 3.5459
| 214 | 0 | 0 | 0 |  | 1.239 | 7.7254 | 3.4193
| 215 | 0 | 0 | 0 |  | 1.1931 | 7.4394 | 3.2927
| 216 | 0 | 0 | 0 |  | 1.147 | 7.1519 | 3.1655
| 217 | 0 | 0 | 0 |  | 1.1009 | 6.8644 | 3.0382
| 218 | 0 | 0 | 0 |  | 1.0547 | 6.5763 | 2.9107
| 219 | 0 | 0 | 0 |  | 1.0084 | 6.2876 | 2.783
| 220 | 0 | 0 | 0 |  | 0.96202 | 5.9985 | 2.655
| 221 | 0 | 0 | 0 |  | 0.91556 | 5.7088 | 2.5268
| 222 | 0 | 0 | 0 |  | 0.86903 | 5.4186 | 2.3983
| 223 | 0 | 0 | 0 |  | 0.82273 | 5.1299 | 2.2706
| 224 | 0 | 0 | 0 |  | 0.77653 | 4.8419 | 2.1431
| 225 | 0 | 0 | 0 |  | 0.73039 | 4.5542 | 2.0157
| 226 | 0 | 0 | 0 |  | 0.68395 | 4.2647 | 1.8876
| 227 | 0 | 0 | 0 |  | 0.63737 | 3.9742 | 1.759
| 228 | 0 | 0 | 0 |  | 0.59061 | 3.6826 | 1.63
| 229 | 0 | 0 | 0 |  | 0.54365 | 3.3898 | 1.5004
| 230 | 0 | 0 | 0 |  | 0.49648 | 3.0957 | 1.3702
| 231 | 0 | 0 | 0 |  | 0.44906 | 2.8 | 1.2393
| 232 | 0 | 0 | 0 |  | 0.40174 | 2.505 | 1.1087
| 233 | 0 | 0 | 0 |  | 0.35437 | 2.2096 | 0.97799
| 234 | 0 | 0 | 0 |  | 0.30687 | 1.9134 | 0.84691
| 235 | 0 | 0 | 0 |  | 0.25918 | 1.6161 | 0.71529
| 236 | 0 | 0 | 0 |  | 0.21129 | 1.3174 | 0.58311
| 237 | 0 | 0 | 0 |  | 0.1632 | 1.0176 | 0.45039
| 238 | 0 | 0 | 0 |  | 0.115 | 0.71705 | 0.31737
| 239 | 0 | 0 | 0 |  | 0.066875 | 0.41698 | 0.18456
| 240 | 0 | 0 | 0 |  | 0.018616 | 0.11608 | 0.051377
| 241 | 0 | 0 | 0 |  | 0 | 0 | 0
| 242 | 0 | 0 | 0 |  | 0 | 0 | 0
| 243 | 0 | 0 | 0 |  | 0 | 0 | 0
| 244 | 0 | 0 | 0 |  | 0 | 0 | 0
| 245 | 0 | 0 | 0 |  | 0 | 0 | 0
| 246 | 0 | 0 | 0 |  | 0 | 0 | 0
| 247 | 0 | 0 | 0 |  | 0 | 0 | 0
| 248 | 0 | 0 | 0 |  | 0 | 0 | 0
| 249 | 0 | 0 | 0 |  | 0 | 0 | 0
| 250 | 0 | 0 | 0 |  | 0 | 0 | 0
| 251 | 0 | 0 | 0 |  | 0 | 0 | 0
| 252 | 0 | 0 | 0 |  | 0 | 0 | 0
| 253 | 0 | 0 | 0 |  | 0 | 0 | 0
| 254 | 0 | 0 | 0 |  | 0 | 0 | 0
| 255 | 0 | 0 | 0 |  | 0 | 0 | 0
| 256 | 0 | 0 | 0 |  | 0 | 0 | 0
| 257 | 0 | 0 | 0 |  | 0 | 0 | 0
| 258 | 0.13497 | 0.45311 | 0.12877 |  | 0 | 0 | 0
| 259 | 0.16686 | 0.56018 | 0.1592 |  | 0 | 0 | 0
| 260 | 0.1987 | 0.66706 | 0.18958 |  | 0 | 0 | 0
| 261 | 0.23048 | 0.77376 | 0.2199 |  | 0 | 0 | 0
| 262 | 0.26222 | 0.88031 | 0.25018 |  | 0 | 0 | 0
| 263 | 0.25412 | 0.85313 | 0.24246 |  | 0 | 0 | 0
| 264 | 0.22181 | 0.74465 | 0.21163 |  | 0 | 0 | 0
| 265 | 0.19555 | 0.65649 | 0.18657 |  | 0 | 0 | 0
| 266 | 0.17262 | 0.5795 | 0.16469 |  | 0 | 0 | 0
| 267 | 0.14966 | 0.50244 | 0.14279 |  | 0 | 0 | 0
| 268 | 0.12501 | 0.41967 | 0.11927 |  | 0 | 0 | 0
| 269 | 0.097973 | 0.32891 | 0.093476 |  | 0 | 0 | 0
| 270 | 0.068324 | 0.22937 | 0.065188 |  | 0 | 0 | 0
| 271 | 0.065989 | 0.22153 | 0.06296 |  | 0 | 0 | 0
| 272 | 0.10185 | 0.34192 | 0.097172 |  | 0 | 0 | 0
| 273 | 0.1356 | 0.45525 | 0.12938 |  | 0 | 0 | 0
| 274 | 0.16781 | 0.56337 | 0.16011 |  | 0 | 0 | 0
| 275 | 0.19991 | 0.67114 | 0.19074 |  | 0 | 0 | 0
| 276 | 0.23198 | 0.77879 | 0.22133 |  | 0 | 0 | 0
| 277 | 0.26401 | 0.88631 | 0.25189 |  | 0 | 0 | 0
| 278 | 0.29599 | 0.99369 | 0.28241 |  | 0 | 0 | 0
| 279 | 0.32794 | 1.1009 | 0.31289 |  | 0 | 0 | 0
| 280 | 0.35984 | 1.208 | 0.34333 |  | 0 | 0 | 0
| 281 | 0.39171 | 1.315 | 0.37373 |  | 0 | 0 | 0
| 282 | 0.42354 | 1.4219 | 0.4041 |  | 0 | 0 | 0
| 283 | 0.45534 | 1.5286 | 0.43444 |  | 0 | 0 | 0
| 284 | 0.4871 | 1.6353 | 0.46474 |  | 0 | 0 | 0
| 285 | 0.51882 | 1.7418 | 0.49501 |  | 0 | 0 | 0
| 286 | 0.55065 | 1.8486 | 0.52537 |  | 0 | 0 | 0
| 287 | 0.54566 | 1.8318 | 0.52061 |  | 0 | 0 | 0
| 288 | 0.51583 | 1.7317 | 0.49216 |  | 0 | 0 | 0
| 289 | 0.49101 | 1.6484 | 0.46847 |  | 0 | 0 | 0
| 290 | 0.46868 | 1.5734 | 0.44716 |  | 0 | 0 | 0
| 291 | 0.44536 | 1.4951 | 0.42492 |  | 0 | 0 | 0
| 292 | 0.42011 | 1.4104 | 0.40083 |  | 0 | 0 | 0
| 293 | 0.39292 | 1.3191 | 0.37489 |  | 0 | 0 | 0
| 294 | 0.36379 | 1.2213 | 0.34709 |  | 0 | 0 | 0
| 295 | 0.36265 | 1.2175 | 0.346 |  | 0 | 0 | 0
| 296 | 0.4 | 1.3428 | 0.38164 |  | 0 | 0 | 0
| 297 | 0.39506 | 1.3263 | 0.37692 |  | 0 | 0 | 0
| 298 | 0.35821 | 1.2026 | 0.34177 |  | 0 | 0 | 0
| 299 | 2.207 | 7.4091 | 2.1057 |  | 0 | 0 | 0
| 300 | 2.1696 | 7.2835 | 2.07 |  | 0 | 0 | 0
| 301 | 2.1322 | 7.1582 | 2.0344 |  | 0 | 0 | 0
| 302 | 2.0949 | 7.033 | 1.9988 |  | 0 | 0 | 0
| 303 | 0 | 0 | 0 |  | 0 | 0 | 0
| 304 | 0 | 0 | 0 |  | 0 | 0 | 0
| 305 | 0 | 0 | 0 |  | 0 | 0 | 0
| 306 | 0 | 0 | 0 |  | 0 | 0 | 0
| 307 | 0 | 0 | 0 |  | 0 | 0 | 0
| 308 | 0 | 0 | 0 |  | 0 | 0 | 0
| 309 | 0 | 0 | 0 |  | 0 | 0 | 0
| 310 | 0.35226 | 1.1826 | 0.33609 |  | 0 | 0 | 0
| 311 | 0.35281 | 1.1844 | 0.33662 |  | 0 | 0 | 0
| 312 | 0.32777 | 1.1004 | 0.31272 |  | 0 | 0 | 0
| 313 | 0.30437 | 1.0218 | 0.2904 |  | 0 | 0 | 0
| 314 | 0.2818 | 0.94603 | 0.26886 |  | 0 | 0 | 0
| 315 | 0.25836 | 0.86735 | 0.2465 |  | 0 | 0 | 0
| 316 | 0.23323 | 0.78298 | 0.22252 |  | 0 | 0 | 0
| 317 | 0.2064 | 0.6929 | 0.19692 |  | 0 | 0 | 0
| 318 | 0 | 0 | 0 |  | 0 | 0 | 0
| 319 | 0 | 0 | 0 |  | 0 | 0 | 0
| 320 | 0 | 0 | 0 |  | 0 | 0 | 0
| 321 | 0 | 0 | 0 |  | 0 | 0 | 0
| 322 | 0 | 0 | 0 |  | 0 | 0 | 0
| 323 | 0 | 0 | 0 |  | 0 | 0 | 0
| 324 | 0 | 0 | 0 |  | 0 | 0 | 0
| 325 | 0 | 0 | 0 |  | 0 | 0 | 0
| 326 | 0 | 0 | 0 |  | 0 | 0 | 0
| 327 | 0 | 0 | 0 |  | 0 | 0 | 0
| 328 | 0 | 0 | 0 |  | 0 | 0 | 0
| 329 | 0 | 0 | 0 |  | 0 | 0 | 0
| 330 | 0 | 0 | 0 |  | 0.020574 | 0.12828 | 0.05678
| 331 | 0 | 0 | 0 |  | 0.049041 | 0.30578 | 0.13534
| 332 | 0 | 0 | 0 |  | 0.077501 | 0.48324 | 0.21389
| 333 | 0 | 0 | 0 |  | 0.10605 | 0.66128 | 0.29269
| 334 | 0 | 0 | 0 |  | 0.13474 | 0.84015 | 0.37186
| 335 | 0 | 0 | 0 |  | 0.16358 | 1.0199 | 0.45144
| 336 | 0 | 0 | 0 |  | 0.19224 | 1.1987 | 0.53054
| 337 | 0 | 0 | 0 |  | 0.22088 | 1.3772 | 0.60958
| 338 | 0 | 0 | 0 |  | 0.24949 | 1.5557 | 0.68855
| 339 | 0 | 0 | 0 |  | 0.27808 | 1.7339 | 0.76744
| 340 | 0 | 0 | 0 |  | 0.30664 | 1.912 | 0.84626
| 341 | 0 | 0 | 0 |  | 0.33516 | 2.0898 | 0.92498
| 342 | 0 | 0 | 0 |  | 0.36365 | 2.2675 | 1.0036
| 343 | 0 | 0 | 0 |  | 0.39239 | 2.4466 | 1.0829
| 344 | 0 | 0 | 0 |  | 0.42124 | 2.6266 | 1.1625
| 345 | 0 | 0 | 0 |  | 0.45014 | 2.8068 | 1.2423
| 346 | 0 | 0 | 0 |  | 0.47875 | 2.9851 | 1.3213
| 347 | 0 | 0 | 0 |  | 0.5072 | 3.1625 | 1.3998
| 348 | 0 | 0 | 0 |  | 0.53545 | 3.3387 | 1.4777
| 349 | 0 | 0 | 0 |  | 0.56348 | 3.5135 | 1.5551
| 350 | 0 | 0 | 0 |  | 0.59125 | 3.6866 | 1.6317
| 351 | 0 | 0 | 0 |  | 0.61878 | 3.8583 | 1.7077
| 352 | 0 | 0 | 0 |  | 0.64636 | 4.0303 | 1.7838
| 353 | 0 | 0 | 0 |  | 0.67374 | 4.201 | 1.8594
| 354 | 0 | 0 | 0 |  | 0.70087 | 4.3701 | 1.9343
| 355 | 0 | 0 | 0 |  | 0.72779 | 4.538 | 2.0086
| 356 | 0 | 0 | 0 |  | 0.7545 | 4.7045 | 2.0823
| 357 | 0 | 0 | 0 |  | 0.781 | 4.8697 | 2.1554
| 358 | 0 | 0 | 0 |  | 0.8073 | 5.0338 | 2.228
| 359 | 0 | 0 | 0 |  | 0.83362 | 5.1978 | 2.3006
| 360 | 0 | 0 | 0 |  | 0.85973 | 5.3607 | 2.3727
| 361 | 0 | 0 | 0 |  | 0.88585 | 5.5235 | 2.4448
| 362 | 0 | 0 | 0 |  | 0.91189 | 5.6859 | 2.5166
| 363 | 0 | 0 | 0 |  | 0.93784 | 5.8477 | 2.5882
| 364 | 0 | 0 | 0 |  | 0.96369 | 6.0089 | 2.6596
| 365 | 0 | 0 | 0 |  | 0.98946 | 6.1696 | 2.7307
| 366 | 0 | 0 | 0 |  | 1.0151 | 6.3297 | 2.8016
| 367 | 0 | 0 | 0 |  | 1.041 | 6.4909 | 2.873
| 368 | 0 | 0 | 0 |  | 1.0669 | 6.6526 | 2.9445
| 369 | 0 | 0 | 0 |  | 1.0929 | 6.8144 | 3.0161
| 370 | 0 | 0 | 0 |  | 1.1185 | 6.9743 | 3.0869
| 371 | 0 | 0 | 0 |  | 1.144 | 7.1331 | 3.1572
| 372 | 0 | 0 | 0 |  | 1.1692 | 7.2906 | 3.2269
| 373 | 0 | 0 | 0 |  | 1.1943 | 7.4466 | 3.296
| 374 | 0 | 0 | 0 |  | 1.219 | 7.601 | 3.3643
| 375 | 0 | 0 | 0 |  | 1.2435 | 7.7535 | 3.4318
| 376 | 0 | 0 | 0 |  | 1.2679 | 7.9059 | 3.4992
| 377 | 0 | 0 | 0 |  | 1.2922 | 8.0574 | 3.5663
| 378 | 0 | 0 | 0 |  | 1.3164 | 8.2079 | 3.6329
| 379 | 0 | 0 | 0 |  | 1.3402 | 8.3568 | 3.6988
| 380 | 0 | 0 | 0 |  | 1.3639 | 8.5041 | 3.764
| 381 | 0 | 0 | 0 |  | 1.3872 | 8.6495 | 3.8284
| 382 | 0 | 0 | 0 |  | 1.4103 | 8.7934 | 3.892
| 383 | 0 | 0 | 0 |  | 1.4333 | 8.9369 | 3.9556
| 384 | 0 | 0 | 0 |  | 1.456 | 9.0789 | 4.0184
| 385 | 0 | 0 | 0 |  | 1.4788 | 9.2205 | 4.0811
| 386 | 0 | 0 | 0 |  | 1.5013 | 9.3613 | 4.1434
| 387 | 0 | 0 | 0 |  | 1.5238 | 9.5012 | 4.2053
| 388 | 0 | 0 | 0 |  | 1.5461 | 9.6403 | 4.2669
| 389 | 0 | 0 | 0 |  | 1.5682 | 9.7784 | 4.328
| 390 | 0 | 0 | 0 |  | 1.5902 | 9.9156 | 4.3887
| 391 | 0 | 0 | 0 |  | 1.6124 | 10.0537 | 4.4499
| 392 | 0 | 0 | 0 |  | 1.6346 | 10.192 | 4.5111
| 393 | 0 | 0 | 0 |  | 1.6567 | 10.33 | 4.5722
| 394 | 0 | 0 | 0 |  | 1.6784 | 10.4656 | 4.6322
| 395 | 0 | 0 | 0 |  | 1.6999 | 10.5996 | 4.6915
| 396 | 0 | 0 | 0 |  | 1.7211 | 10.7318 | 4.75
| 397 | 0 | 0 | 0 |  | 1.742 | 10.8621 | 4.8077
| 398 | 0 | 0 | 0 |  | 1.7626 | 10.9903 | 4.8644
| 399 | 0 | 0 | 0 |  | 1.7828 | 11.1162 | 4.9201
| 400 | 0 | 0 | 0 |  | 1.8029 | 11.2417 | 4.9757
| 401 | 0 | 0 | 0 |  | 1.8229 | 11.3661 | 5.0308
| 402 | 0 | 0 | 0 |  | 1.8425 | 11.4888 | 5.0851
| 403 | 0 | 0 | 0 |  | 1.7076 | 10.6473 | 4.7126
| 404 | 0 | 0 | 0 |  | 1.6604 | 10.3533 | 4.5825
| 405 | 0 | 0 | 0 |  | 1.613 | 10.0572 | 4.4514
| 406 | 0 | 0 | 0 |  | 1.5652 | 9.7596 | 4.3197
| 407 | 0 | 0 | 0 |  | 1.5174 | 9.4616 | 4.1878
| 408 | 0 | 0 | 0 |  | 1.4694 | 9.162 | 4.0552
| 409 | 0 | 0 | 0 |  | 1.4213 | 8.8621 | 3.9225
| 410 | 0 | 0 | 0 |  | 1.3731 | 8.5616 | 3.7894
| 411 | 0 | 0 | 0 |  | 1.3248 | 8.2603 | 3.6561
| 412 | 0 | 0 | 0 |  | 1.2763 | 7.9583 | 3.5224
| 413 | 0 | 0 | 0 |  | 1.2278 | 7.6556 | 3.3885
| 414 | 0 | 0 | 0 |  | 1.1791 | 7.3523 | 3.2542
| 415 | 0 | 0 | 0 |  | 1.1307 | 7.0503 | 3.1205
| 416 | 0 | 0 | 0 |  | 1.0823 | 6.7487 | 2.9871
| 417 | 0 | 0 | 0 |  | 1.034 | 6.4476 | 2.8538
| 418 | 0 | 0 | 0 |  | 0.98577 | 6.1466 | 2.7205
| 419 | 0 | 0 | 0 |  | 0.93748 | 5.8455 | 2.5873
| 420 | 0 | 0 | 0 |  | 0.88917 | 5.5442 | 2.4539
| 421 | 0 | 0 | 0 |  | 0.84081 | 5.2427 | 2.3205
| 422 | 0 | 0 | 0 |  | 0.79238 | 4.9407 | 2.1868
| 423 | 0 | 0 | 0 |  | 0.7439 | 4.6385 | 2.053
| 424 | 0 | 0 | 0 |  | 0.69538 | 4.3359 | 1.9191
| 425 | 0 | 0 | 0 |  | 0.64672 | 4.0325 | 1.7848
| 426 | 0 | 0 | 0 |  | 0.59787 | 3.7279 | 1.65
| 427 | 0 | 0 | 0 |  | 0.54892 | 3.4227 | 1.5149
| 428 | 0 | 0 | 0 |  | 0.49997 | 3.1175 | 1.3798
| 429 | 0 | 0 | 0 |  | 0.4511 | 2.8128 | 1.245
| 430 | 0 | 0 | 0 |  | 0.40236 | 2.5089 | 1.1104
| 431 | 0 | 0 | 0 |  | 0.35378 | 2.2059 | 0.97637
| 432 | 0 | 0 | 0 |  | 0.30501 | 1.9018 | 0.84176
| 433 | 0 | 0 | 0 |  | 0.25621 | 1.5976 | 0.7071
| 434 | 0 | 0 | 0 |  | 0.2074 | 1.2932 | 0.57239
| 435 | 0 | 0 | 0 |  | 0.15858 | 0.98879 | 0.43765
| 436 | 0 | 0 | 0 |  | 0.10975 | 0.68433 | 0.30289
| 437 | 0 | 0 | 0 |  | 0.06092 | 0.37985 | 0.16813
| 438 | 0 | 0 | 0 |  | 0.012091 | 0.075392 | 0.033369
| 439 | 0 | 0 | 0 |  | 0 | 0 | 0
| 440 | 0 | 0 | 0 |  | 0 | 0 | 0
| 441 | 0 | 0 | 0 |  | 0 | 0 | 0
| 442 | 0 | 0 | 0 |  | 0 | 0 | 0
| 443 | 0 | 0 | 0 |  | 0 | 0 | 0
| 444 | 0 | 0 | 0 |  | 0 | 0 | 0
| 445 | 0 | 0 | 0 |  | 0 | 0 | 0
| 446 | 0 | 0 | 0 |  | 0 | 0 | 0
| 447 | 0 | 0 | 0 |  | 0 | 0 | 0
| 448 | 0 | 0 | 0 |  | 0 | 0 | 0
| 449 | 0 | 0 | 0 |  | 0 | 0 | 0
| 450 | 0 | 0 | 0 |  | 0 | 0 | 0
| 451 | 0 | 0 | 0 |  | 0 | 0 | 0
| 452 | 0 | 0 | 0 |  | 0 | 0 | 0
| 453 | 0 | 0 | 0 |  | 0 | 0 | 0
| 454 | 0.027733 | 0.093105 | 0.02646 |  | 0 | 0 | 0
| 455 | 0.023474 | 0.078804 | 0.022396 |  | 0 | 0 | 0
| 456 | 0 | 0 | 0 |  | 0 | 0 | 0
| 457 | 0 | 0 | 0 |  | 0 | 0 | 0
| 458 | 0 | 0 | 0 |  | 0 | 0 | 0
| 459 | 0 | 0 | 0 |  | 0 | 0 | 0
| 460 | 0 | 0 | 0 |  | 0 | 0 | 0
| 461 | 0 | 0 | 0 |  | 0 | 0 | 0
| 462 | 0 | 0 | 0 |  | 0 | 0 | 0
| 463 | 0 | 0 | 0 |  | 0 | 0 | 0
| 464 | 0 | 0 | 0 |  | 0 | 0 | 0
| 465 | 0 | 0 | 0 |  | 0 | 0 | 0
| 466 | 0 | 0 | 0 |  | 0 | 0 | 0
| 467 | 1.6978 | 5.6996 | 1.6198 |  | 0 | 0 | 0
| 468 | 1.6615 | 5.578 | 1.5853 |  | 0 | 0 | 0
| 469 | 1.6254 | 5.4567 | 1.5508 |  | 0 | 0 | 0
| 470 | 1.5893 | 5.3355 | 1.5164 |  | 0 | 0 | 0
| 471 | 0 | 0 | 0 |  | 0 | 0 | 0
| 472 | 0 | 0 | 0 |  | 0 | 0 | 0
| 473 | 0 | 0 | 0 |  | 0 | 0 | 0
| 474 | 0 | 0 | 0 |  | 0 | 0 | 0
| 475 | 0 | 0 | 0 |  | 0 | 0 | 0
| 476 | 0 | 0 | 0 |  | 0 | 0 | 0
| 477 | 0 | 0 | 0 |  | 0 | 0 | 0
| 478 | 0 | 0 | 0 |  | 0 | 0 | 0
| 479 | 0 | 0 | 0 |  | 0 | 0 | 0
| 480 | 0 | 0 | 0 |  | 0 | 0 | 0
| 481 | 0 | 0 | 0 |  | 0 | 0 | 0
| 482 | 0 | 0 | 0 |  | 0 | 0 | 0
| 483 | 0 | 0 | 0 |  | 0 | 0 | 0
| 484 | 0 | 0 | 0 |  | 0 | 0 | 0
| 485 | 0 | 0 | 0 |  | 0 | 0 | 0
| 486 | 0 | 0 | 0 |  | 0 | 0 | 0
| 487 | 0 | 0 | 0 |  | 0 | 0 | 0
| 488 | 0 | 0 | 0 |  | 0 | 0 | 0
| 489 | 0 | 0 | 0 |  | 0 | 0 | 0
| 490 | 0 | 0 | 0 |  | 0 | 0 | 0
| 491 | 0 | 0 | 0 |  | 0 | 0 | 0
| 492 | 0 | 0 | 0 |  | 0 | 0 | 0
| 493 | 0 | 0 | 0 |  | 0 | 0 | 0
| 494 | 0 | 0 | 0 |  | 0 | 0 | 0
| 495 | 0 | 0 | 0 |  | 0 | 0 | 0
| 496 | 0 | 0 | 0 |  | 0 | 0 | 0
| 497 | 0 | 0 | 0 |  | 0 | 0 | 0
| 498 | 0 | 0 | 0 |  | 0 | 0 | 0
| 499 | 0 | 0 | 0 |  | 0 | 0 | 0
| 500 | 0 | 0 | 0 |  | 0 | 0 | 0
| 501 | 0 | 0 | 0 |  | 0 | 0 | 0
| 502 | 0 | 0 | 0 |  | 0 | 0 | 0
| 503 | 0 | 0 | 0 |  | 0 | 0 | 0
| 504 | 0 | 0 | 0 |  | 0 | 0 | 0
| 505 | 0 | 0 | 0 |  | 0 | 0 | 0
| 506 | 0 | 0 | 0 |  | 0 | 0 | 0
| 507 | 0 | 0 | 0 |  | 0 | 0 | 0
| 508 | 0 | 0 | 0 |  | 0 | 0 | 0
| 509 | 0 | 0 | 0 |  | 0 | 0 | 0
| 510 | 0 | 0 | 0 |  | 0 | 0 | 0
| 511 | 0 | 0 | 0 |  | 0 | 0 | 0
| 512 | 0 | 0 | 0 |  | 0 | 0 | 0
| 513 | 0 | 0 | 0 |  | 0 | 0 | 0
| 514 | 0 | 0 | 0 |  | 0 | 0 | 0
| 515 | 0 | 0 | 0 |  | 0 | 0 | 0
| 516 | 0 | 0 | 0 |  | 0 | 0 | 0
| 517 | 0 | 0 | 0 |  | 0 | 0 | 0
| 518 | 0 | 0 | 0 |  | 0 | 0 | 0
| 519 | 0 | 0 | 0 |  | 0 | 0 | 0
| 520 | 0 | 0 | 0 |  | 0 | 0 | 0
| 521 | 0 | 0 | 0 |  | 0 | 0 | 0
| 522 | 0 | 0 | 0 |  | 0 | 0 | 0
| 523 | 0 | 0 | 0 |  | 0 | 0 | 0
| 524 | 0 | 0 | 0 |  | 0 | 0 | 0
| 525 | 0 | 0 | 0 |  | 0 | 0 | 0
| 526 | 0 | 0 | 0 |  | 0 | 0 | 0
| 527 | 0 | 0 | 0 |  | 0 | 0 | 0
| 528 | 0 | 0 | 0 |  | 0 | 0 | 0
| 529 | 0 | 0 | 0 |  | 0.0067035 | 0.041798 | 0.0185
| 530 | 0 | 0 | 0 |  | 0.032967 | 0.20556 | 0.090982
| 531 | 0 | 0 | 0 |  | 0.059223 | 0.36927 | 0.16344
| 532 | 0 | 0 | 0 |  | 0.08547 | 0.53293 | 0.23588
| 533 | 0 | 0 | 0 |  | 0.1117 | 0.69651 | 0.30828
| 534 | 0 | 0 | 0 |  | 0.13792 | 0.86 | 0.38065
| 535 | 0 | 0 | 0 |  | 0.16442 | 1.0252 | 0.45376
| 536 | 0 | 0 | 0 |  | 0.19105 | 1.1913 | 0.52727
| 537 | 0 | 0 | 0 |  | 0.21779 | 1.358 | 0.60106
| 538 | 0 | 0 | 0 |  | 0.24432 | 1.5234 | 0.67426
| 539 | 0 | 0 | 0 |  | 0.27074 | 1.6882 | 0.7472
| 540 | 0 | 0 | 0 |  | 0.29705 | 1.8522 | 0.81979
| 541 | 0 | 0 | 0 |  | 0.3232 | 2.0152 | 0.89197
| 542 | 0 | 0 | 0 |  | 0.34917 | 2.1772 | 0.96364
| 543 | 0 | 0 | 0 |  | 0.37493 | 2.3378 | 1.0347
| 544 | 0 | 0 | 0 |  | 0.40075 | 2.4988 | 1.106
| 545 | 0 | 0 | 0 |  | 0.42651 | 2.6594 | 1.1771
| 546 | 0 | 0 | 0 |  | 0.45219 | 2.8195 | 1.248
| 547 | 0 | 0 | 0 |  | 0.47771 | 2.9786 | 1.3184
| 548 | 0 | 0 | 0 |  | 0.50304 | 3.1366 | 1.3883
| 549 | 0 | 0 | 0 |  | 0.52814 | 3.2931 | 1.4576
| 550 | 0 | 0 | 0 |  | 0.55308 | 3.4486 | 1.5264
| 551 | 0 | 0 | 0 |  | 0.57805 | 3.6043 | 1.5953
| 552 | 0 | 0 | 0 |  | 0.60285 | 3.759 | 1.6638
| 553 | 0 | 0 | 0 |  | 0.62768 | 3.9138 | 1.7323
| 554 | 0 | 0 | 0 |  | 0.65245 | 4.0682 | 1.8006
| 555 | 0 | 0 | 0 |  | 0.67715 | 4.2223 | 1.8688
| 556 | 0 | 0 | 0 |  | 0.70179 | 4.3759 | 1.9368
| 557 | 0 | 0 | 0 |  | 0.72636 | 4.5291 | 2.0046
| 558 | 0 | 0 | 0 |  | 0.75086 | 4.6818 | 2.0722
| 559 | 0 | 0 | 0 |  | 0.77558 | 4.836 | 2.1405
| 560 | 0 | 0 | 0 |  | 0.80039 | 4.9907 | 2.2089
| 561 | 0 | 0 | 0 |  | 0.82525 | 5.1457 | 2.2775
| 562 | 0 | 0 | 0 |  | 0.84979 | 5.2987 | 2.3453
| 563 | 0 | 0 | 0 |  | 0.87417 | 5.4507 | 2.4125
| 564 | 0 | 0 | 0 |  | 0.89835 | 5.6015 | 2.4793
| 565 | 0 | 0 | 0 |  | 0.92229 | 5.7507 | 2.5453
| 566 | 0 | 0 | 0 |  | 0.94597 | 5.8984 | 2.6107
| 567 | 0 | 0 | 0 |  | 0.96936 | 6.0443 | 2.6752
| 568 | 0 | 0 | 0 |  | 0.99278 | 6.1903 | 2.7399
| 569 | 0 | 0 | 0 |  | 1.0161 | 6.3356 | 2.8042
| 570 | 0 | 0 | 0 |  | 1.0392 | 6.4796 | 2.8679
| 571 | 0 | 0 | 0 |  | 1.062 | 6.6219 | 2.9309
| 572 | 0 | 0 | 0 |  | 1.0845 | 6.7624 | 2.9931
| 573 | 0 | 0 | 0 |  | 1.1068 | 6.9012 | 3.0545
| 574 | 0 | 0 | 0 |  | 1.1288 | 7.0386 | 3.1153
| 575 | 0 | 0 | 0 |  | 1.1508 | 7.1758 | 3.1761
| 576 | 0 | 0 | 0 |  | 1.1726 | 7.3116 | 3.2362
| 577 | 0 | 0 | 0 |  | 1.1944 | 7.4473 | 3.2962
| 578 | 0 | 0 | 0 |  | 1.216 | 7.5823 | 3.356
| 579 | 0 | 0 | 0 |  | 1.2376 | 7.7165 | 3.4154
| 580 | 0 | 0 | 0 |  | 1.259 | 7.8501 | 3.4745
| 581 | 0 | 0 | 0 |  | 1.2803 | 7.9829 | 3.5333
| 582 | 0 | 0 | 0 |  | 1.3015 | 8.115 | 3.5918
| 583 | 0 | 0 | 0 |  | 1.3228 | 8.2482 | 3.6507
| 584 | 0 | 0 | 0 |  | 1.3442 | 8.3816 | 3.7098
| 585 | 0 | 0 | 0 |  | 1.3656 | 8.5152 | 3.7689
| 586 | 0 | 0 | 0 |  | 1.3871 | 8.6487 | 3.828
| 587 | 0 | 0 | 0 |  | 1.4084 | 8.7819 | 3.887
| 588 | 0 | 0 | 0 |  | 1.4297 | 8.9146 | 3.9457
| 589 | 0 | 0 | 0 |  | 1.4509 | 9.0466 | 4.0041
| 590 | 0 | 0 | 0 |  | 1.4719 | 9.1777 | 4.0621
| 591 | 0 | 0 | 0 |  | 1.4928 | 9.3081 | 4.1199
| 592 | 0 | 0 | 0 |  | 1.5136 | 9.4378 | 4.1773
| 593 | 0 | 0 | 0 |  | 1.5342 | 9.566 | 4.234
| 594 | 0 | 0 | 0 |  | 1.5545 | 9.6925 | 4.29
| 595 | 0 | 0 | 0 |  | 1.5745 | 9.8177 | 4.3454
| 596 | 0 | 0 | 0 |  | 1.5945 | 9.9424 | 4.4006
| 597 | 0 | 0 | 0 |  | 1.6145 | 10.0668 | 4.4556
| 598 | 0 | 0 | 0 |  | 1.6344 | 10.1912 | 4.5107
| 599 | 0 | 0 | 0 |  | 1.6544 | 10.3159 | 4.5659
| 600 | 0 | 0 | 0 |  | 1.5595 | 9.724 | 4.304
| 601 | 0 | 0 | 0 |  | 1.5129 | 9.4334 | 4.1753
| 602 | 0 | 0 | 0 |  | 1.4662 | 9.1419 | 4.0463
| 603 | 0 | 0 | 0 |  | 1.4193 | 8.8496 | 3.9169
| 604 | 0 | 0 | 0 |  | 1.3723 | 8.5566 | 3.7872
| 605 | 0 | 0 | 0 |  | 1.3252 | 8.2628 | 3.6572
| 606 | 0 | 0 | 0 |  | 1.2779 | 7.9683 | 3.5268
| 607 | 0 | 0 | 0 |  | 1.2309 | 7.675 | 3.3971
| 608 | 0 | 0 | 0 |  | 1.1839 | 7.3822 | 3.2674
| 609 | 0 | 0 | 0 |  | 1.137 | 7.0897 | 3.138
| 610 | 0 | 0 | 0 |  | 1.0902 | 6.7975 | 3.0086
| 611 | 0 | 0 | 0 |  | 1.0433 | 6.5054 | 2.8793
| 612 | 0 | 0 | 0 |  | 0.99644 | 6.2131 | 2.75
| 613 | 0 | 0 | 0 |  | 0.94954 | 5.9206 | 2.6205
| 614 | 0 | 0 | 0 |  | 0.90261 | 5.6281 | 2.491
| 615 | 0 | 0 | 0 |  | 0.85572 | 5.3356 | 2.3616
| 616 | 0 | 0 | 0 |  | 0.80886 | 5.0435 | 2.2323
| 617 | 0 | 0 | 0 |  | 0.76205 | 4.7516 | 2.1031
| 618 | 0 | 0 | 0 |  | 0.71532 | 4.4603 | 1.9742
| 619 | 0 | 0 | 0 |  | 0.66868 | 4.1694 | 1.8454
| 620 | 0 | 0 | 0 |  | 0.62214 | 3.8793 | 1.717
| 621 | 0 | 0 | 0 |  | 0.57567 | 3.5895 | 1.5887
| 622 | 0 | 0 | 0 |  | 0.5293 | 3.3003 | 1.4608
| 623 | 0 | 0 | 0 |  | 0.48304 | 3.0119 | 1.3331
| 624 | 0 | 0 | 0 |  | 0.43656 | 2.7221 | 1.2048
| 625 | 0 | 0 | 0 |  | 0.39005 | 2.4321 | 1.0765
| 626 | 0 | 0 | 0 |  | 0.34351 | 2.1419 | 0.94801
| 627 | 0 | 0 | 0 |  | 0.29694 | 1.8515 | 0.8195
| 628 | 0 | 0 | 0 |  | 0.25036 | 1.5611 | 0.69094
| 629 | 0 | 0 | 0 |  | 0.20376 | 1.2705 | 0.56234
| 630 | 0 | 0 | 0 |  | 0.15715 | 0.97988 | 0.4337
| 631 | 0 | 0 | 0 |  | 0.11084 | 0.69112 | 0.3059
| 632 | 0 | 0 | 0 |  | 0.064699 | 0.40342 | 0.17856
| 633 | 0 | 0 | 0 |  | 0.018689 | 0.11653 | 0.051579
| 634 | 0 | 0 | 0 |  | 0 | 0 | 0
| 635 | 1.3886 | 4.6619 | 1.3249 |  | 0 | 0 | 0
| 636 | 1.3532 | 4.543 | 1.2911 |  | 0 | 0 | 0
| 637 | 1.3179 | 4.4244 | 1.2574 |  | 0 | 0 | 0
| 638 | 1.2826 | 4.3059 | 1.2237 |  | 0 | 0 | 0
| 639 | 1.2474 | 4.1877 | 1.1901 |  | 0 | 0 | 0
| 640 | 1.2416 | 4.1681 | 1.1846 |  | 0 | 0 | 0
| 641 | 1.276 | 4.2837 | 1.2174 |  | 0 | 0 | 0
| 642 | 1.3104 | 4.3991 | 1.2502 |  | 0 | 0 | 0
| 643 | 1.3447 | 4.5142 | 1.2829 |  | 0 | 0 | 0
| 644 | 1.3789 | 4.6292 | 1.3156 |  | 0 | 0 | 0
| 645 | 1.4142 | 4.7477 | 1.3493 |  | 0 | 0 | 0
| 646 | 1.4522 | 4.8751 | 1.3855 |  | 0 | 0 | 0
| 647 | 1.4548 | 4.8841 | 1.3881 |  | 0 | 0 | 0
| 648 | 1.4326 | 4.8094 | 1.3668 |  | 0 | 0 | 0
| 649 | 1.412 | 4.7401 | 1.3471 |  | 0 | 0 | 0
| 650 | 1.3921 | 4.6736 | 1.3282 |  | 0 | 0 | 0
| 651 | 1.3714 | 4.6041 | 1.3085 |  | 0 | 0 | 0
| 652 | 1.349 | 4.5289 | 1.2871 |  | 0 | 0 | 0
| 653 | 1.3249 | 4.4479 | 1.2641 |  | 0 | 0 | 0
| 654 | 1.2991 | 4.3612 | 1.2395 |  | 0 | 0 | 0
| 655 | 1.3011 | 4.3679 | 1.2413 |  | 0 | 0 | 0
| 656 | 1.3417 | 4.5043 | 1.2801 |  | 0 | 0 | 0
| 657 | 1.3403 | 4.4997 | 1.2788 |  | 0 | 0 | 0
| 658 | 1.3077 | 4.3901 | 1.2477 |  | 0 | 0 | 0
| 659 | 0 | 0 | 0 |  | 0 | 0 | 0
| 660 | 0 | 0 | 0 |  | 0 | 0 | 0
| 661 | 0 | 0 | 0 |  | 0 | 0 | 0
| 662 | 0 | 0 | 0 |  | 0 | 0 | 0
| 663 | 0 | 0 | 0 |  | 0 | 0 | 0
| 664 | 0 | 0 | 0 |  | 0 | 0 | 0
| 665 | 0 | 0 | 0 |  | 0 | 0 | 0
| 666 | 0 | 0 | 0 |  | 0 | 0 | 0
| 667 | 0 | 0 | 0 |  | 0 | 0 | 0
| 668 | 0 | 0 | 0 |  | 0 | 0 | 0
| 669 | 0 | 0 | 0 |  | 0 | 0 | 0
| 670 | 0 | 0 | 0 |  | 0 | 0 | 0
| 671 | 0 | 0 | 0 |  | 0 | 0 | 0
| 672 | 0 | 0 | 0 |  | 0 | 0 | 0
| Total | 104.8727 | 352.0728 | 100.0589 | 0 | 274.7886 | 1713.3877 | 758.3626 | 0

## Spring_autumn
| T0 | 273 | K
spring/autumn
|  | Hot Sink ASHP |  |  |  | Cold Sink ASHP
| Rating Condition | A15.3W20 |  |  |  | A15.3W10
Condenser Temp | ºC | 25 |  |  |  | 15
Evaporator Temp | ºC | 4 |  |  |  | 4
h1 | kJ/kg | 524.9 |  |  |  | 523.4
h2,act | kJ/kg | 542.3 |  |  |  | 539.6
h3 | kJ/kg | 236.1 |  |  |  | 217.1
h4 | kJ/kg | 236.1 |  |  |  | 217.7
s1 | J/kg.K | 2138.2 |  |  |  | 2166.6
s2,act | J/kg.K | 2149.2 |  |  |  | 2177.2
s3 | J/kg.K | 1124.3 |  |  |  | 1062.1
s4 | J/kg.K | 1126.7 |  |  |  | 1063.8
|  | Expansion Valve | Compressor | Condenser | Total | Expansion Valve | Compressor | Condenser | Total | Total
Total Exergy Destruction | kWh | 0 | 0 | -17.7514 | -17.7514 | 274.7886 | 1713.3877 | 758.3626 | 2746.5389 | 2728.7875 | kWh
[6 empty] | 10% | 62.38% | 27.61% | 100%
Hours
| 1 | 0 | 0 | 0 |  | 0.0014388 | 0.0089712 | 0.0039707
| 2 | 0 | 0 | 0 |  | 0.0014383 | 0.0089685 | 0.0039696
| 3 | 0 | 0 | 0 |  | 0.0014378 | 0.0089651 | 0.003968
| 4 | 0 | 0 | 0 |  | 0.0014371 | 0.0089608 | 0.0039661
| 5 | 0 | 0 | 0 |  | 0.0014363 | 0.0089556 | 0.0039639
| 6 | 0 | 0 | 0 |  | 0.0014353 | 0.0089497 | 0.0039612
| 7 | 0 | 0 | 0 |  | 0.0017356 | 0.010822 | 0.0047898
| 8 | 0 | 0 | 0 |  | 0.0022032 | 0.013738 | 0.0060805
| 9 | 0 | 0 | 0 |  | 0.002774 | 0.017297 | 0.0076557
| 10 | 0 | 0 | 0 |  | 0.003092 | 0.01928 | 0.0085334
| 11 | 0 | 0 | 0 |  | 0.0033004 | 0.020579 | 0.0091085
| 12 | 0 | 0 | 0 |  | 0.0033689 | 0.021006 | 0.0092975
| 13 | 0 | 0 | 0 |  | 0.0032673 | 0.020372 | 0.009017
| 14 | 0 | 0 | 0 |  | 0.0029653 | 0.01849 | 0.0081837
| 15 | 0 | 0 | 0 |  | 0.0024835 | 0.015486 | 0.0068541
| 16 | 0 | 0 | 0 |  | 0.0021301 | 0.013282 | 0.0058787
| 17 | 0 | 0 | 0 |  | 0.0016487 | 0.01028 | 0.0045502
| 18 | 0 | 0 | 0 |  | 0.00099923 | 0.0062305 | 0.0027577
| 19 | 0 | 0 | 0 |  | 0.00021939 | 0.0013679 | 0.00060546
| 20 | 0 | 0 | 0 |  | 0 | 0 | 0
| 21 | 0 | 0 | 0 |  | 0 | 0 | 0
| 22 | 0 | 0 | 0 |  | 0 | 0 | 0
| 23 | 0 | 0 | 0 |  | 0 | 0 | 0
| 24 | 0 | 0 | 0 |  | 0 | 0 | 0
| 25 | 0 | 0 | 0 |  | 0 | 0 | 0
| 26 | 0 | 0 | 0 |  | 0 | 0 | 0
| 27 | 0 | 0 | 0 |  | 0 | 0 | 0
| 28 | 0 | 0 | 0 |  | 0 | 0 | 0
| 29 | 0 | 0 | 0 |  | 0 | 0 | 0
| 30 | 0 | 0 | 0 |  | 0 | 0 | 0
| 31 | 0 | 0 | 0 |  | 0 | 0 | 0
| 32 | 0 | 0 | 0 |  | 0 | 0 | 0
| 33 | 0 | 0 | 0 |  | 0 | 0 | 0
| 34 | 0 | 0 | 0 |  | 0 | 0 | 0
| 35 | 0 | 0 | 0 |  | 0 | 0 | 0
| 36 | 0 | 0 | 0 |  | 0 | 0 | 0
| 37 | 0 | 0 | 0 |  | 0 | 0 | 0
| 38 | 0 | 0 | 0 |  | 0 | 0 | 0
| 39 | 0 | 0 | 0 |  | 0 | 0 | 0
| 40 | 0 | 0 | 0 |  | 0 | 0 | 0
| 41 | 0 | 0 | 0 |  | 0 | 0 | 0
| 42 | 0 | 0 | 0 |  | 0 | 0 | 0
| 43 | 0 | 0 | 0 |  | 0 | 0 | 0
| 44 | 0 | 0 | 0 |  | 0 | 0 | 0
| 45 | 0 | 0 | 0 |  | 0 | 0 | 0
| 46 | 0 | 0 | 0 |  | 0 | 0 | 0
| 47 | 0 | 0 | 0 |  | 0 | 0 | 0
| 48 | 0 | 0 | 0 |  | 0 | 0 | 0
| 49 | 0 | 0 | 0 |  | 0 | 0 | 0
| 50 | 0 | 0 | 0 |  | 0 | 0 | 0
| 51 | 0 | 0 | 0 |  | 0 | 0 | 0
| 52 | 0 | 0 | 0 |  | 0 | 0 | 0
| 53 | 0 | 0 | 0 |  | 0 | 0 | 0
| 54 | 0 | 0 | 0 |  | 0 | 0 | 0
| 55 | 0 | 0 | 0 |  | 0 | 0 | 0
| 56 | 0 | 0 | 0 |  | 0 | 0 | 0
| 57 | 0 | 0 | 0 |  | 0 | 0 | 0
| 58 | 0 | 0 | 0 |  | 0 | 0 | 0
| 59 | 0 | 0 | 0 |  | 0 | 0 | 0
| 60 | 0 | 0 | 0 |  | 0 | 0 | 0
| 61 | 0 | 0 | 0 |  | 0 | 0 | 0
| 62 | 0 | 0 | 0 |  | 0 | 0 | 0
| 63 | 0 | 0 | 0 |  | 0 | 0 | 0
| 64 | 0 | 0 | 0 |  | 0 | 0 | 0
| 65 | 0 | 0 | 0 |  | 0 | 0 | 0
| 66 | 0 | 0 | 0 |  | 0 | 0 | 0
| 67 | 0 | 0 | 0 |  | 0 | 0 | 0
| 68 | 0 | 0 | 0 |  | 0 | 0 | 0
| 69 | 0 | 0 | 0 |  | 0 | 0 | 0
| 70 | 0 | 0 | 0 |  | 0 | 0 | 0
| 71 | 0 | 0 | 0 |  | 0 | 0 | 0
| 72 | 0 | 0 | 0 |  | 0 | 0 | 0
| 73 | 0 | 0 | 0 |  | 0 | 0 | 0
| 74 | 0 | 0 | 0 |  | 0 | 0 | 0
| 75 | 0 | 0 | 0 |  | 0 | 0 | 0
| 76 | 0 | 0 | 0 |  | 0 | 0 | 0
| 77 | 0 | 0 | 0 |  | 0 | 0 | 0
| 78 | 0 | 0 | 0 |  | 0 | 0 | 0
| 79 | 0 | 0 | 0 |  | 0 | 0 | 0
| 80 | 0 | 0 | 0 |  | 0 | 0 | 0
| 81 | 0 | 0 | 0 |  | 0 | 0 | 0
| 82 | 0 | 0 | 0 |  | 0 | 0 | 0
| 83 | 0 | 0 | 0 |  | 0 | 0 | 0
| 84 | 0 | 0 | 0 |  | 0 | 0 | 0
| 85 | 0 | 0 | 0 |  | 0 | 0 | 0
| 86 | 0 | 0 | 0 |  | 0 | 0 | 0
| 87 | 0 | 0 | 0 |  | 0 | 0 | 0
| 88 | 0 | 0 | 0 |  | 0 | 0 | 0
| 89 | 0 | 0 | 0 |  | 0 | 0 | 0
| 90 | 0 | 0 | 0 |  | 0 | 0 | 0
| 91 | 0 | 0 | 0 |  | 0 | 0 | 0
| 92 | 0 | 0 | 0 |  | 0 | 0 | 0
| 93 | 0 | 0 | 0 |  | 0 | 0 | 0
| 94 | 0 | 0 | 0 |  | 0 | 0 | 0
| 95 | 0 | 0 | 0 |  | 0 | 0 | 0
| 96 | 0 | 0 | 0 |  | 0 | 0 | 0
| 97 | 0 | 0 | 0 |  | 0 | 0 | 0
| 98 | 0 | 0 | 0 |  | 0 | 0 | 0
| 99 | 0 | 0 | 0 |  | 0 | 0 | 0
| 100 | 0 | 0 | 0 |  | 0 | 0 | 0
| 101 | 0 | 0 | 0 |  | 0 | 0 | 0
| 102 | 0 | 0 | 0 |  | 0 | 0 | 0
| 103 | 0 | 0 | 0 |  | 0 | 0 | 0
| 104 | 0 | 0 | 0 |  | 0 | 0 | 0
| 105 | 0 | 0 | 0 |  | 0 | 0 | 0
| 106 | 0 | 0 | 0 |  | 0 | 0 | 0
| 107 | 0 | 0 | 0 |  | 0 | 0 | 0
| 108 | 0 | 0 | 0 |  | 0 | 0 | 0
| 109 | 0 | 0 | 0 |  | 0 | 0 | 0
| 110 | 0 | 0 | 0 |  | 0 | 0 | 0
| 111 | 0 | 0 | 0 |  | 0 | 0 | 0
| 112 | 0 | 0 | -0.19536 |  | 0 | 0 | 0
| 113 | 0 | 0 | -0.20047 |  | 0 | 0 | 0
| 114 | 0 | 0 | -0.20558 |  | 0 | 0 | 0
| 115 | 0 | 0 | -0.21068 |  | 0 | 0 | 0
| 116 | 0 | 0 | -0.21577 |  | 0 | 0 | 0
| 117 | 0 | 0 | -0.22086 |  | 0 | 0 | 0
| 118 | 0 | 0 | -0.22597 |  | 0 | 0 | 0
| 119 | 0 | 0 | -0.22487 |  | 0 | 0 | 0
| 120 | 0 | 0 | -0.21953 |  | 0 | 0 | 0
| 121 | 0 | 0 | -0.21505 |  | 0 | 0 | 0
| 122 | 0 | 0 | -0.21098 |  | 0 | 0 | 0
| 123 | 0 | 0 | -0.20675 |  | 0 | 0 | 0
| 124 | 0 | 0 | -0.20219 |  | 0 | 0 | 0
| 125 | 0 | 0 | -0.19731 |  | 0 | 0 | 0
| 126 | 0 | 0 | -0.19209 |  | 0 | 0 | 0
| 127 | 0 | 0 | -0.19163 |  | 0 | 0 | 0
| 128 | 0 | 0 | -0.19768 |  | 0 | 0 | 0
| 129 | 0 | 0 | -0.19657 |  | 0 | 0 | 0
| 130 | 0 | 0 | -0.19005 |  | 0 | 0 | 0
| 131 | 0 | 0 | -0.1833 |  | 0 | 0 | 0
| 132 | 0 | 0 | -0.49595 |  | 0 | 0 | 0
| 133 | 0 | 0 | -0.48933 |  | 0 | 0 | 0
| 134 | 0 | 0 | -0.48272 |  | 0 | 0 | 0
| 135 | 0 | 0 | -0.47613 |  | 0 | 0 | 0
| 136 | 0 | 0 | 0 |  | 0 | 0 | 0
| 137 | 0 | 0 | 0 |  | 0 | 0 | 0
| 138 | 0 | 0 | 0 |  | 0 | 0 | 0
| 139 | 0 | 0 | 0 |  | 0 | 0 | 0
| 140 | 0 | 0 | 0 |  | 0 | 0 | 0
| 141 | 0 | 0 | 0 |  | 0 | 0 | 0
| 142 | 0 | 0 | 0 |  | 0 | 0 | 0
| 143 | 0 | 0 | 0 |  | 0.020301 | 0.12658 | 0.056026
| 144 | 0 | 0 | 0 |  | 0.047964 | 0.29907 | 0.13237
| 145 | 0 | 0 | 0 |  | 0.075618 | 0.4715 | 0.20869
| 146 | 0 | 0 | 0 |  | 0.10326 | 0.64386 | 0.28498
| 147 | 0 | 0 | 0 |  | 0.13089 | 0.81613 | 0.36123
| 148 | 0 | 0 | 0 |  | 0.1585 | 0.98831 | 0.43743
| 149 | 0 | 0 | 0 |  | 0.1861 | 1.1604 | 0.51359
| 150 | 0 | 0 | 0 |  | 0.21367 | 1.3323 | 0.58968
| 151 | 0 | 0 | 0 |  | 0.2415 | 1.5058 | 0.6665
| 152 | 0 | 0 | 0 |  | 0.26947 | 1.6802 | 0.74369
| 153 | 0 | 0 | 0 |  | 0.29753 | 1.8552 | 0.82113
| 154 | 0 | 0 | 0 |  | 0.3254 | 2.0289 | 0.89803
| 155 | 0 | 0 | 0 |  | 0.35322 | 2.2025 | 0.97483
| 156 | 0 | 0 | 0 |  | 0.38101 | 2.3757 | 1.0515
| 157 | 0 | 0 | 0 |  | 0.4087 | 2.5483 | 1.1279
| 158 | 0 | 0 | 0 |  | 0.43627 | 2.7203 | 1.204
| 159 | 0 | 0 | 0 |  | 0.46376 | 2.8917 | 1.2799
| 160 | 0 | 0 | 0 |  | 0.49143 | 3.0642 | 1.3563
| 161 | 0 | 0 | 0 |  | 0.51907 | 3.2366 | 1.4325
| 162 | 0 | 0 | 0 |  | 0.54663 | 3.4084 | 1.5086
| 163 | 0 | 0 | 0 |  | 0.57414 | 3.5799 | 1.5845
| 164 | 0 | 0 | 0 |  | 0.60159 | 3.7511 | 1.6603
| 165 | 0 | 0 | -0.13688 |  | 0.6291 | 3.9226 | 1.7362
| 166 | 0 | 0 | -0.14217 |  | 0.6567 | 4.0947 | 1.8124
| 167 | 0 | 0 | -0.1407 |  | 0.6844 | 4.2675 | 1.8888
| 168 | 0 | 0 | -0.13468 |  | 0.71188 | 4.4388 | 1.9647
| 169 | 0 | 0 | -0.12969 |  | 0.73929 | 4.6097 | 2.0403
| 170 | 0 | 0 | -0.12554 |  | 0.76662 | 4.7801 | 2.1157
| 171 | 0 | 0 | -0.12138 |  | 0.79388 | 4.9501 | 2.191
| 172 | 0 | 0 | -0.11694 |  | 0.82106 | 5.1196 | 2.266
| 173 | 0 | 0 | -0.112 |  | 0.84817 | 5.2886 | 2.3408
| 174 | 0 | 0 | 0 |  | 0.87519 | 5.457 | 2.4153
| 175 | 0 | 0 | 0 |  | 0.90241 | 5.6268 | 2.4905
| 176 | 0 | 0 | 0 |  | 0.92971 | 5.797 | 2.5658
| 177 | 0 | 0 | 0 |  | 0.95701 | 5.9673 | 2.6412
| 178 | 0 | 0 | 0 |  | 0.98398 | 6.1354 | 2.7156
| 179 | 0 | 0 | 0 |  | 1.0107 | 6.3023 | 2.7895
| 180 | 0 | 0 | 0 |  | 1.0373 | 6.4677 | 2.8627
| 181 | 0 | 0 | 0 |  | 1.0635 | 6.6314 | 2.9351
| 182 | 0 | 0 | 0 |  | 1.0895 | 6.7932 | 3.0067
| 183 | 0 | 0 | 0 |  | 1.1151 | 6.9532 | 3.0776
| 184 | 0 | 0 | 0 |  | 1.1408 | 7.1133 | 3.1484
| 185 | 0 | 0 | 0 |  | 1.1663 | 7.2719 | 3.2186
| 186 | 0 | 0 | 0 |  | 1.1914 | 7.4287 | 3.288
| 187 | 0 | 0 | 0 |  | 1.2163 | 7.584 | 3.3567
| 188 | 0 | 0 | 0 |  | 1.2409 | 7.7377 | 3.4248
| 189 | 0 | 0 | 0 |  | 1.2653 | 7.8897 | 3.4921
| 190 | 0 | 0 | 0 |  | 1.2895 | 8.0404 | 3.5588
| 191 | 0 | 0 | 0 |  | 1.3136 | 8.1908 | 3.6253
| 192 | 0 | 0 | 0 |  | 1.3375 | 8.3398 | 3.6913
| 193 | 0 | 0 | 0 |  | 1.3614 | 8.4885 | 3.7571
| 194 | 0 | 0 | 0 |  | 1.3851 | 8.6364 | 3.8225
| 195 | 0 | 0 | 0 |  | 1.4087 | 8.7834 | 3.8876
| 196 | 0 | 0 | 0 |  | 1.4321 | 8.9297 | 3.9524
| 197 | 0 | 0 | 0 |  | 1.4554 | 9.0751 | 4.0167
| 198 | 0 | 0 | 0 |  | 1.4786 | 9.2196 | 4.0807
| 199 | 0 | 0 | 0 |  | 1.502 | 9.3652 | 4.1451
| 200 | 0 | 0 | 0 |  | 1.5253 | 9.5109 | 4.2096
| 201 | 0 | 0 | 0 |  | 1.5487 | 9.6565 | 4.2741
| 202 | 0 | 0 | 0 |  | 1.5717 | 9.7999 | 4.3375
| 203 | 0 | 0 | 0 |  | 1.5945 | 9.942 | 4.4004
| 204 | 0 | 0 | 0 |  | 1.617 | 10.0825 | 4.4626
| 205 | 0 | 0 | 0 |  | 1.6393 | 10.2214 | 4.5241
| 206 | 0 | 0 | 0 |  | 1.6612 | 10.3583 | 4.5847
| 207 | 0 | 0 | 0 |  | 1.555 | 9.6961 | 4.2916
| 208 | 0 | 0 | 0 |  | 1.5105 | 9.4183 | 4.1686
| 209 | 0 | 0 | 0 |  | 1.4658 | 9.1396 | 4.0453
| 210 | 0 | 0 | 0 |  | 1.4209 | 8.8599 | 3.9215
| 211 | 0 | 0 | 0 |  | 1.3758 | 8.5787 | 3.797
| 212 | 0 | 0 | 0 |  | 1.3305 | 8.2959 | 3.6719
| 213 | 0 | 0 | 0 |  | 1.2848 | 8.0113 | 3.5459
| 214 | 0 | 0 | 0 |  | 1.239 | 7.7254 | 3.4193
| 215 | 0 | 0 | 0 |  | 1.1931 | 7.4394 | 3.2927
| 216 | 0 | 0 | 0 |  | 1.147 | 7.1519 | 3.1655
| 217 | 0 | 0 | 0 |  | 1.1009 | 6.8644 | 3.0382
| 218 | 0 | 0 | 0 |  | 1.0547 | 6.5763 | 2.9107
| 219 | 0 | 0 | 0 |  | 1.0084 | 6.2876 | 2.783
| 220 | 0 | 0 | 0 |  | 0.96202 | 5.9985 | 2.655
| 221 | 0 | 0 | 0 |  | 0.91556 | 5.7088 | 2.5268
| 222 | 0 | 0 | 0 |  | 0.86903 | 5.4186 | 2.3983
| 223 | 0 | 0 | 0 |  | 0.82273 | 5.1299 | 2.2706
| 224 | 0 | 0 | 0 |  | 0.77653 | 4.8419 | 2.1431
| 225 | 0 | 0 | 0 |  | 0.73039 | 4.5542 | 2.0157
| 226 | 0 | 0 | 0 |  | 0.68395 | 4.2647 | 1.8876
| 227 | 0 | 0 | 0 |  | 0.63737 | 3.9742 | 1.759
| 228 | 0 | 0 | 0 |  | 0.59061 | 3.6826 | 1.63
| 229 | 0 | 0 | 0 |  | 0.54365 | 3.3898 | 1.5004
| 230 | 0 | 0 | 0 |  | 0.49648 | 3.0957 | 1.3702
| 231 | 0 | 0 | 0 |  | 0.44906 | 2.8 | 1.2393
| 232 | 0 | 0 | 0 |  | 0.40174 | 2.505 | 1.1087
| 233 | 0 | 0 | 0 |  | 0.35437 | 2.2096 | 0.97799
| 234 | 0 | 0 | 0 |  | 0.30687 | 1.9134 | 0.84691
| 235 | 0 | 0 | 0 |  | 0.25918 | 1.6161 | 0.71529
| 236 | 0 | 0 | 0 |  | 0.21129 | 1.3174 | 0.58311
| 237 | 0 | 0 | 0 |  | 0.1632 | 1.0176 | 0.45039
| 238 | 0 | 0 | 0 |  | 0.115 | 0.71705 | 0.31737
| 239 | 0 | 0 | 0 |  | 0.066875 | 0.41698 | 0.18456
| 240 | 0 | 0 | 0 |  | 0.018616 | 0.11608 | 0.051377
| 241 | 0 | 0 | 0 |  | 0 | 0 | 0
| 242 | 0 | 0 | 0 |  | 0 | 0 | 0
| 243 | 0 | 0 | 0 |  | 0 | 0 | 0
| 244 | 0 | 0 | 0 |  | 0 | 0 | 0
| 245 | 0 | 0 | 0 |  | 0 | 0 | 0
| 246 | 0 | 0 | 0 |  | 0 | 0 | 0
| 247 | 0 | 0 | 0 |  | 0 | 0 | 0
| 248 | 0 | 0 | 0 |  | 0 | 0 | 0
| 249 | 0 | 0 | 0 |  | 0 | 0 | 0
| 250 | 0 | 0 | 0 |  | 0 | 0 | 0
| 251 | 0 | 0 | 0 |  | 0 | 0 | 0
| 252 | 0 | 0 | 0 |  | 0 | 0 | 0
| 253 | 0 | 0 | 0 |  | 0 | 0 | 0
| 254 | 0 | 0 | 0 |  | 0 | 0 | 0
| 255 | 0 | 0 | 0 |  | 0 | 0 | 0
| 256 | 0 | 0 | 0 |  | 0 | 0 | 0
| 257 | 0 | 0 | 0 |  | 0 | 0 | 0
| 258 | 0 | 0 | -0.022846 |  | 0 | 0 | 0
| 259 | 0 | 0 | -0.028244 |  | 0 | 0 | 0
| 260 | 0 | 0 | -0.033633 |  | 0 | 0 | 0
| 261 | 0 | 0 | -0.039013 |  | 0 | 0 | 0
| 262 | 0 | 0 | -0.044385 |  | 0 | 0 | 0
| 263 | 0 | 0 | -0.043014 |  | 0 | 0 | 0
| 264 | 0 | 0 | -0.037545 |  | 0 | 0 | 0
| 265 | 0 | 0 | -0.0331 |  | 0 | 0 | 0
| 266 | 0 | 0 | -0.029218 |  | 0 | 0 | 0
| 267 | 0 | 0 | -0.025333 |  | 0 | 0 | 0
| 268 | 0 | 0 | -0.02116 |  | 0 | 0 | 0
| 269 | 0 | 0 | -0.016583 |  | 0 | 0 | 0
| 270 | 0 | 0 | -0.011565 |  | 0 | 0 | 0
| 271 | 0 | 0 | -0.01117 |  | 0 | 0 | 0
| 272 | 0 | 0 | -0.017239 |  | 0 | 0 | 0
| 273 | 0 | 0 | -0.022953 |  | 0 | 0 | 0
| 274 | 0 | 0 | -0.028405 |  | 0 | 0 | 0
| 275 | 0 | 0 | -0.033839 |  | 0 | 0 | 0
| 276 | 0 | 0 | -0.039266 |  | 0 | 0 | 0
| 277 | 0 | 0 | -0.044687 |  | 0 | 0 | 0
| 278 | 0 | 0 | -0.050101 |  | 0 | 0 | 0
| 279 | 0 | 0 | -0.055509 |  | 0 | 0 | 0
| 280 | 0 | 0 | -0.060909 |  | 0 | 0 | 0
| 281 | 0 | 0 | -0.066303 |  | 0 | 0 | 0
| 282 | 0 | 0 | -0.071691 |  | 0 | 0 | 0
| 283 | 0 | 0 | -0.077073 |  | 0 | 0 | 0
| 284 | 0 | 0 | -0.082449 |  | 0 | 0 | 0
| 285 | 0 | 0 | -0.087819 |  | 0 | 0 | 0
| 286 | 0 | 0 | -0.093206 |  | 0 | 0 | 0
| 287 | 0 | 0 | -0.092361 |  | 0 | 0 | 0
| 288 | 0 | 0 | -0.087313 |  | 0 | 0 | 0
| 289 | 0 | 0 | -0.083111 |  | 0 | 0 | 0
| 290 | 0 | 0 | -0.079331 |  | 0 | 0 | 0
| 291 | 0 | 0 | -0.075385 |  | 0 | 0 | 0
| 292 | 0 | 0 | -0.071111 |  | 0 | 0 | 0
| 293 | 0 | 0 | -0.066508 |  | 0 | 0 | 0
| 294 | 0 | 0 | -0.061578 |  | 0 | 0 | 0
| 295 | 0 | 0 | -0.061384 |  | 0 | 0 | 0
| 296 | 0 | 0 | -0.067706 |  | 0 | 0 | 0
| 297 | 0 | 0 | -0.06687 |  | 0 | 0 | 0
| 298 | 0 | 0 | -0.060633 |  | 0 | 0 | 0
| 299 | 0 | 0 | -0.37357 |  | 0 | 0 | 0
| 300 | 0 | 0 | -0.36723 |  | 0 | 0 | 0
| 301 | 0 | 0 | -0.36091 |  | 0 | 0 | 0
| 302 | 0 | 0 | -0.3546 |  | 0 | 0 | 0
| 303 | 0 | 0 | 0 |  | 0 | 0 | 0
| 304 | 0 | 0 | 0 |  | 0 | 0 | 0
| 305 | 0 | 0 | 0 |  | 0 | 0 | 0
| 306 | 0 | 0 | 0 |  | 0 | 0 | 0
| 307 | 0 | 0 | 0 |  | 0 | 0 | 0
| 308 | 0 | 0 | 0 |  | 0 | 0 | 0
| 309 | 0 | 0 | 0 |  | 0 | 0 | 0
| 310 | 0 | 0 | -0.059625 |  | 0 | 0 | 0
| 311 | 0 | 0 | -0.059719 |  | 0 | 0 | 0
| 312 | 0 | 0 | -0.05548 |  | 0 | 0 | 0
| 313 | 0 | 0 | -0.05152 |  | 0 | 0 | 0
| 314 | 0 | 0 | -0.047698 |  | 0 | 0 | 0
| 315 | 0 | 0 | -0.043732 |  | 0 | 0 | 0
| 316 | 0 | 0 | -0.039477 |  | 0 | 0 | 0
| 317 | 0 | 0 | -0.034936 |  | 0 | 0 | 0
| 318 | 0 | 0 | 0 |  | 0 | 0 | 0
| 319 | 0 | 0 | 0 |  | 0 | 0 | 0
| 320 | 0 | 0 | 0 |  | 0 | 0 | 0
| 321 | 0 | 0 | 0 |  | 0 | 0 | 0
| 322 | 0 | 0 | 0 |  | 0 | 0 | 0
| 323 | 0 | 0 | 0 |  | 0 | 0 | 0
| 324 | 0 | 0 | 0 |  | 0 | 0 | 0
| 325 | 0 | 0 | 0 |  | 0 | 0 | 0
| 326 | 0 | 0 | 0 |  | 0 | 0 | 0
| 327 | 0 | 0 | 0 |  | 0 | 0 | 0
| 328 | 0 | 0 | 0 |  | 0 | 0 | 0
| 329 | 0 | 0 | 0 |  | 0 | 0 | 0
| 330 | 0 | 0 | 0 |  | 0.020574 | 0.12828 | 0.05678
| 331 | 0 | 0 | 0 |  | 0.049041 | 0.30578 | 0.13534
| 332 | 0 | 0 | 0 |  | 0.077501 | 0.48324 | 0.21389
| 333 | 0 | 0 | 0 |  | 0.10605 | 0.66128 | 0.29269
| 334 | 0 | 0 | 0 |  | 0.13474 | 0.84015 | 0.37186
| 335 | 0 | 0 | 0 |  | 0.16358 | 1.0199 | 0.45144
| 336 | 0 | 0 | 0 |  | 0.19224 | 1.1987 | 0.53054
| 337 | 0 | 0 | 0 |  | 0.22088 | 1.3772 | 0.60958
| 338 | 0 | 0 | 0 |  | 0.24949 | 1.5557 | 0.68855
| 339 | 0 | 0 | 0 |  | 0.27808 | 1.7339 | 0.76744
| 340 | 0 | 0 | 0 |  | 0.30664 | 1.912 | 0.84626
| 341 | 0 | 0 | 0 |  | 0.33516 | 2.0898 | 0.92498
| 342 | 0 | 0 | 0 |  | 0.36365 | 2.2675 | 1.0036
| 343 | 0 | 0 | 0 |  | 0.39239 | 2.4466 | 1.0829
| 344 | 0 | 0 | 0 |  | 0.42124 | 2.6266 | 1.1625
| 345 | 0 | 0 | 0 |  | 0.45014 | 2.8068 | 1.2423
| 346 | 0 | 0 | 0 |  | 0.47875 | 2.9851 | 1.3213
| 347 | 0 | 0 | 0 |  | 0.5072 | 3.1625 | 1.3998
| 348 | 0 | 0 | 0 |  | 0.53545 | 3.3387 | 1.4777
| 349 | 0 | 0 | 0 |  | 0.56348 | 3.5135 | 1.5551
| 350 | 0 | 0 | 0 |  | 0.59125 | 3.6866 | 1.6317
| 351 | 0 | 0 | 0 |  | 0.61878 | 3.8583 | 1.7077
| 352 | 0 | 0 | 0 |  | 0.64636 | 4.0303 | 1.7838
| 353 | 0 | 0 | 0 |  | 0.67374 | 4.201 | 1.8594
| 354 | 0 | 0 | 0 |  | 0.70087 | 4.3701 | 1.9343
| 355 | 0 | 0 | 0 |  | 0.72779 | 4.538 | 2.0086
| 356 | 0 | 0 | 0 |  | 0.7545 | 4.7045 | 2.0823
| 357 | 0 | 0 | 0 |  | 0.781 | 4.8697 | 2.1554
| 358 | 0 | 0 | 0 |  | 0.8073 | 5.0338 | 2.228
| 359 | 0 | 0 | 0 |  | 0.83362 | 5.1978 | 2.3006
| 360 | 0 | 0 | 0 |  | 0.85973 | 5.3607 | 2.3727
| 361 | 0 | 0 | 0 |  | 0.88585 | 5.5235 | 2.4448
| 362 | 0 | 0 | 0 |  | 0.91189 | 5.6859 | 2.5166
| 363 | 0 | 0 | 0 |  | 0.93784 | 5.8477 | 2.5882
| 364 | 0 | 0 | 0 |  | 0.96369 | 6.0089 | 2.6596
| 365 | 0 | 0 | 0 |  | 0.98946 | 6.1696 | 2.7307
| 366 | 0 | 0 | 0 |  | 1.0151 | 6.3297 | 2.8016
| 367 | 0 | 0 | 0 |  | 1.041 | 6.4909 | 2.873
| 368 | 0 | 0 | 0 |  | 1.0669 | 6.6526 | 2.9445
| 369 | 0 | 0 | 0 |  | 1.0929 | 6.8144 | 3.0161
| 370 | 0 | 0 | 0 |  | 1.1185 | 6.9743 | 3.0869
| 371 | 0 | 0 | 0 |  | 1.144 | 7.1331 | 3.1572
| 372 | 0 | 0 | 0 |  | 1.1692 | 7.2906 | 3.2269
| 373 | 0 | 0 | 0 |  | 1.1943 | 7.4466 | 3.296
| 374 | 0 | 0 | 0 |  | 1.219 | 7.601 | 3.3643
| 375 | 0 | 0 | 0 |  | 1.2435 | 7.7535 | 3.4318
| 376 | 0 | 0 | 0 |  | 1.2679 | 7.9059 | 3.4992
| 377 | 0 | 0 | 0 |  | 1.2922 | 8.0574 | 3.5663
| 378 | 0 | 0 | 0 |  | 1.3164 | 8.2079 | 3.6329
| 379 | 0 | 0 | 0 |  | 1.3402 | 8.3568 | 3.6988
| 380 | 0 | 0 | 0 |  | 1.3639 | 8.5041 | 3.764
| 381 | 0 | 0 | 0 |  | 1.3872 | 8.6495 | 3.8284
| 382 | 0 | 0 | 0 |  | 1.4103 | 8.7934 | 3.892
| 383 | 0 | 0 | 0 |  | 1.4333 | 8.9369 | 3.9556
| 384 | 0 | 0 | 0 |  | 1.456 | 9.0789 | 4.0184
| 385 | 0 | 0 | 0 |  | 1.4788 | 9.2205 | 4.0811
| 386 | 0 | 0 | 0 |  | 1.5013 | 9.3613 | 4.1434
| 387 | 0 | 0 | 0 |  | 1.5238 | 9.5012 | 4.2053
| 388 | 0 | 0 | 0 |  | 1.5461 | 9.6403 | 4.2669
| 389 | 0 | 0 | 0 |  | 1.5682 | 9.7784 | 4.328
| 390 | 0 | 0 | 0 |  | 1.5902 | 9.9156 | 4.3887
| 391 | 0 | 0 | 0 |  | 1.6124 | 10.0537 | 4.4499
| 392 | 0 | 0 | 0 |  | 1.6346 | 10.192 | 4.5111
| 393 | 0 | 0 | 0 |  | 1.6567 | 10.33 | 4.5722
| 394 | 0 | 0 | 0 |  | 1.6784 | 10.4656 | 4.6322
| 395 | 0 | 0 | 0 |  | 1.6999 | 10.5996 | 4.6915
| 396 | 0 | 0 | 0 |  | 1.7211 | 10.7318 | 4.75
| 397 | 0 | 0 | 0 |  | 1.742 | 10.8621 | 4.8077
| 398 | 0 | 0 | 0 |  | 1.7626 | 10.9903 | 4.8644
| 399 | 0 | 0 | 0 |  | 1.7828 | 11.1162 | 4.9201
| 400 | 0 | 0 | 0 |  | 1.8029 | 11.2417 | 4.9757
| 401 | 0 | 0 | 0 |  | 1.8229 | 11.3661 | 5.0308
| 402 | 0 | 0 | 0 |  | 1.8425 | 11.4888 | 5.0851
| 403 | 0 | 0 | 0 |  | 1.7076 | 10.6473 | 4.7126
| 404 | 0 | 0 | 0 |  | 1.6604 | 10.3533 | 4.5825
| 405 | 0 | 0 | 0 |  | 1.613 | 10.0572 | 4.4514
| 406 | 0 | 0 | 0 |  | 1.5652 | 9.7596 | 4.3197
| 407 | 0 | 0 | 0 |  | 1.5174 | 9.4616 | 4.1878
| 408 | 0 | 0 | 0 |  | 1.4694 | 9.162 | 4.0552
| 409 | 0 | 0 | 0 |  | 1.4213 | 8.8621 | 3.9225
| 410 | 0 | 0 | 0 |  | 1.3731 | 8.5616 | 3.7894
| 411 | 0 | 0 | 0 |  | 1.3248 | 8.2603 | 3.6561
| 412 | 0 | 0 | 0 |  | 1.2763 | 7.9583 | 3.5224
| 413 | 0 | 0 | 0 |  | 1.2278 | 7.6556 | 3.3885
| 414 | 0 | 0 | 0 |  | 1.1791 | 7.3523 | 3.2542
| 415 | 0 | 0 | 0 |  | 1.1307 | 7.0503 | 3.1205
| 416 | 0 | 0 | 0 |  | 1.0823 | 6.7487 | 2.9871
| 417 | 0 | 0 | 0 |  | 1.034 | 6.4476 | 2.8538
| 418 | 0 | 0 | 0 |  | 0.98577 | 6.1466 | 2.7205
| 419 | 0 | 0 | 0 |  | 0.93748 | 5.8455 | 2.5873
| 420 | 0 | 0 | 0 |  | 0.88917 | 5.5442 | 2.4539
| 421 | 0 | 0 | 0 |  | 0.84081 | 5.2427 | 2.3205
| 422 | 0 | 0 | 0 |  | 0.79238 | 4.9407 | 2.1868
| 423 | 0 | 0 | 0 |  | 0.7439 | 4.6385 | 2.053
| 424 | 0 | 0 | 0 |  | 0.69538 | 4.3359 | 1.9191
| 425 | 0 | 0 | 0 |  | 0.64672 | 4.0325 | 1.7848
| 426 | 0 | 0 | 0 |  | 0.59787 | 3.7279 | 1.65
| 427 | 0 | 0 | 0 |  | 0.54892 | 3.4227 | 1.5149
| 428 | 0 | 0 | 0 |  | 0.49997 | 3.1175 | 1.3798
| 429 | 0 | 0 | 0 |  | 0.4511 | 2.8128 | 1.245
| 430 | 0 | 0 | 0 |  | 0.40236 | 2.5089 | 1.1104
| 431 | 0 | 0 | 0 |  | 0.35378 | 2.2059 | 0.97637
| 432 | 0 | 0 | 0 |  | 0.30501 | 1.9018 | 0.84176
| 433 | 0 | 0 | 0 |  | 0.25621 | 1.5976 | 0.7071
| 434 | 0 | 0 | 0 |  | 0.2074 | 1.2932 | 0.57239
| 435 | 0 | 0 | 0 |  | 0.15858 | 0.98879 | 0.43765
| 436 | 0 | 0 | 0 |  | 0.10975 | 0.68433 | 0.30289
| 437 | 0 | 0 | 0 |  | 0.06092 | 0.37985 | 0.16813
| 438 | 0 | 0 | 0 |  | 0.012091 | 0.075392 | 0.033369
| 439 | 0 | 0 | 0 |  | 0 | 0 | 0
| 440 | 0 | 0 | 0 |  | 0 | 0 | 0
| 441 | 0 | 0 | 0 |  | 0 | 0 | 0
| 442 | 0 | 0 | 0 |  | 0 | 0 | 0
| 443 | 0 | 0 | 0 |  | 0 | 0 | 0
| 444 | 0 | 0 | 0 |  | 0 | 0 | 0
| 445 | 0 | 0 | 0 |  | 0 | 0 | 0
| 446 | 0 | 0 | 0 |  | 0 | 0 | 0
| 447 | 0 | 0 | 0 |  | 0 | 0 | 0
| 448 | 0 | 0 | 0 |  | 0 | 0 | 0
| 449 | 0 | 0 | 0 |  | 0 | 0 | 0
| 450 | 0 | 0 | 0 |  | 0 | 0 | 0
| 451 | 0 | 0 | 0 |  | 0 | 0 | 0
| 452 | 0 | 0 | 0 |  | 0 | 0 | 0
| 453 | 0 | 0 | 0 |  | 0 | 0 | 0
| 454 | 0 | 0 | -0.0046943 |  | 0 | 0 | 0
| 455 | 0 | 0 | -0.0039733 |  | 0 | 0 | 0
| 456 | 0 | 0 | 0 |  | 0 | 0 | 0
| 457 | 0 | 0 | 0 |  | 0 | 0 | 0
| 458 | 0 | 0 | 0 |  | 0 | 0 | 0
| 459 | 0 | 0 | 0 |  | 0 | 0 | 0
| 460 | 0 | 0 | 0 |  | 0 | 0 | 0
| 461 | 0 | 0 | 0 |  | 0 | 0 | 0
| 462 | 0 | 0 | 0 |  | 0 | 0 | 0
| 463 | 0 | 0 | 0 |  | 0 | 0 | 0
| 464 | 0 | 0 | 0 |  | 0 | 0 | 0
| 465 | 0 | 0 | 0 |  | 0 | 0 | 0
| 466 | 0 | 0 | 0 |  | 0 | 0 | 0
| 467 | 0 | 0 | -0.28737 |  | 0 | 0 | 0
| 468 | 0 | 0 | -0.28124 |  | 0 | 0 | 0
| 469 | 0 | 0 | -0.27512 |  | 0 | 0 | 0
| 470 | 0 | 0 | -0.26902 |  | 0 | 0 | 0
| 471 | 0 | 0 | 0 |  | 0 | 0 | 0
| 472 | 0 | 0 | 0 |  | 0 | 0 | 0
| 473 | 0 | 0 | 0 |  | 0 | 0 | 0
| 474 | 0 | 0 | 0 |  | 0 | 0 | 0
| 475 | 0 | 0 | 0 |  | 0 | 0 | 0
| 476 | 0 | 0 | 0 |  | 0 | 0 | 0
| 477 | 0 | 0 | 0 |  | 0 | 0 | 0
| 478 | 0 | 0 | 0 |  | 0 | 0 | 0
| 479 | 0 | 0 | 0 |  | 0 | 0 | 0
| 480 | 0 | 0 | 0 |  | 0 | 0 | 0
| 481 | 0 | 0 | 0 |  | 0 | 0 | 0
| 482 | 0 | 0 | 0 |  | 0 | 0 | 0
| 483 | 0 | 0 | 0 |  | 0 | 0 | 0
| 484 | 0 | 0 | 0 |  | 0 | 0 | 0
| 485 | 0 | 0 | 0 |  | 0 | 0 | 0
| 486 | 0 | 0 | 0 |  | 0 | 0 | 0
| 487 | 0 | 0 | 0 |  | 0 | 0 | 0
| 488 | 0 | 0 | 0 |  | 0 | 0 | 0
| 489 | 0 | 0 | 0 |  | 0 | 0 | 0
| 490 | 0 | 0 | 0 |  | 0 | 0 | 0
| 491 | 0 | 0 | 0 |  | 0 | 0 | 0
| 492 | 0 | 0 | 0 |  | 0 | 0 | 0
| 493 | 0 | 0 | 0 |  | 0 | 0 | 0
| 494 | 0 | 0 | 0 |  | 0 | 0 | 0
| 495 | 0 | 0 | 0 |  | 0 | 0 | 0
| 496 | 0 | 0 | 0 |  | 0 | 0 | 0
| 497 | 0 | 0 | 0 |  | 0 | 0 | 0
| 498 | 0 | 0 | 0 |  | 0 | 0 | 0
| 499 | 0 | 0 | 0 |  | 0 | 0 | 0
| 500 | 0 | 0 | 0 |  | 0 | 0 | 0
| 501 | 0 | 0 | 0 |  | 0 | 0 | 0
| 502 | 0 | 0 | 0 |  | 0 | 0 | 0
| 503 | 0 | 0 | 0 |  | 0 | 0 | 0
| 504 | 0 | 0 | 0 |  | 0 | 0 | 0
| 505 | 0 | 0 | 0 |  | 0 | 0 | 0
| 506 | 0 | 0 | 0 |  | 0 | 0 | 0
| 507 | 0 | 0 | 0 |  | 0 | 0 | 0
| 508 | 0 | 0 | 0 |  | 0 | 0 | 0
| 509 | 0 | 0 | 0 |  | 0 | 0 | 0
| 510 | 0 | 0 | 0 |  | 0 | 0 | 0
| 511 | 0 | 0 | 0 |  | 0 | 0 | 0
| 512 | 0 | 0 | 0 |  | 0 | 0 | 0
| 513 | 0 | 0 | 0 |  | 0 | 0 | 0
| 514 | 0 | 0 | 0 |  | 0 | 0 | 0
| 515 | 0 | 0 | 0 |  | 0 | 0 | 0
| 516 | 0 | 0 | 0 |  | 0 | 0 | 0
| 517 | 0 | 0 | 0 |  | 0 | 0 | 0
| 518 | 0 | 0 | 0 |  | 0 | 0 | 0
| 519 | 0 | 0 | 0 |  | 0 | 0 | 0
| 520 | 0 | 0 | 0 |  | 0 | 0 | 0
| 521 | 0 | 0 | 0 |  | 0 | 0 | 0
| 522 | 0 | 0 | 0 |  | 0 | 0 | 0
| 523 | 0 | 0 | 0 |  | 0 | 0 | 0
| 524 | 0 | 0 | 0 |  | 0 | 0 | 0
| 525 | 0 | 0 | 0 |  | 0 | 0 | 0
| 526 | 0 | 0 | 0 |  | 0 | 0 | 0
| 527 | 0 | 0 | 0 |  | 0 | 0 | 0
| 528 | 0 | 0 | 0 |  | 0 | 0 | 0
| 529 | 0 | 0 | 0 |  | 0.0067035 | 0.041798 | 0.0185
| 530 | 0 | 0 | 0 |  | 0.032967 | 0.20556 | 0.090982
| 531 | 0 | 0 | 0 |  | 0.059223 | 0.36927 | 0.16344
| 532 | 0 | 0 | 0 |  | 0.08547 | 0.53293 | 0.23588
| 533 | 0 | 0 | 0 |  | 0.1117 | 0.69651 | 0.30828
| 534 | 0 | 0 | 0 |  | 0.13792 | 0.86 | 0.38065
| 535 | 0 | 0 | 0 |  | 0.16442 | 1.0252 | 0.45376
| 536 | 0 | 0 | 0 |  | 0.19105 | 1.1913 | 0.52727
| 537 | 0 | 0 | 0 |  | 0.21779 | 1.358 | 0.60106
| 538 | 0 | 0 | 0 |  | 0.24432 | 1.5234 | 0.67426
| 539 | 0 | 0 | 0 |  | 0.27074 | 1.6882 | 0.7472
| 540 | 0 | 0 | 0 |  | 0.29705 | 1.8522 | 0.81979
| 541 | 0 | 0 | 0 |  | 0.3232 | 2.0152 | 0.89197
| 542 | 0 | 0 | 0 |  | 0.34917 | 2.1772 | 0.96364
| 543 | 0 | 0 | 0 |  | 0.37493 | 2.3378 | 1.0347
| 544 | 0 | 0 | 0 |  | 0.40075 | 2.4988 | 1.106
| 545 | 0 | 0 | 0 |  | 0.42651 | 2.6594 | 1.1771
| 546 | 0 | 0 | 0 |  | 0.45219 | 2.8195 | 1.248
| 547 | 0 | 0 | 0 |  | 0.47771 | 2.9786 | 1.3184
| 548 | 0 | 0 | 0 |  | 0.50304 | 3.1366 | 1.3883
| 549 | 0 | 0 | 0 |  | 0.52814 | 3.2931 | 1.4576
| 550 | 0 | 0 | 0 |  | 0.55308 | 3.4486 | 1.5264
| 551 | 0 | 0 | 0 |  | 0.57805 | 3.6043 | 1.5953
| 552 | 0 | 0 | 0 |  | 0.60285 | 3.759 | 1.6638
| 553 | 0 | 0 | 0 |  | 0.62768 | 3.9138 | 1.7323
| 554 | 0 | 0 | 0 |  | 0.65245 | 4.0682 | 1.8006
| 555 | 0 | 0 | 0 |  | 0.67715 | 4.2223 | 1.8688
| 556 | 0 | 0 | 0 |  | 0.70179 | 4.3759 | 1.9368
| 557 | 0 | 0 | 0 |  | 0.72636 | 4.5291 | 2.0046
| 558 | 0 | 0 | 0 |  | 0.75086 | 4.6818 | 2.0722
| 559 | 0 | 0 | 0 |  | 0.77558 | 4.836 | 2.1405
| 560 | 0 | 0 | 0 |  | 0.80039 | 4.9907 | 2.2089
| 561 | 0 | 0 | 0 |  | 0.82525 | 5.1457 | 2.2775
| 562 | 0 | 0 | 0 |  | 0.84979 | 5.2987 | 2.3453
| 563 | 0 | 0 | 0 |  | 0.87417 | 5.4507 | 2.4125
| 564 | 0 | 0 | 0 |  | 0.89835 | 5.6015 | 2.4793
| 565 | 0 | 0 | 0 |  | 0.92229 | 5.7507 | 2.5453
| 566 | 0 | 0 | 0 |  | 0.94597 | 5.8984 | 2.6107
| 567 | 0 | 0 | 0 |  | 0.96936 | 6.0443 | 2.6752
| 568 | 0 | 0 | 0 |  | 0.99278 | 6.1903 | 2.7399
| 569 | 0 | 0 | 0 |  | 1.0161 | 6.3356 | 2.8042
| 570 | 0 | 0 | 0 |  | 1.0392 | 6.4796 | 2.8679
| 571 | 0 | 0 | 0 |  | 1.062 | 6.6219 | 2.9309
| 572 | 0 | 0 | 0 |  | 1.0845 | 6.7624 | 2.9931
| 573 | 0 | 0 | 0 |  | 1.1068 | 6.9012 | 3.0545
| 574 | 0 | 0 | 0 |  | 1.1288 | 7.0386 | 3.1153
| 575 | 0 | 0 | 0 |  | 1.1508 | 7.1758 | 3.1761
| 576 | 0 | 0 | 0 |  | 1.1726 | 7.3116 | 3.2362
| 577 | 0 | 0 | 0 |  | 1.1944 | 7.4473 | 3.2962
| 578 | 0 | 0 | 0 |  | 1.216 | 7.5823 | 3.356
| 579 | 0 | 0 | 0 |  | 1.2376 | 7.7165 | 3.4154
| 580 | 0 | 0 | 0 |  | 1.259 | 7.8501 | 3.4745
| 581 | 0 | 0 | 0 |  | 1.2803 | 7.9829 | 3.5333
| 582 | 0 | 0 | 0 |  | 1.3015 | 8.115 | 3.5918
| 583 | 0 | 0 | 0 |  | 1.3228 | 8.2482 | 3.6507
| 584 | 0 | 0 | 0 |  | 1.3442 | 8.3816 | 3.7098
| 585 | 0 | 0 | 0 |  | 1.3656 | 8.5152 | 3.7689
| 586 | 0 | 0 | 0 |  | 1.3871 | 8.6487 | 3.828
| 587 | 0 | 0 | 0 |  | 1.4084 | 8.7819 | 3.887
| 588 | 0 | 0 | 0 |  | 1.4297 | 8.9146 | 3.9457
| 589 | 0 | 0 | 0 |  | 1.4509 | 9.0466 | 4.0041
| 590 | 0 | 0 | 0 |  | 1.4719 | 9.1777 | 4.0621
| 591 | 0 | 0 | 0 |  | 1.4928 | 9.3081 | 4.1199
| 592 | 0 | 0 | 0 |  | 1.5136 | 9.4378 | 4.1773
| 593 | 0 | 0 | 0 |  | 1.5342 | 9.566 | 4.234
| 594 | 0 | 0 | 0 |  | 1.5545 | 9.6925 | 4.29
| 595 | 0 | 0 | 0 |  | 1.5745 | 9.8177 | 4.3454
| 596 | 0 | 0 | 0 |  | 1.5945 | 9.9424 | 4.4006
| 597 | 0 | 0 | 0 |  | 1.6145 | 10.0668 | 4.4556
| 598 | 0 | 0 | 0 |  | 1.6344 | 10.1912 | 4.5107
| 599 | 0 | 0 | 0 |  | 1.6544 | 10.3159 | 4.5659
| 600 | 0 | 0 | 0 |  | 1.5595 | 9.724 | 4.304
| 601 | 0 | 0 | 0 |  | 1.5129 | 9.4334 | 4.1753
| 602 | 0 | 0 | 0 |  | 1.4662 | 9.1419 | 4.0463
| 603 | 0 | 0 | 0 |  | 1.4193 | 8.8496 | 3.9169
| 604 | 0 | 0 | 0 |  | 1.3723 | 8.5566 | 3.7872
| 605 | 0 | 0 | 0 |  | 1.3252 | 8.2628 | 3.6572
| 606 | 0 | 0 | 0 |  | 1.2779 | 7.9683 | 3.5268
| 607 | 0 | 0 | 0 |  | 1.2309 | 7.675 | 3.3971
| 608 | 0 | 0 | 0 |  | 1.1839 | 7.3822 | 3.2674
| 609 | 0 | 0 | 0 |  | 1.137 | 7.0897 | 3.138
| 610 | 0 | 0 | 0 |  | 1.0902 | 6.7975 | 3.0086
| 611 | 0 | 0 | 0 |  | 1.0433 | 6.5054 | 2.8793
| 612 | 0 | 0 | 0 |  | 0.99644 | 6.2131 | 2.75
| 613 | 0 | 0 | 0 |  | 0.94954 | 5.9206 | 2.6205
| 614 | 0 | 0 | 0 |  | 0.90261 | 5.6281 | 2.491
| 615 | 0 | 0 | 0 |  | 0.85572 | 5.3356 | 2.3616
| 616 | 0 | 0 | 0 |  | 0.80886 | 5.0435 | 2.2323
| 617 | 0 | 0 | 0 |  | 0.76205 | 4.7516 | 2.1031
| 618 | 0 | 0 | 0 |  | 0.71532 | 4.4603 | 1.9742
| 619 | 0 | 0 | 0 |  | 0.66868 | 4.1694 | 1.8454
| 620 | 0 | 0 | 0 |  | 0.62214 | 3.8793 | 1.717
| 621 | 0 | 0 | 0 |  | 0.57567 | 3.5895 | 1.5887
| 622 | 0 | 0 | 0 |  | 0.5293 | 3.3003 | 1.4608
| 623 | 0 | 0 | 0 |  | 0.48304 | 3.0119 | 1.3331
| 624 | 0 | 0 | 0 |  | 0.43656 | 2.7221 | 1.2048
| 625 | 0 | 0 | 0 |  | 0.39005 | 2.4321 | 1.0765
| 626 | 0 | 0 | 0 |  | 0.34351 | 2.1419 | 0.94801
| 627 | 0 | 0 | 0 |  | 0.29694 | 1.8515 | 0.8195
| 628 | 0 | 0 | 0 |  | 0.25036 | 1.5611 | 0.69094
| 629 | 0 | 0 | 0 |  | 0.20376 | 1.2705 | 0.56234
| 630 | 0 | 0 | 0 |  | 0.15715 | 0.97988 | 0.4337
| 631 | 0 | 0 | 0 |  | 0.11084 | 0.69112 | 0.3059
| 632 | 0 | 0 | 0 |  | 0.064699 | 0.40342 | 0.17856
| 633 | 0 | 0 | 0 |  | 0.018689 | 0.11653 | 0.051579
| 634 | 0 | 0 | 0 |  | 0 | 0 | 0
| 635 | 0 | 0 | -0.23505 |  | 0 | 0 | 0
| 636 | 0 | 0 | -0.22906 |  | 0 | 0 | 0
| 637 | 0 | 0 | -0.22307 |  | 0 | 0 | 0
| 638 | 0 | 0 | -0.2171 |  | 0 | 0 | 0
| 639 | 0 | 0 | -0.21114 |  | 0 | 0 | 0
| 640 | 0 | 0 | -0.21016 |  | 0 | 0 | 0
| 641 | 0 | 0 | -0.21598 |  | 0 | 0 | 0
| 642 | 0 | 0 | -0.2218 |  | 0 | 0 | 0
| 643 | 0 | 0 | -0.22761 |  | 0 | 0 | 0
| 644 | 0 | 0 | -0.2334 |  | 0 | 0 | 0
| 645 | 0 | 0 | -0.23938 |  | 0 | 0 | 0
| 646 | 0 | 0 | -0.2458 |  | 0 | 0 | 0
| 647 | 0 | 0 | -0.24626 |  | 0 | 0 | 0
| 648 | 0 | 0 | -0.24249 |  | 0 | 0 | 0
| 649 | 0 | 0 | -0.239 |  | 0 | 0 | 0
| 650 | 0 | 0 | -0.23564 |  | 0 | 0 | 0
| 651 | 0 | 0 | -0.23214 |  | 0 | 0 | 0
| 652 | 0 | 0 | -0.22835 |  | 0 | 0 | 0
| 653 | 0 | 0 | -0.22426 |  | 0 | 0 | 0
| 654 | 0 | 0 | -0.21989 |  | 0 | 0 | 0
| 655 | 0 | 0 | -0.22023 |  | 0 | 0 | 0
| 656 | 0 | 0 | -0.2271 |  | 0 | 0 | 0
| 657 | 0 | 0 | -0.22687 |  | 0 | 0 | 0
| 658 | 0 | 0 | -0.22135 |  | 0 | 0 | 0
| 659 | 0 | 0 | 0 |  | 0 | 0 | 0
| 660 | 0 | 0 | 0 |  | 0 | 0 | 0
| 661 | 0 | 0 | 0 |  | 0 | 0 | 0
| 662 | 0 | 0 | 0 |  | 0 | 0 | 0
| 663 | 0 | 0 | 0 |  | 0 | 0 | 0
| 664 | 0 | 0 | 0 |  | 0 | 0 | 0
| 665 | 0 | 0 | 0 |  | 0 | 0 | 0
| 666 | 0 | 0 | 0 |  | 0 | 0 | 0
| 667 | 0 | 0 | 0 |  | 0 | 0 | 0
| 668 | 0 | 0 | 0 |  | 0 | 0 | 0
| 669 | 0 | 0 | 0 |  | 0 | 0 | 0
| 670 | 0 | 0 | 0 |  | 0 | 0 | 0
| 671 | 0 | 0 | 0 |  | 0 | 0 | 0
| 672 | 0 | 0 | 0 |  | 0 | 0 | 0
| Total | 0 | 0 | -17.7514 | 0 | 274.7886 | 1713.3877 | 758.3626 | 0