## DC Chiller Comparison
| Edes (MWh) |  |  |  | Exergy Destruction per 672 h, Edes (MWh)
| Winter | Spring/autumn | Summer |  | Winter | Spring/autumn | Summer |  | Winter | Spring/autumn | Summer
Heat Network |  |  |  | Heat Network |  |  |  | Heat Network
DC condenser heat transfer |  |  |  | DC condenser heat transfer |  |  |  | DC condenser heat transfer
Hot | 41.7 | 39.8 | 36.5 | Hot | 41.7 | 39.8 | 36.5 | Hot | 6.435% | 7.327% | 8.947%
Cold | 13.2 | 25 | 40.1 | Cold | 13.2 | 25 | 40.1 | Cold | 2.037% | 4.603% | 9.829%
Sink mixing |  |  |  | Sink |  |  |  | Sink
Hot | 284 | 222 | 161 | Hot mixing | 184.6185 | 176.223 | 161.4254 | Hot mixing | 28.49% | 32.44% | 39.57%
Cold | 31 | 49 | 68 | Cold mixing | 21.9768 | 41.4731 | 66.6028 | Cold mixing | 3.391% | 7.635% | 16.33%
|  |  |  | Sink cooling* | 43.1667 | 82.668 | 79.3422 | Sink cooling* | 6.661% | 15.22% | 19.45%
WSHP |  |  |  | WSHP |  |  |  | WSHP
Hot | 301 | 139 | 0 | Hot | 301 | 139 | 0 | Hot | 46.45% | 25.59% | 0%
Cold | 39 | 39 | 24 | Cold | 39 | 39 | 24 | Cold | 6.018% | 7.18% | 5.883%
Large-scale ASHP |  |  |  | Large-scale ASHP |  |  |  | Large-scale ASHP
Hot | 0.6 | 0 | 0 | Hot (Qh) | 0.6 | 0 | 0 | Hot (Qh) | 0.09258% | 0% | 0%
Cold | 2.8 | 0 | 0 | Cold (Qc) | 2.8 | 0 | 0 | Cold (Qc) | 0.4321% | 0% | 0%
Total | 713.3 | 513.8 | 329.6 | Total | 648.062 | 543.1641 | 407.9704 | Total | 100% | 100% | 100%
Counterfactual |  |  |  | Counterfactual
Individual ASHP | 936.6 | 299.51 | 48.07 | Individual ASHP | 936.6 | 299.51 | 48.07 | Counterfactual
DC chiller | 0 | 0 | 0 | DC chiller | 194.315 | 129.6685 | 93.0903 | Individual ASHP | 82.82% | 69.79% | 34.05%
Total | 936.6 | 299.51 | 48.07 | Total | 1130.915 | 429.1785 | 141.1603 | DC chiller | 17.18% | 30.21% | 65.95%
[8 empty] | Total | 100% | 100% | 100%
% Change | 23.84% | -71.55% | -585.7% | % Change | 42.7% | -26.56% | -189%
|  |  |  | * Sink cooling represents the exergy destruction associated with the 'unutilsed' DC chiller condenser heat |  |  |  | * Sink cooling represents the exergy destruction associated with the 'unutilsed' DC chiller condenser heat