## Winter
[13 empty] | ºC | K
T0 | K | 273 | [9 empty] | T2/T1 | 1.4 | 0.97342
cp water | kJ/kg.K | 4.18 | [9 empty] | LN | 0.33647 | -0.026938
Tcond.sat | ºC | 30 | [9 empty] | T0 | 91.8569 | -7.354
T evap.sat | ºC | 5 | [9 empty] | T2-T1 | 8 | -8
Thot sink | ºC | 20 | 293 | K | [9 empty] | -0.64602
Tcold sink | ºC | 10 | 283 | K | Approach Temp | [7 empty] | 315.5625 | -203.8597
Tcond.hot, out | ºC | 28 | 301 | K | 2 | K
Thp.hot, out | ºC | 10 | 283 | K | 5 | K
Tcond.cold, out | ºC | 25 | 298 | K | 5 | K
Thp.cold, out | ºC | 7 | 280 | K | 2 | K
Winter
|  |  | Hot Sink | [5 empty] | Cold Sink
|  |  | Condenser |  |  | HP Evaporator |  |  | Condenser |  |  | HP Evaporator |  |  | total Ex dest
|  |  | Qcond, hot | ṁcond, hot | Edest cond, hot | Qhp, hot | ṁhp, hot | Edest hp, hot | Qcond, cold | ṁcond, cold | Edest cond, cold | Qhp, cold | ṁhp, cold | Edest hp, hot
|  |  | kW | kg/s | kW | kW | kg/s | kW | kW | kg/s | kW | kW | kg/s | kW
|  | Total | 2286226.9586 |  | 184618.5382 | 1909080.9577 |  | 99249.4526 | 339293.6997 |  | 20368.5074 | 346237.4417 |  | 10451.5937 | 314688.0919
Hours
| 31.5563 | 1 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 3 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 4 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 5 | 3044.25 | 91.0362 | 245.8308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 6 | 3267 | 97.6974 | 263.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 7 | 3489.75 | 104.3586 | 281.806 | 6195.2581 | 148.2119 | 322.0796 | 0 | 0 | 0 | 1127.2042 | 89.8887 | 34.026
|  | 8 | 3712.5 | 111.0197 | 299.7936 | 6196.777 | 148.2483 | 322.1585 | 0 | 0 | 0 | 1125.6854 | 89.7676 | 33.9802
|  | 9 | 3732.6611 | 111.6226 | 301.4217 | 0 | 0 | 0 | 202.5889 | 3.2311 | 12.1618 | 0 | 0 | 0
|  | 10 | 3726.13 | 111.4273 | 300.8943 | 0 | 0 | 0 | 431.87 | 6.8879 | 25.9261 | 0 | 0 | 0
|  | 11 | 3719.6339 | 111.2331 | 300.3697 | 0 | 0 | 0 | 661.1161 | 10.5441 | 39.6882 | 0 | 0 | 0
|  | 12 | 3713.1725 | 111.0398 | 299.848 | 0 | 0 | 0 | 890.3275 | 14.1998 | 53.4482 | 0 | 0 | 0
|  | 13 | 3706.7458 | 110.8477 | 299.329 | 0 | 0 | 0 | 1119.5042 | 17.8549 | 67.2062 | 0 | 0 | 0
|  | 14 | 3700.3537 | 110.6565 | 298.8128 | 0 | 0 | 0 | 1348.6463 | 21.5095 | 80.962 | 0 | 0 | 0
|  | 15 | 3693.9961 | 110.4664 | 298.2994 | 0 | 0 | 0 | 1206.5039 | 19.2425 | 72.4289 | 0 | 0 | 0
|  | 16 | 3693.5554 | 110.4532 | 298.2638 | 6190.7174 | 148.1033 | 321.8435 | 1404.9446 | 22.4074 | 84.3418 | 1131.7449 | 90.2508 | 34.1631
|  | 17 | 3701.1356 | 110.6799 | 298.8759 | 6189.8846 | 148.0834 | 321.8002 | 2090.3644 | 33.3391 | 125.4889 | 1132.5778 | 90.3172 | 34.1882
|  | 18 | 3708.6838 | 110.9056 | 299.4855 | 6188.6965 | 148.0549 | 321.7384 | 1934.3162 | 30.8503 | 116.121 | 1133.7659 | 90.412 | 34.2241
|  | 19 | 3716.1999 | 111.1304 | 300.0924 | 6187.4206 | 148.0244 | 321.6721 | 2223.8001 | 35.4673 | 133.4994 | 1135.0418 | 90.5137 | 34.2626
|  | 20 | 3723.6835 | 111.3542 | 300.6967 | 6186.1574 | 147.9942 | 321.6064 | 1919.3165 | 30.6111 | 115.2206 | 1136.3049 | 90.6144 | 34.3007
|  | 21 | 3731.135 | 111.577 | 301.2985 | 6184.8066 | 147.9619 | 321.5362 | 2357.365 | 37.5975 | 141.5175 | 1137.6557 | 90.7221 | 34.3415
|  | 22 | 3738.5542 | 111.7989 | 301.8976 | 6183.6692 | 147.9347 | 321.4771 | 1607.4458 | 25.6371 | 96.4983 | 1138.7931 | 90.8128 | 34.3758
|  | 23 | 3737.9181 | 111.7798 | 301.8462 | 0 | 0 | 0 | 865.5819 | 13.8051 | 51.9627 | 0 | 0 | 0
|  | 24 | 3731.4337 | 111.5859 | 301.3226 | 0 | 0 | 0 | 129.5663 | 2.0664 | 7.7781 | 0 | 0 | 0
|  | 25 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 26 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 27 | 2554.2 | 76.3816 | 206.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 28 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 29 | 2948.7857 | 88.1814 | 238.1218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 30 | 3139.7143 | 93.891 | 253.5398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 31 | 3330.6429 | 99.6006 | 268.9577 | 6184.2213 | 147.9479 | 321.5058 | 0 | 0 | 0 | 1138.2411 | 90.7688 | 34.3592
|  | 32 | 3521.5714 | 105.3102 | 284.3757 | 6185.7687 | 147.9849 | 321.5862 | 0 | 0 | 0 | 1136.6936 | 90.6454 | 34.3125
|  | 33 | 3712.5 | 111.0197 | 299.7936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 34 | 3708.2572 | 110.8929 | 299.451 | 0 | 0 | 0 | 195.1714 | 3.1128 | 11.7165 | 0 | 0 | 0
|  | 35 | 3701.9642 | 110.7047 | 298.9429 | 0 | 0 | 0 | 392.3929 | 6.2583 | 23.5562 | 0 | 0 | 0
|  | 36 | 3695.7053 | 110.5175 | 298.4374 | 0 | 0 | 0 | 589.5804 | 9.4032 | 35.3937 | 0 | 0 | 0
|  | 37 | 3689.4802 | 110.3313 | 297.9347 | 0 | 0 | 0 | 786.7341 | 12.5476 | 47.2293 | 0 | 0 | 0
|  | 38 | 3682.936 | 110.1356 | 297.4063 | 0 | 0 | 0 | 984.2068 | 15.6971 | 59.084 | 0 | 0 | 0
|  | 39 | 3675.8975 | 109.9252 | 296.8379 | 0 | 0 | 0 | 1182.1739 | 18.8544 | 70.9684 | 0 | 0 | 0
|  | 40 | 3674.7605 | 109.8912 | 296.7461 | 6182.2176 | 147.8999 | 321.4016 | 1374.2395 | 21.9177 | 82.4985 | 1140.2447 | 90.9286 | 34.4197
|  | 41 | 3681.6431 | 110.097 | 297.3019 | 6182.0263 | 147.8954 | 321.3917 | 1218.8569 | 19.4395 | 73.1705 | 1140.4361 | 90.9439 | 34.4254
|  | 42 | 3688.4966 | 110.3019 | 297.8553 | 6181.7454 | 147.8886 | 321.3771 | 1509.0034 | 24.067 | 90.5886 | 1140.717 | 90.9663 | 34.4339
|  | 43 | 3695.3205 | 110.506 | 298.4064 | 6181.0746 | 147.8726 | 321.3422 | 1799.1795 | 28.695 | 108.0085 | 1141.3878 | 91.0198 | 34.4542
|  | 44 | 3702.114 | 110.7092 | 298.955 | 6180.1147 | 147.8496 | 321.2923 | 1940.886 | 30.9551 | 116.5154 | 1142.3477 | 91.0963 | 34.4831
|  | 45 | 3708.8766 | 110.9114 | 299.5011 | 6178.7659 | 147.8174 | 321.2222 | 2379.6234 | 37.9525 | 142.8537 | 1143.6964 | 91.2039 | 34.5239
|  | 46 | 3715.6078 | 111.1127 | 300.0446 | 6177.6302 | 147.7902 | 321.1631 | 1630.3922 | 26.0031 | 97.8758 | 1144.8321 | 91.2944 | 34.5581
|  | 47 | 3714.2866 | 111.0732 | 299.9379 | 0 | 0 | 0 | 889.2134 | 14.182 | 53.3813 | 0 | 0 | 0
|  | 48 | 3707.1295 | 110.8591 | 299.36 | 0 | 0 | 0 | 153.8705 | 2.4541 | 9.2372 | 0 | 0 | 0
|  | 49 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 50 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 51 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 52 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 53 | 2992.8462 | 89.499 | 241.6798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 54 | 3198.4615 | 95.6478 | 258.2838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 55 | 3404.0769 | 101.7966 | 274.8877 | 6178.3696 | 147.8079 | 321.2016 | 0 | 0 | 0 | 1144.0927 | 91.2355 | 34.5358
|  | 56 | 3609.6923 | 107.9453 | 291.4917 | 6179.9544 | 147.8458 | 321.284 | 0 | 0 | 0 | 1142.5079 | 91.1091 | 34.488
|  | 57 | 3683.1396 | 110.1417 | 297.4227 | 0 | 0 | 0 | 132.1681 | 2.1079 | 7.9343 | 0 | 0 | 0
|  | 58 | 3676.1537 | 109.9328 | 296.8586 | 0 | 0 | 0 | 344.7693 | 5.4987 | 20.6972 | 0 | 0 | 0
|  | 59 | 3669.2028 | 109.725 | 296.2973 | 0 | 0 | 0 | 557.3357 | 8.8889 | 33.458 | 0 | 0 | 0
|  | 60 | 3662.2867 | 109.5181 | 295.7388 | 0 | 0 | 0 | 769.8672 | 12.2786 | 46.2167 | 0 | 0 | 0
|  | 61 | 3655.4053 | 109.3124 | 295.1831 | 0 | 0 | 0 | 982.3639 | 15.6677 | 58.9734 | 0 | 0 | 0
|  | 62 | 3648.5585 | 109.1076 | 294.6302 | 0 | 0 | 0 | 1194.8261 | 19.0562 | 71.7279 | 0 | 0 | 0
|  | 63 | 3641.7462 | 108.9039 | 294.0801 | 0 | 0 | 0 | 1407.2538 | 22.4442 | 84.4804 | 0 | 0 | 0
|  | 64 | 3640.8211 | 108.8762 | 294.0054 | 6175.0853 | 147.7293 | 321.0308 | 1259.6789 | 20.0906 | 75.6212 | 1147.3771 | 91.4974 | 34.635
|  | 65 | 3647.9123 | 109.0883 | 294.578 | 6174.8127 | 147.7228 | 321.0167 | 1519.8877 | 24.2406 | 91.242 | 1147.6496 | 91.5191 | 34.6432
|  | 66 | 3654.9732 | 109.2994 | 295.1482 | 6174.1912 | 147.7079 | 320.9843 | 1780.1268 | 28.3912 | 106.8647 | 1148.2711 | 91.5687 | 34.6619
|  | 67 | 3662.0028 | 109.5097 | 295.7159 | 6173.0611 | 147.6809 | 320.9256 | 2277.9972 | 36.3317 | 136.7529 | 1149.4012 | 91.6588 | 34.6961
|  | 68 | 3669.0002 | 109.7189 | 296.2809 | 6171.6036 | 147.646 | 320.8498 | 2270.9998 | 36.2201 | 136.3328 | 1150.8587 | 91.775 | 34.7401
|  | 69 | 3675.9651 | 109.9272 | 296.8434 | 6170.0197 | 147.6081 | 320.7675 | 2561.0349 | 40.8459 | 153.7443 | 1152.4426 | 91.9013 | 34.7879
|  | 70 | 3682.8976 | 110.1345 | 297.4032 | 6168.8314 | 147.5797 | 320.7057 | 1781.9024 | 28.4195 | 106.9713 | 1153.631 | 91.9961 | 34.8237
|  | 71 | 3681.7798 | 110.1011 | 297.3129 | 0 | 0 | 0 | 1010.8202 | 16.1215 | 60.6816 | 0 | 0 | 0
|  | 72 | 3674.8423 | 109.8936 | 296.7527 | 0 | 0 | 0 | 245.5577 | 3.9164 | 14.7413 | 0 | 0 | 0
|  | 73 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 74 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 75 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 76 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 77 | 2970 | 88.8158 | 239.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 78 | 3168 | 94.7368 | 255.8239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 79 | 3366 | 100.6579 | 271.8129 | 6172.5793 | 147.6694 | 320.9005 | 0 | 0 | 0 | 1149.883 | 91.6972 | 34.7106
|  | 80 | 3564 | 106.5789 | 287.8019 | 6174.7521 | 147.7213 | 321.0135 | 0 | 0 | 0 | 1147.7103 | 91.5239 | 34.645
|  | 81 | 3660.4576 | 109.4634 | 295.5911 | 6176.9282 | 147.7734 | 321.1266 | 101.5424 | 1.6195 | 6.0958 | 1145.5341 | 91.3504 | 34.5793
|  | 82 | 3667.5166 | 109.6745 | 296.1611 | 6178.9146 | 147.8209 | 321.2299 | 292.4834 | 4.6648 | 17.5584 | 1143.5477 | 91.192 | 34.5194
|  | 83 | 3674.5505 | 109.8849 | 296.7291 | 6180.6832 | 147.8632 | 321.3218 | 483.4495 | 7.7105 | 29.0225 | 1141.7791 | 91.051 | 34.466
|  | 84 | 3681.5587 | 110.0945 | 297.2951 | 6182.234 | 147.9003 | 321.4025 | 674.4413 | 10.7566 | 40.4881 | 1140.2283 | 90.9273 | 34.4192
|  | 85 | 3688.8938 | 110.3138 | 297.8874 | 6183.5673 | 147.9322 | 321.4718 | 865.1062 | 13.7975 | 51.9341 | 1138.895 | 90.821 | 34.3789
|  | 86 | 3696.7305 | 110.5482 | 298.5202 | 6184.6842 | 147.959 | 321.5299 | 1055.2695 | 16.8305 | 63.35 | 1137.7781 | 90.7319 | 34.3452
|  | 87 | 3704.5388 | 110.7817 | 299.1508 | 6185.8188 | 147.9861 | 321.5888 | 898.9612 | 14.3375 | 53.9665 | 1136.6435 | 90.6414 | 34.311
|  | 88 | 3712.3191 | 111.0143 | 299.779 | 6186.8707 | 148.0113 | 321.6435 | 1237.6809 | 19.7397 | 74.3006 | 1135.5916 | 90.5575 | 34.2792
|  | 89 | 3720.0706 | 111.2461 | 300.405 | 6187.506 | 148.0265 | 321.6766 | 1576.4294 | 25.1424 | 94.6363 | 1134.9563 | 90.5069 | 34.26
|  | 90 | 3727.7926 | 111.4771 | 301.0286 | 6187.7253 | 148.0317 | 321.688 | 1915.2074 | 30.5456 | 114.9739 | 1134.737 | 90.4894 | 34.2534
|  | 91 | 3735.4846 | 111.7071 | 301.6497 | 6188.0385 | 148.0392 | 321.7042 | 1499.1404 | 23.9097 | 89.9965 | 1134.4238 | 90.4644 | 34.2439
|  | 92 | 3743.1476 | 111.9362 | 302.2685 | 6188.9543 | 148.0611 | 321.7518 | 1083.1024 | 17.2744 | 65.0209 | 1133.508 | 90.3914 | 34.2163
|  | 93 | 3750.7831 | 112.1646 | 302.8851 | 6190.4717 | 148.0974 | 321.8307 | 667.0919 | 10.6394 | 40.0469 | 1131.9906 | 90.2704 | 34.1705
|  | 94 | 3758.3924 | 112.3921 | 303.4996 | 6192.5897 | 148.1481 | 321.9408 | 251.1076 | 4.0049 | 15.0745 | 1129.8726 | 90.1015 | 34.1066
|  | 95 | 3601.125 | 107.6891 | 290.7998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 96 | 2970 | 88.8158 | 239.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 97 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 98 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 99 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 100 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 101 | 2943 | 88.0084 | 237.6546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 102 | 3132 | 93.6603 | 252.9168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 103 | 3321 | 99.3122 | 268.179 | 6204.8684 | 148.4418 | 322.5792 | 0 | 0 | 0 | 1117.594 | 89.1223 | 33.7359
|  | 104 | 3510 | 104.9641 | 283.4413 | 6207.3272 | 148.5006 | 322.707 | 0 | 0 | 0 | 1115.1352 | 88.9262 | 33.6617
|  | 105 | 3699 | 110.616 | 298.7035 | 6209.7603 | 148.5589 | 322.8335 | 0 | 0 | 0 | 1112.702 | 88.7322 | 33.5882
|  | 106 | 3754.8469 | 112.2861 | 303.2133 | 6212.1017 | 148.6149 | 322.9552 | 133.1531 | 2.1237 | 7.9935 | 1110.3606 | 88.5455 | 33.5176
|  | 107 | 3762.5496 | 112.5164 | 303.8353 | 6214.1813 | 148.6646 | 323.0634 | 314.4504 | 5.0152 | 18.8771 | 1108.281 | 88.3797 | 33.4548
|  | 108 | 3770.226 | 112.746 | 304.4552 | 6215.9906 | 148.7079 | 323.1574 | 495.774 | 7.9071 | 29.7623 | 1106.4717 | 88.2354 | 33.4002
|  | 109 | 3777.8758 | 112.9748 | 305.0729 | 6217.5299 | 148.7447 | 323.2374 | 677.1242 | 10.7994 | 40.6492 | 1104.9324 | 88.1126 | 33.3537
|  | 110 | 3785.4984 | 113.2027 | 305.6885 | 6218.9841 | 148.7795 | 323.313 | 584.6445 | 9.3245 | 35.0974 | 1103.4782 | 87.9967 | 33.3098
|  | 111 | 3793.094 | 113.4298 | 306.3018 | 6220.5379 | 148.8167 | 323.3938 | 492.1917 | 7.8499 | 29.5473 | 1101.9244 | 87.8728 | 33.2629
|  | 112 | 3800.3983 | 113.6483 | 306.8917 | 6222.1909 | 148.8562 | 323.4798 | 400.0302 | 6.3801 | 24.0146 | 1100.2714 | 87.7409 | 33.213
|  | 113 | 3805.2969 | 113.7948 | 307.2872 | 6223.9407 | 148.8981 | 323.5707 | 310.2745 | 4.9486 | 18.6264 | 1098.5216 | 87.6014 | 33.1602
|  | 114 | 3810.1744 | 113.9406 | 307.6811 | 6225.7855 | 148.9422 | 323.6666 | 220.5398 | 3.5174 | 13.2395 | 1096.6768 | 87.4543 | 33.1045
|  | 115 | 3815.0311 | 114.0859 | 308.0733 | 6227.7249 | 148.9886 | 323.7675 | 130.826 | 2.0865 | 7.8538 | 1094.7374 | 87.2996 | 33.046
|  | 116 | 3819.8673 | 114.2305 | 308.4638 | 6229.7587 | 149.0373 | 323.8732 | 41.1327 | 0.65602 | 2.4693 | 1092.7036 | 87.1375 | 32.9846
|  | 117 | 3824.6831 | 114.3745 | 308.8527 | 6231.6288 | 149.082 | 323.9704 | 333.3169 | 5.3161 | 20.0097 | 1090.8336 | 86.9883 | 32.9281
|  | 118 | 3712.5 | 111.0197 | 299.7936 | 6233.5582 | 149.1282 | 324.0707 | 0 | 0 | 0 | 1088.9042 | 86.8345 | 32.8699
|  | 119 | 3267 | 97.6974 | 263.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 120 | 2821.5 | 84.375 | 227.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 121 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 122 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 123 | 2545.7143 | 76.1278 | 205.5728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 124 | 2715.4286 | 81.203 | 219.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 125 | 2885.1429 | 86.2782 | 232.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 126 | 3054.8571 | 91.3534 | 246.6873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 127 | 3224.5714 | 96.4286 | 260.3922 | 6240.7781 | 149.3009 | 324.4461 | 0 | 0 | 0 | 1081.6843 | 86.2587 | 32.6519
|  | 128 | 3394.2857 | 101.5038 | 274.0971 | 6242.6135 | 149.3448 | 324.5415 | 0 | 0 | 0 | 1079.8489 | 86.1124 | 32.5965
|  | 129 | 3564 | 106.5789 | 287.8019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 130 | 3733.7143 | 111.6541 | 301.5068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 131 | 3764.8271 | 112.5845 | 304.0192 | 0 | 0 | 0 | 138.6014 | 2.2105 | 8.3205 | 0 | 0 | 0
|  | 132 | 3755.2519 | 112.2982 | 303.246 | 0 | 0 | 0 | 317.8909 | 5.07 | 19.0837 | 0 | 0 | 0
|  | 133 | 3745.4524 | 112.0052 | 302.4546 | 0 | 0 | 0 | 412.5476 | 6.5797 | 24.7661 | 0 | 0 | 0
|  | 134 | 3735.6931 | 111.7133 | 301.6666 | 0 | 0 | 0 | 422.3069 | 6.7354 | 25.352 | 0 | 0 | 0
|  | 135 | 3725.974 | 111.4227 | 300.8817 | 0 | 0 | 0 | 856.3117 | 13.6573 | 51.4062 | 0 | 0 | 0
|  | 136 | 3725.0993 | 111.3965 | 300.8111 | 6243.8336 | 149.374 | 324.6049 | 1026.9007 | 16.378 | 61.647 | 1078.6288 | 86.0151 | 32.5597
|  | 137 | 3732.9701 | 111.6319 | 301.4467 | 6244.2172 | 149.3832 | 324.6249 | 781.4299 | 12.463 | 46.9109 | 1078.2452 | 85.9845 | 32.5481
|  | 138 | 3740.811 | 111.8664 | 302.0798 | 6244.906 | 149.3997 | 324.6607 | 535.989 | 8.5485 | 32.1765 | 1077.5563 | 85.9295 | 32.5273
|  | 139 | 3748.6226 | 112.1 | 302.7106 | 6245.8194 | 149.4215 | 324.7082 | 409.3774 | 6.5291 | 24.5758 | 1076.6429 | 85.8567 | 32.4998
|  | 140 | 3756.4056 | 112.3327 | 303.3391 | 6247.0371 | 149.4506 | 324.7715 | 45.1944 | 0.7208 | 2.7131 | 1075.4252 | 85.7596 | 32.463
|  | 141 | 3564 | 106.5789 | 287.8019 | 6248.5284 | 149.4863 | 324.849 | 0 | 0 | 0 | 1073.934 | 85.6407 | 32.418
|  | 142 | 3326.4 | 99.4737 | 268.6151 | 6249.9972 | 149.5215 | 324.9254 | 0 | 0 | 0 | 1072.4651 | 85.5235 | 32.3736
|  | 143 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 144 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 145 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 146 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 147 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 148 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 149 | 2821.5 | 84.375 | 227.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 150 | 2970 | 88.8158 | 239.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 151 | 3118.5 | 93.2566 | 251.8267 | 6251.6888 | 149.5619 | 325.0133 | 0 | 0 | 0 | 1070.7736 | 85.3886 | 32.3226
|  | 152 | 3267 | 97.6974 | 263.8184 | 6252.8938 | 149.5908 | 325.0759 | 0 | 0 | 0 | 1069.5685 | 85.2925 | 32.2862
|  | 153 | 3415.5 | 102.1382 | 275.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 154 | 3564 | 106.5789 | 287.8019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 155 | 3712.5 | 111.0197 | 299.7936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 156 | 3742.1908 | 111.9076 | 302.1913 | 0 | 0 | 0 | 118.8092 | 1.8949 | 7.1324 | 0 | 0 | 0
|  | 157 | 3736.0623 | 111.7244 | 301.6964 | 0 | 0 | 0 | 273.4377 | 4.361 | 16.415 | 0 | 0 | 0
|  | 158 | 3729.9669 | 111.5421 | 301.2041 | 0 | 0 | 0 | 428.0331 | 6.8267 | 25.6957 | 0 | 0 | 0
|  | 159 | 3723.9043 | 111.3608 | 300.7146 | 0 | 0 | 0 | 285.5957 | 4.555 | 17.1449 | 0 | 0 | 0
|  | 160 | 3723.8709 | 111.3598 | 300.7119 | 6250.9438 | 149.5441 | 324.9746 | 434.1291 | 6.9239 | 26.0617 | 1071.5185 | 85.448 | 32.3451
|  | 161 | 3731.8788 | 111.5992 | 301.3585 | 6250.9347 | 149.5439 | 324.9741 | 1020.1212 | 16.2699 | 61.24 | 1071.5277 | 85.4488 | 32.3454
|  | 162 | 3739.8544 | 111.8378 | 302.0026 | 6250.6101 | 149.5361 | 324.9572 | 863.6456 | 13.7743 | 51.8464 | 1071.8523 | 85.4747 | 32.3552
|  | 163 | 3747.7975 | 112.0753 | 302.644 | 6250.1706 | 149.5256 | 324.9344 | 1152.7025 | 18.3844 | 69.1991 | 1072.2918 | 85.5097 | 32.3684
|  | 164 | 3755.7079 | 112.3118 | 303.2828 | 6249.7368 | 149.5152 | 324.9118 | 818.0921 | 13.0477 | 49.1118 | 1072.7256 | 85.5443 | 32.3815
|  | 165 | 3763.0571 | 112.5316 | 303.8763 | 6249.7291 | 149.515 | 324.9114 | 484.0429 | 7.72 | 29.0581 | 1072.7333 | 85.5449 | 32.3817
|  | 166 | 3768.2611 | 112.6872 | 304.2965 | 6250.1445 | 149.525 | 324.933 | 152.1389 | 2.4265 | 9.1332 | 1072.3178 | 85.5118 | 32.3692
|  | 167 | 3593.7 | 107.4671 | 290.2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 168 | 3267 | 97.6974 | 263.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 169 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 170 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 171 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 172 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 173 | 3044.25 | 91.0362 | 245.8308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 174 | 3267 | 97.6974 | 263.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 175 | 3489.75 | 104.3586 | 281.806 | 6246.1972 | 149.4306 | 324.7278 | 0 | 0 | 0 | 1076.2651 | 85.8266 | 32.4884
|  | 176 | 3712.5 | 111.0197 | 299.7936 | 6246.7904 | 149.4447 | 324.7586 | 0 | 0 | 0 | 1075.6719 | 85.7793 | 32.4705
|  | 177 | 3726.0637 | 111.4253 | 300.8889 | 0 | 0 | 0 | 209.1863 | 3.3363 | 12.5579 | 0 | 0 | 0
|  | 178 | 3719.161 | 111.2189 | 300.3315 | 0 | 0 | 0 | 438.839 | 6.999 | 26.3444 | 0 | 0 | 0
|  | 179 | 3712.2927 | 111.0135 | 299.7769 | 0 | 0 | 0 | 668.4573 | 10.6612 | 40.1289 | 0 | 0 | 0
|  | 180 | 3705.4586 | 110.8092 | 299.225 | 0 | 0 | 0 | 898.0414 | 14.3228 | 53.9113 | 0 | 0 | 0
|  | 181 | 3698.6585 | 110.6058 | 298.6759 | 0 | 0 | 0 | 1127.5915 | 17.9839 | 67.6917 | 0 | 0 | 0
|  | 182 | 3691.8924 | 110.4035 | 298.1295 | 0 | 0 | 0 | 1357.1076 | 21.6445 | 81.47 | 0 | 0 | 0
|  | 183 | 3685.1601 | 110.2022 | 297.5859 | 0 | 0 | 0 | 1215.3399 | 19.3834 | 72.9594 | 0 | 0 | 0
|  | 184 | 3684.425 | 110.1802 | 297.5265 | 6232.7852 | 149.1097 | 324.0305 | 1414.075 | 22.553 | 84.8899 | 1089.6772 | 86.8961 | 32.8932
|  | 185 | 3691.7222 | 110.3984 | 298.1158 | 6230.8034 | 149.0623 | 323.9275 | 2099.7778 | 33.4893 | 126.054 | 1091.6589 | 87.0541 | 32.953
|  | 186 | 3698.9837 | 110.6155 | 298.7022 | 6228.4434 | 149.0058 | 323.8048 | 1944.0163 | 31.005 | 116.7033 | 1094.019 | 87.2423 | 33.0243
|  | 187 | 3706.2094 | 110.8316 | 299.2857 | 6225.9725 | 148.9467 | 323.6764 | 2233.7906 | 35.6266 | 134.0991 | 1096.4898 | 87.4394 | 33.0989
|  | 188 | 3713.399 | 111.0466 | 299.8662 | 6223.4916 | 148.8874 | 323.5474 | 1929.601 | 30.7751 | 115.838 | 1098.9707 | 87.6372 | 33.1738
|  | 189 | 3720.5528 | 111.2606 | 300.4439 | 6220.9005 | 148.8254 | 323.4127 | 2367.9472 | 37.7663 | 142.1528 | 1101.5619 | 87.8438 | 33.252
|  | 190 | 3728.1115 | 111.4866 | 301.0543 | 6218.5004 | 148.768 | 323.2879 | 1617.8885 | 25.8036 | 97.1252 | 1103.962 | 88.0352 | 33.3244
|  | 191 | 3728.0397 | 111.4844 | 301.0485 | 0 | 0 | 0 | 875.4603 | 13.9627 | 52.5557 | 0 | 0 | 0
|  | 192 | 3722.0514 | 111.3054 | 300.5649 | 0 | 0 | 0 | 138.9486 | 2.2161 | 8.3414 | 0 | 0 | 0
|  | 193 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 194 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 195 | 2554.2 | 76.3816 | 206.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 196 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 197 | 2948.7857 | 88.1814 | 238.1218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 198 | 3139.7143 | 93.891 | 253.5398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 199 | 3330.6429 | 99.6006 | 268.9577 | 6207.102 | 148.4953 | 322.6953 | 0 | 0 | 0 | 1115.3603 | 88.9442 | 33.6685
|  | 200 | 3521.5714 | 105.3102 | 284.3757 | 6207.1877 | 148.4973 | 322.6998 | 0 | 0 | 0 | 1115.2746 | 88.9374 | 33.6659
|  | 201 | 3709.5604 | 110.9318 | 299.5563 | 0 | 0 | 0 | 2.9396 | 0.046884 | 0.17647 | 0 | 0 | 0
|  | 202 | 3703.7076 | 110.7568 | 299.0836 | 0 | 0 | 0 | 199.721 | 3.1853 | 11.9897 | 0 | 0 | 0
|  | 203 | 3697.8868 | 110.5827 | 298.6136 | 0 | 0 | 0 | 396.4703 | 6.3233 | 23.8009 | 0 | 0 | 0
|  | 204 | 3692.0979 | 110.4096 | 298.1461 | 0 | 0 | 0 | 593.1878 | 9.4607 | 35.6103 | 0 | 0 | 0
|  | 205 | 3686.3407 | 110.2375 | 297.6812 | 0 | 0 | 0 | 789.8736 | 12.5977 | 47.4178 | 0 | 0 | 0
|  | 206 | 3679.7336 | 110.0399 | 297.1477 | 0 | 0 | 0 | 987.4093 | 15.7482 | 59.2762 | 0 | 0 | 0
|  | 207 | 3673.1597 | 109.8433 | 296.6168 | 0 | 0 | 0 | 1184.9118 | 18.8981 | 71.1327 | 0 | 0 | 0
|  | 208 | 3672.504 | 109.8237 | 296.5639 | 6191.4909 | 148.1218 | 321.8837 | 1376.496 | 21.9537 | 82.6339 | 1130.9714 | 90.1891 | 34.1397
|  | 209 | 3679.8662 | 110.0438 | 297.1584 | 6189.8698 | 148.083 | 321.7994 | 1220.6338 | 19.4678 | 73.2772 | 1132.5926 | 90.3184 | 34.1887
|  | 210 | 3687.1939 | 110.263 | 297.7501 | 6188.2024 | 148.0431 | 321.7128 | 1510.3061 | 24.0878 | 90.6668 | 1134.2599 | 90.4513 | 34.239
|  | 211 | 3694.4867 | 110.4811 | 298.339 | 6186.1887 | 147.9949 | 321.6081 | 1800.0133 | 28.7083 | 108.0585 | 1136.2736 | 90.6119 | 34.2998
|  | 212 | 3701.7441 | 110.6981 | 298.9251 | 6183.9294 | 147.9409 | 321.4906 | 1941.2559 | 30.961 | 116.5376 | 1138.5329 | 90.7921 | 34.368
|  | 213 | 3708.9655 | 110.914 | 299.5082 | 6181.3248 | 147.8786 | 321.3552 | 2379.5345 | 37.9511 | 142.8484 | 1141.1375 | 90.9998 | 34.4466
|  | 214 | 3716.1508 | 111.1289 | 300.0885 | 6178.9769 | 147.8224 | 321.2331 | 1629.8492 | 25.9944 | 97.8432 | 1143.4854 | 91.187 | 34.5175
|  | 215 | 3715.2787 | 111.1028 | 300.018 | 0 | 0 | 0 | 888.2213 | 14.1662 | 53.3218 | 0 | 0 | 0
|  | 216 | 3708.5671 | 110.9021 | 299.4761 | 0 | 0 | 0 | 152.4329 | 2.4311 | 9.1509 | 0 | 0 | 0
|  | 217 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 218 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 219 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 220 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 221 | 2992.8462 | 89.499 | 241.6798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 222 | 3198.4615 | 95.6478 | 258.2838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 223 | 3404.0769 | 101.7966 | 274.8877 | 6170.7128 | 147.6247 | 320.8035 | 0 | 0 | 0 | 1151.7495 | 91.8461 | 34.7669
|  | 224 | 3609.6923 | 107.9453 | 291.4917 | 6171.517 | 147.6439 | 320.8453 | 0 | 0 | 0 | 1150.9453 | 91.7819 | 34.7427
|  | 225 | 3688.507 | 110.3022 | 297.8562 | 0 | 0 | 0 | 126.8007 | 2.0223 | 7.6121 | 0 | 0 | 0
|  | 226 | 3681.9463 | 110.106 | 297.3264 | 0 | 0 | 0 | 338.9768 | 5.4063 | 20.3495 | 0 | 0 | 0
|  | 227 | 3675.4185 | 109.9108 | 296.7992 | 0 | 0 | 0 | 551.1199 | 8.7898 | 33.0849 | 0 | 0 | 0
|  | 228 | 3668.9236 | 109.7166 | 296.2747 | 0 | 0 | 0 | 763.2302 | 12.1727 | 45.8183 | 0 | 0 | 0
|  | 229 | 3662.4615 | 109.5234 | 295.7529 | 0 | 0 | 0 | 975.3077 | 15.5551 | 58.5498 | 0 | 0 | 0
|  | 230 | 3656.032 | 109.3311 | 295.2337 | 0 | 0 | 0 | 1187.3526 | 18.937 | 71.2793 | 0 | 0 | 0
|  | 231 | 3649.635 | 109.1398 | 294.7171 | 0 | 0 | 0 | 1399.365 | 22.3184 | 84.0068 | 0 | 0 | 0
|  | 232 | 3649.8039 | 109.1449 | 294.7308 | 6161.9366 | 147.4148 | 320.3473 | 1250.6961 | 19.9473 | 75.0819 | 1160.5257 | 92.5459 | 35.0319
|  | 233 | 3658.1569 | 109.3946 | 295.4053 | 6161.2858 | 147.3992 | 320.3134 | 1509.6431 | 24.0772 | 90.627 | 1161.1765 | 92.5978 | 35.0515
|  | 234 | 3666.4753 | 109.6434 | 296.077 | 6160.331 | 147.3763 | 320.2638 | 1768.6247 | 28.2077 | 106.1742 | 1162.1313 | 92.6739 | 35.0803
|  | 235 | 3674.7582 | 109.8911 | 296.7459 | 6158.9124 | 147.3424 | 320.19 | 2265.2418 | 36.1283 | 135.9872 | 1163.5499 | 92.7871 | 35.1232
|  | 236 | 3683.0049 | 110.1377 | 297.4118 | 6157.2112 | 147.3017 | 320.1016 | 2256.9951 | 35.9967 | 135.4921 | 1165.2512 | 92.9227 | 35.1745
|  | 237 | 3691.2151 | 110.3832 | 298.0748 | 6155.3679 | 147.2576 | 320.0058 | 2545.7849 | 40.6026 | 152.8288 | 1167.0944 | 93.0697 | 35.2301
|  | 238 | 3699.3889 | 110.6277 | 298.7349 | 6153.9041 | 147.2226 | 319.9297 | 1765.4111 | 28.1565 | 105.9813 | 1168.5583 | 93.1865 | 35.2743
|  | 239 | 3699.5133 | 110.6314 | 298.7449 | 0 | 0 | 0 | 993.0867 | 15.8387 | 59.6171 | 0 | 0 | 0
|  | 240 | 3693.8434 | 110.4618 | 298.2871 | 0 | 0 | 0 | 226.5566 | 3.6133 | 13.6007 | 0 | 0 | 0
|  | 241 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 242 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 243 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 244 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 245 | 2970 | 88.8158 | 239.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 246 | 3168 | 94.7368 | 255.8239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 247 | 3366 | 100.6579 | 271.8129 | 6154.9559 | 147.2477 | 319.9843 | 0 | 0 | 0 | 1167.5064 | 93.1026 | 35.2426
|  | 248 | 3564 | 106.5789 | 287.8019 | 6156.8511 | 147.2931 | 320.0829 | 0 | 0 | 0 | 1165.6112 | 92.9515 | 35.1854
|  | 249 | 3691.0515 | 110.3783 | 298.0616 | 6158.7704 | 147.339 | 320.1826 | 70.9485 | 1.1316 | 4.2592 | 1163.692 | 92.7984 | 35.1274
|  | 250 | 3699.3004 | 110.625 | 298.7277 | 6160.5254 | 147.381 | 320.2739 | 260.6996 | 4.1579 | 15.6503 | 1161.9369 | 92.6584 | 35.0745
|  | 251 | 3707.5203 | 110.8708 | 299.3915 | 6162.0662 | 147.4179 | 320.354 | 450.4797 | 7.1847 | 27.0432 | 1160.3961 | 92.5356 | 35.028
|  | 252 | 3715.7108 | 111.1158 | 300.0529 | 6163.393 | 147.4496 | 320.423 | 640.2892 | 10.2119 | 38.4379 | 1159.0694 | 92.4298 | 34.9879
|  | 253 | 3723.8716 | 111.3598 | 300.7119 | 6164.5058 | 147.4762 | 320.4808 | 830.1284 | 13.2397 | 49.8343 | 1157.9566 | 92.341 | 34.9543
|  | 254 | 3732.0022 | 111.6029 | 301.3685 | 6165.4048 | 147.4977 | 320.5276 | 1019.9978 | 16.2679 | 61.2326 | 1157.0575 | 92.2693 | 34.9272
|  | 255 | 3740.1024 | 111.8452 | 302.0226 | 6166.3241 | 147.5197 | 320.5753 | 863.3976 | 13.7703 | 51.8316 | 1156.1383 | 92.196 | 34.8994
|  | 256 | 3748.1725 | 112.0865 | 302.6743 | 6167.1631 | 147.5398 | 320.619 | 1201.8275 | 19.1679 | 72.1482 | 1155.2992 | 92.1291 | 34.8741
|  | 257 | 3756.2119 | 112.3269 | 303.3235 | 6167.5881 | 147.55 | 320.6411 | 1540.2881 | 24.566 | 92.4667 | 1154.8742 | 92.0952 | 34.8613
|  | 258 | 3763.6903 | 112.5505 | 303.9274 | 6167.5995 | 147.5502 | 320.6417 | 1879.3097 | 29.973 | 112.8189 | 1154.8628 | 92.0943 | 34.8609
|  | 259 | 3769.0225 | 112.71 | 304.358 | 6167.7049 | 147.5527 | 320.6471 | 1465.6025 | 23.3748 | 87.9832 | 1154.7574 | 92.0859 | 34.8577
|  | 260 | 3774.3288 | 112.8687 | 304.7865 | 6168.412 | 147.5697 | 320.6839 | 1051.9212 | 16.7771 | 63.149 | 1154.0504 | 92.0295 | 34.8364
|  | 261 | 3779.6105 | 113.0266 | 305.213 | 6169.7197 | 147.6009 | 320.7519 | 638.2645 | 10.1797 | 38.3163 | 1152.7427 | 91.9253 | 34.7969
|  | 262 | 3784.8691 | 113.1839 | 305.6376 | 6171.6269 | 147.6466 | 320.851 | 224.6309 | 3.5826 | 13.4851 | 1150.8354 | 91.7732 | 34.7394
|  | 263 | 3601.125 | 107.6891 | 290.7998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 264 | 2970 | 88.8158 | 239.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 265 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 266 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 267 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 268 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 269 | 2943 | 88.0084 | 237.6546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 270 | 3132 | 93.6603 | 252.9168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 271 | 3321 | 99.3122 | 268.179 | 6184.7308 | 147.9601 | 321.5323 | 0 | 0 | 0 | 1137.7315 | 90.7282 | 34.3438
|  | 272 | 3510 | 104.9641 | 283.4413 | 6187.6255 | 148.0293 | 321.6828 | 0 | 0 | 0 | 1134.8369 | 90.4974 | 34.2564
|  | 273 | 3699 | 110.616 | 298.7035 | 6190.5577 | 148.0995 | 321.8352 | 0 | 0 | 0 | 1131.9046 | 90.2635 | 34.1679
|  | 274 | 3754.0298 | 112.2617 | 303.1473 | 6193.4612 | 148.1689 | 321.9862 | 133.9702 | 2.1367 | 8.0425 | 1129.0011 | 90.032 | 34.0803
|  | 275 | 3759.4294 | 112.4231 | 303.5833 | 6196.0573 | 148.231 | 322.1211 | 317.5706 | 5.0649 | 19.0644 | 1126.4051 | 89.825 | 34.0019
|  | 276 | 3764.8074 | 112.584 | 304.0176 | 6198.3606 | 148.2861 | 322.2409 | 501.1926 | 7.9935 | 30.0876 | 1124.1017 | 89.6413 | 33.9324
|  | 277 | 3770.1632 | 112.7441 | 304.4501 | 6200.3917 | 148.3347 | 322.3465 | 684.8368 | 10.9224 | 41.1122 | 1122.0706 | 89.4793 | 33.8711
|  | 278 | 3775.4964 | 112.9036 | 304.8808 | 6202.3355 | 148.3812 | 322.4475 | 594.6464 | 9.484 | 35.6979 | 1120.1268 | 89.3243 | 33.8124
|  | 279 | 3780.8072 | 113.0624 | 305.3096 | 6204.3765 | 148.4301 | 322.5536 | 504.4785 | 8.0459 | 30.2849 | 1118.0858 | 89.1615 | 33.7508
|  | 280 | 3786.0958 | 113.2206 | 305.7367 | 6206.5145 | 148.4812 | 322.6648 | 414.3328 | 6.6082 | 24.8733 | 1115.9479 | 88.9911 | 33.6862
|  | 281 | 3791.3625 | 113.3781 | 306.162 | 6208.749 | 148.5347 | 322.7809 | 324.2089 | 5.1708 | 19.4629 | 1113.7134 | 88.8129 | 33.6188
|  | 282 | 3796.6077 | 113.5349 | 306.5856 | 6211.0796 | 148.5904 | 322.9021 | 234.1066 | 3.7338 | 14.0539 | 1111.3827 | 88.627 | 33.5484
|  | 283 | 3801.8316 | 113.6911 | 307.0074 | 6213.506 | 148.6485 | 323.0282 | 144.0256 | 2.2971 | 8.6462 | 1108.9564 | 88.4335 | 33.4752
|  | 284 | 3807.0344 | 113.8467 | 307.4275 | 6216.0278 | 148.7088 | 323.1593 | 53.9656 | 0.8607 | 3.2397 | 1106.4346 | 88.2324 | 33.3991
|  | 285 | 3812.2163 | 114.0017 | 307.846 | 6218.3869 | 148.7652 | 323.282 | 345.7837 | 5.5149 | 20.7581 | 1104.0755 | 88.0443 | 33.3278
|  | 286 | 3712.5 | 111.0197 | 299.7936 | 6220.8103 | 148.8232 | 323.408 | 0 | 0 | 0 | 1101.6521 | 87.851 | 33.2547
|  | 287 | 3267 | 97.6974 | 263.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 288 | 2821.5 | 84.375 | 227.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 289 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 290 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 291 | 2545.7143 | 76.1278 | 205.5728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 292 | 2715.4286 | 81.203 | 219.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 293 | 2885.1429 | 86.2782 | 232.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 294 | 3054.8571 | 91.3534 | 246.6873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 295 | 3224.5714 | 96.4286 | 260.3922 | 6232.4993 | 149.1029 | 324.0157 | 0 | 0 | 0 | 1089.9631 | 86.9189 | 32.9018
|  | 296 | 3394.2857 | 101.5038 | 274.0971 | 6234.8434 | 149.1589 | 324.1375 | 0 | 0 | 0 | 1087.6189 | 86.732 | 32.8311
|  | 297 | 3564 | 106.5789 | 287.8019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 298 | 3733.7143 | 111.6541 | 301.5068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 299 | 3756.8349 | 112.3455 | 303.3738 | 0 | 0 | 0 | 146.5937 | 2.338 | 8.8003 | 0 | 0 | 0
|  | 300 | 3747.3692 | 112.0625 | 302.6094 | 0 | 0 | 0 | 325.7737 | 5.1958 | 19.5569 | 0 | 0 | 0
|  | 301 | 3737.9422 | 111.7806 | 301.8482 | 0 | 0 | 0 | 420.0578 | 6.6995 | 25.2169 | 0 | 0 | 0
|  | 302 | 3728.5538 | 111.4998 | 301.09 | 0 | 0 | 0 | 429.4462 | 6.8492 | 25.7805 | 0 | 0 | 0
|  | 303 | 3720.7913 | 111.2677 | 300.4632 | 0 | 0 | 0 | 861.4944 | 13.7399 | 51.7173 | 0 | 0 | 0
|  | 304 | 3720.0967 | 111.2469 | 300.4071 | 6240.0242 | 149.2829 | 324.4069 | 1031.9033 | 16.4578 | 61.9473 | 1082.4382 | 86.3188 | 32.6747
|  | 305 | 3727.4413 | 111.4665 | 301.0002 | 6240.9074 | 149.304 | 324.4528 | 786.9587 | 12.5512 | 47.2428 | 1081.5549 | 86.2484 | 32.648
|  | 306 | 3734.7572 | 111.6853 | 301.591 | 6242.0948 | 149.3324 | 324.5145 | 542.0428 | 8.645 | 32.54 | 1080.3675 | 86.1537 | 32.6122
|  | 307 | 3742.045 | 111.9033 | 302.1795 | 6243.5055 | 149.3662 | 324.5879 | 415.955 | 6.6341 | 24.9706 | 1078.9568 | 86.0412 | 32.5696
|  | 308 | 3749.3054 | 112.1204 | 302.7658 | 6245.2192 | 149.4072 | 324.677 | 52.2946 | 0.83404 | 3.1394 | 1077.2431 | 85.9046 | 32.5179
|  | 309 | 3564 | 106.5789 | 287.8019 | 6247.2132 | 149.4549 | 324.7806 | 0 | 0 | 0 | 1075.2492 | 85.7455 | 32.4577
|  | 310 | 3326.4 | 99.4737 | 268.6151 | 6249.1861 | 149.5021 | 324.8832 | 0 | 0 | 0 | 1073.2762 | 85.5882 | 32.3981
|  | 311 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 312 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 313 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 314 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 315 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 316 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 317 | 2821.5 | 84.375 | 227.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 318 | 2970 | 88.8158 | 239.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 319 | 3118.5 | 93.2566 | 251.8267 | 6255.3922 | 149.6505 | 325.2058 | 0 | 0 | 0 | 1067.0702 | 85.0933 | 32.2108
|  | 320 | 3267 | 97.6974 | 263.8184 | 6257.0924 | 149.6912 | 325.2942 | 0 | 0 | 0 | 1065.37 | 84.9577 | 32.1595
|  | 321 | 3415.5 | 102.1382 | 275.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 322 | 3564 | 106.5789 | 287.8019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 323 | 3712.5 | 111.0197 | 299.7936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 324 | 3712.857 | 111.0304 | 299.8225 | 0 | 0 | 0 | 148.143 | 2.3627 | 8.8933 | 0 | 0 | 0
|  | 325 | 3706.24 | 110.8325 | 299.2881 | 0 | 0 | 0 | 303.26 | 4.8367 | 18.2053 | 0 | 0 | 0
|  | 326 | 3699.656 | 110.6356 | 298.7565 | 0 | 0 | 0 | 458.344 | 7.3101 | 27.5153 | 0 | 0 | 0
|  | 327 | 3693.1051 | 110.4397 | 298.2275 | 0 | 0 | 0 | 316.3949 | 5.0462 | 18.9938 | 0 | 0 | 0
|  | 328 | 3692.5981 | 110.4246 | 298.1865 | 6258.9144 | 149.7348 | 325.3889 | 465.4019 | 7.4227 | 27.939 | 1063.548 | 84.8124 | 32.1045
|  | 329 | 3700.136 | 110.65 | 298.7952 | 6259.3464 | 149.7451 | 325.4114 | 1051.864 | 16.7761 | 63.1456 | 1063.1159 | 84.778 | 32.0914
|  | 330 | 3707.6425 | 110.8745 | 299.4014 | 6259.4609 | 149.7479 | 325.4174 | 895.8575 | 14.288 | 53.7802 | 1063.0014 | 84.7689 | 32.088
|  | 331 | 3715.1176 | 111.098 | 300.005 | 6259.4584 | 149.7478 | 325.4172 | 1185.3824 | 18.9056 | 71.161 | 1063.0039 | 84.7691 | 32.0881
|  | 332 | 3722.5609 | 111.3206 | 300.6061 | 6259.4594 | 149.7478 | 325.4173 | 851.2391 | 13.5764 | 51.1017 | 1063.0029 | 84.769 | 32.088
|  | 333 | 3729.9732 | 111.5423 | 301.2047 | 6259.8845 | 149.758 | 325.4394 | 517.1268 | 8.2476 | 31.0442 | 1062.5778 | 84.7351 | 32.0752
|  | 334 | 3737.3555 | 111.763 | 301.8008 | 6260.7329 | 149.7783 | 325.4835 | 183.0445 | 2.9194 | 10.9885 | 1061.7294 | 84.6674 | 32.0496
|  | 335 | 3593.7 | 107.4671 | 290.2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 336 | 3267 | 97.6974 | 263.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 337 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 338 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 339 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 340 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 341 | 3044.25 | 91.0362 | 245.8308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 342 | 3267 | 97.6974 | 263.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 343 | 3489.75 | 104.3586 | 281.806 | 6261.0947 | 149.787 | 325.5023 | 0 | 0 | 0 | 1061.3676 | 84.6386 | 32.0387
|  | 344 | 3712.2687 | 111.0128 | 299.775 | 6262.1452 | 149.8121 | 325.5569 | 0.23128 | 0.0036887 | 0.013884 | 1060.3171 | 84.5548 | 32.0069
|  | 345 | 3711.7157 | 110.9963 | 299.7303 | 0 | 0 | 0 | 223.5343 | 3.5651 | 13.4192 | 0 | 0 | 0
|  | 346 | 3705.1602 | 110.8002 | 299.2009 | 0 | 0 | 0 | 452.8398 | 7.2223 | 27.1849 | 0 | 0 | 0
|  | 347 | 3698.6375 | 110.6052 | 298.6742 | 0 | 0 | 0 | 682.1125 | 10.879 | 40.9486 | 0 | 0 | 0
|  | 348 | 3692.1475 | 110.4111 | 298.1501 | 0 | 0 | 0 | 911.3525 | 14.5351 | 54.7104 | 0 | 0 | 0
|  | 349 | 3685.6901 | 110.218 | 297.6287 | 0 | 0 | 0 | 1140.5599 | 18.1907 | 68.4702 | 0 | 0 | 0
|  | 350 | 3679.2651 | 110.0259 | 297.1099 | 0 | 0 | 0 | 1369.7349 | 21.8459 | 82.228 | 0 | 0 | 0
|  | 351 | 3672.8725 | 109.8347 | 296.5936 | 0 | 0 | 0 | 1227.6275 | 19.5794 | 73.697 | 0 | 0 | 0
|  | 352 | 3672.5112 | 109.8239 | 296.5645 | 6251.7227 | 149.5627 | 325.0151 | 1425.9888 | 22.743 | 85.6051 | 1070.7397 | 85.3859 | 32.3216
|  | 353 | 3680.188 | 110.0535 | 297.1844 | 6250.1622 | 149.5254 | 324.9339 | 2111.312 | 33.6732 | 126.7465 | 1072.3001 | 85.5104 | 32.3687
|  | 354 | 3687.8284 | 110.2819 | 297.8014 | 6248.2215 | 149.479 | 324.833 | 1955.1716 | 31.183 | 117.373 | 1074.2408 | 85.6651 | 32.4273
|  | 355 | 3695.4321 | 110.5093 | 298.4154 | 6246.1681 | 149.4299 | 324.7263 | 2244.5679 | 35.7985 | 134.7461 | 1076.2942 | 85.8289 | 32.4892
|  | 356 | 3702.9991 | 110.7356 | 299.0264 | 6244.1027 | 149.3804 | 324.6189 | 1940.0009 | 30.941 | 116.4623 | 1078.3597 | 85.9936 | 32.5516
|  | 357 | 3710.5295 | 110.9608 | 299.6345 | 6241.925 | 149.3283 | 324.5057 | 2377.9705 | 37.9262 | 142.7545 | 1080.5374 | 86.1673 | 32.6173
|  | 358 | 3718.0231 | 111.1849 | 300.2397 | 6239.9361 | 149.2808 | 324.4023 | 1627.9769 | 25.9645 | 97.7308 | 1082.5262 | 86.3259 | 32.6774
|  | 359 | 3717.4387 | 111.1674 | 300.1925 | 0 | 0 | 0 | 886.0613 | 14.1318 | 53.1921 | 0 | 0 | 0
|  | 360 | 3710.8963 | 110.9718 | 299.6641 | 0 | 0 | 0 | 150.1037 | 2.394 | 9.011 | 0 | 0 | 0
|  | 361 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 362 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 363 | 2554.2 | 76.3816 | 206.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 364 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 365 | 2948.7857 | 88.1814 | 238.1218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 366 | 3139.7143 | 93.891 | 253.5398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 367 | 3330.6429 | 99.6006 | 268.9577 | 6232.4378 | 149.1014 | 324.0125 | 0 | 0 | 0 | 1090.0245 | 86.9238 | 32.9037
|  | 368 | 3521.5714 | 105.3102 | 284.3757 | 6232.9203 | 149.1129 | 324.0376 | 0 | 0 | 0 | 1089.542 | 86.8853 | 32.8891
|  | 369 | 3693.3152 | 110.446 | 298.2444 | 0 | 0 | 0 | 19.1848 | 0.30598 | 1.1517 | 0 | 0 | 0
|  | 370 | 3686.9114 | 110.2545 | 297.7273 | 0 | 0 | 0 | 216.5172 | 3.4532 | 12.998 | 0 | 0 | 0
|  | 371 | 3680.5397 | 110.064 | 297.2128 | 0 | 0 | 0 | 413.8174 | 6.6 | 24.8423 | 0 | 0 | 0
|  | 372 | 3674.2002 | 109.8744 | 296.7008 | 0 | 0 | 0 | 611.0855 | 9.7462 | 36.6847 | 0 | 0 | 0
|  | 373 | 3667.8927 | 109.6858 | 296.1915 | 0 | 0 | 0 | 808.3216 | 12.8919 | 48.5252 | 0 | 0 | 0
|  | 374 | 3661.617 | 109.4981 | 295.6847 | 0 | 0 | 0 | 1005.5258 | 16.0371 | 60.3638 | 0 | 0 | 0
|  | 375 | 3655.3732 | 109.3114 | 295.1805 | 0 | 0 | 0 | 1202.6983 | 19.1818 | 72.2005 | 0 | 0 | 0
|  | 376 | 3655.1005 | 109.3032 | 295.1585 | 6220.1793 | 148.8081 | 323.3752 | 1393.8995 | 22.2313 | 83.6787 | 1102.283 | 87.9014 | 33.2737
|  | 377 | 3662.8542 | 109.5351 | 295.7846 | 6218.6913 | 148.7725 | 323.2978 | 1237.6458 | 19.7392 | 74.2985 | 1103.7711 | 88.02 | 33.3187
|  | 378 | 3670.572 | 109.7659 | 296.4079 | 6217.0927 | 148.7343 | 323.2147 | 1526.928 | 24.3529 | 91.6647 | 1105.3696 | 88.1475 | 33.3669
|  | 379 | 3678.2533 | 109.9956 | 297.0281 | 6215.0835 | 148.6862 | 323.1103 | 1816.2467 | 28.9673 | 109.0331 | 1107.3788 | 88.3077 | 33.4276
|  | 380 | 3685.8975 | 110.2242 | 297.6454 | 6212.7646 | 148.6307 | 322.9897 | 1957.1025 | 31.2138 | 117.4889 | 1109.6977 | 88.4926 | 33.4976
|  | 381 | 3693.5038 | 110.4517 | 298.2597 | 6210.0364 | 148.5655 | 322.8479 | 2394.9962 | 38.1977 | 143.7766 | 1112.4259 | 88.7102 | 33.5799
|  | 382 | 3701.0719 | 110.678 | 298.8708 | 6207.5009 | 148.5048 | 322.7161 | 1644.9281 | 26.2349 | 98.7485 | 1114.9614 | 88.9124 | 33.6565
|  | 383 | 3700.5712 | 110.663 | 298.8304 | 0 | 0 | 0 | 902.9288 | 14.4008 | 54.2047 | 0 | 0 | 0
|  | 384 | 3694.1749 | 110.4717 | 298.3139 | 0 | 0 | 0 | 166.8251 | 2.6607 | 10.0149 | 0 | 0 | 0
|  | 385 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 386 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 387 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 388 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 389 | 2992.8462 | 89.499 | 241.6798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 390 | 3198.4615 | 95.6478 | 258.2838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 391 | 3404.0769 | 101.7966 | 274.8877 | 6195.0742 | 148.2075 | 322.07 | 0 | 0 | 0 | 1127.3881 | 89.9034 | 34.0316
|  | 392 | 3609.6923 | 107.9453 | 291.4917 | 6195.0732 | 148.2075 | 322.07 | 0 | 0 | 0 | 1127.3891 | 89.9034 | 34.0316
|  | 393 | 3676.7973 | 109.9521 | 296.9106 | 0 | 0 | 0 | 138.5103 | 2.2091 | 8.3151 | 0 | 0 | 0
|  | 394 | 3670.5391 | 109.7649 | 296.4052 | 0 | 0 | 0 | 350.384 | 5.5883 | 21.0343 | 0 | 0 | 0
|  | 395 | 3664.3124 | 109.5787 | 295.9024 | 0 | 0 | 0 | 562.226 | 8.9669 | 33.7516 | 0 | 0 | 0
|  | 396 | 3658.1173 | 109.3935 | 295.4021 | 0 | 0 | 0 | 774.0365 | 12.3451 | 46.467 | 0 | 0 | 0
|  | 397 | 3651.9537 | 109.2091 | 294.9044 | 0 | 0 | 0 | 985.8156 | 15.7227 | 59.1806 | 0 | 0 | 0
|  | 398 | 3645.8213 | 109.0258 | 294.4092 | 0 | 0 | 0 | 1197.5633 | 19.0999 | 71.8922 | 0 | 0 | 0
|  | 399 | 3639.7202 | 108.8433 | 293.9165 | 0 | 0 | 0 | 1409.2798 | 22.4766 | 84.602 | 0 | 0 | 0
|  | 400 | 3639.5078 | 108.837 | 293.8993 | 6176.8551 | 147.7717 | 321.1228 | 1260.9922 | 20.1115 | 75.7 | 1145.6073 | 91.3562 | 34.5815
|  | 401 | 3647.3058 | 109.0701 | 294.5291 | 6174.8248 | 147.7231 | 321.0173 | 1520.4942 | 24.2503 | 91.2784 | 1147.6376 | 91.5181 | 34.6428
|  | 402 | 3655.0661 | 109.3022 | 295.1557 | 6172.4285 | 147.6658 | 320.8927 | 1780.0339 | 28.3897 | 106.8591 | 1150.0338 | 91.7092 | 34.7152
|  | 403 | 3662.7881 | 109.5331 | 295.7793 | 6169.5823 | 147.5977 | 320.7447 | 2277.2119 | 36.3192 | 136.7058 | 1152.88 | 91.9362 | 34.8011
|  | 404 | 3670.4709 | 109.7629 | 296.3997 | 6166.492 | 147.5237 | 320.5841 | 2269.5291 | 36.1966 | 136.2446 | 1155.9704 | 92.1826 | 34.8944
|  | 405 | 3678.1144 | 109.9915 | 297.0169 | 6163.2601 | 147.4464 | 320.4161 | 2558.8856 | 40.8116 | 153.6152 | 1159.2023 | 92.4404 | 34.9919
|  | 406 | 3685.7187 | 110.2189 | 297.631 | 6160.4082 | 147.3782 | 320.2678 | 1779.0813 | 28.3745 | 106.802 | 1162.0541 | 92.6678 | 35.078
|  | 407 | 3685.9745 | 110.2265 | 297.6516 | 0 | 0 | 0 | 1006.6255 | 16.0546 | 60.4298 | 0 | 0 | 0
|  | 408 | 3680.5997 | 110.0658 | 297.2176 | 0 | 0 | 0 | 239.8003 | 3.8246 | 14.3957 | 0 | 0 | 0
|  | 409 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 410 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 411 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 412 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 413 | 2970 | 88.8158 | 239.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 414 | 3168 | 94.7368 | 255.8239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 415 | 3366 | 100.6579 | 271.8129 | 6149.1757 | 147.1095 | 319.6838 | 0 | 0 | 0 | 1173.2867 | 93.5635 | 35.4171
|  | 416 | 3564 | 106.5789 | 287.8019 | 6149.7212 | 147.1225 | 319.7122 | 0 | 0 | 0 | 1172.7411 | 93.52 | 35.4006
|  | 417 | 3680.1414 | 110.0521 | 297.1806 | 6150.2874 | 147.1361 | 319.7416 | 81.8586 | 1.3056 | 4.9141 | 1172.1749 | 93.4749 | 35.3835
|  | 418 | 3688.6536 | 110.3066 | 297.868 | 6150.6838 | 147.1455 | 319.7622 | 271.3464 | 4.3277 | 16.2895 | 1171.7786 | 93.4433 | 35.3715
|  | 419 | 3697.1326 | 110.5602 | 298.5527 | 6150.8692 | 147.15 | 319.7719 | 460.8674 | 7.3504 | 27.6668 | 1171.5932 | 93.4285 | 35.3659
|  | 420 | 3705.5781 | 110.8127 | 299.2347 | 6150.8439 | 147.1494 | 319.7706 | 650.4219 | 10.3736 | 39.0462 | 1171.6184 | 93.4305 | 35.3667
|  | 421 | 3713.9897 | 111.0643 | 299.9139 | 6150.6082 | 147.1437 | 319.7583 | 840.0103 | 13.3973 | 50.4276 | 1171.8541 | 93.4493 | 35.3738
|  | 422 | 3722.3671 | 111.3148 | 300.5904 | 6150.1625 | 147.1331 | 319.7351 | 1029.6329 | 16.4216 | 61.811 | 1172.2999 | 93.4848 | 35.3873
|  | 423 | 3730.7099 | 111.5643 | 301.2641 | 6149.7406 | 147.123 | 319.7132 | 872.7901 | 13.9201 | 52.3954 | 1172.7217 | 93.5185 | 35.4
|  | 424 | 3739.0186 | 111.8128 | 301.9351 | 6149.2425 | 147.1111 | 319.6873 | 1210.9814 | 19.3139 | 72.6977 | 1173.2199 | 93.5582 | 35.4151
|  | 425 | 3747.2925 | 112.0602 | 302.6032 | 6148.3342 | 147.0893 | 319.6401 | 1549.2075 | 24.7083 | 93.0022 | 1174.1281 | 93.6306 | 35.4425
|  | 426 | 3755.5308 | 112.3065 | 303.2685 | 6147.0166 | 147.0578 | 319.5716 | 1887.4692 | 30.1032 | 113.3087 | 1175.4457 | 93.7357 | 35.4822
|  | 427 | 3763.4684 | 112.5439 | 303.9095 | 6145.7995 | 147.0287 | 319.5083 | 1471.1566 | 23.4634 | 88.3166 | 1176.6628 | 93.8328 | 35.519
|  | 428 | 3768.9918 | 112.7091 | 304.3555 | 6145.1898 | 147.0141 | 319.4766 | 1057.2582 | 16.8622 | 63.4694 | 1177.2725 | 93.8814 | 35.5374
|  | 429 | 3774.4867 | 112.8734 | 304.7992 | 6145.1852 | 147.014 | 319.4764 | 643.3883 | 10.2614 | 38.6239 | 1177.2771 | 93.8817 | 35.5375
|  | 430 | 3779.9546 | 113.0369 | 305.2408 | 6145.7846 | 147.0283 | 319.5075 | 229.5454 | 3.661 | 13.7801 | 1176.6777 | 93.8339 | 35.5194
|  | 431 | 3601.125 | 107.6891 | 290.7998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 432 | 2970 | 88.8158 | 239.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 433 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 434 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 435 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 436 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 437 | 2943 | 88.0084 | 237.6546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 438 | 3132 | 93.6603 | 252.9168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 439 | 3321 | 99.3122 | 268.179 | 6147.0728 | 147.0592 | 319.5745 | 0 | 0 | 0 | 1175.3895 | 93.7312 | 35.4805
|  | 440 | 3510 | 104.9641 | 283.4413 | 6148.7154 | 147.0985 | 319.6599 | 0 | 0 | 0 | 1173.747 | 93.6002 | 35.431
|  | 441 | 3699 | 110.616 | 298.7035 | 6150.4009 | 147.1388 | 319.7475 | 0 | 0 | 0 | 1172.0615 | 93.4658 | 35.3801
|  | 442 | 3751.7524 | 112.1936 | 302.9634 | 6152.0609 | 147.1785 | 319.8338 | 136.2476 | 2.173 | 8.1792 | 1170.4015 | 93.3334 | 35.33
|  | 443 | 3757.3109 | 112.3598 | 303.4122 | 6153.5243 | 147.2135 | 319.9099 | 319.6891 | 5.0987 | 19.1916 | 1168.938 | 93.2167 | 35.2858
|  | 444 | 3762.8446 | 112.5253 | 303.8591 | 6154.7831 | 147.2436 | 319.9754 | 503.1554 | 8.0248 | 30.2055 | 1167.6792 | 93.1164 | 35.2478
|  | 445 | 3768.3532 | 112.69 | 304.3039 | 6155.8374 | 147.2688 | 320.0302 | 686.6468 | 10.9513 | 41.2208 | 1166.6249 | 93.0323 | 35.216
|  | 446 | 3773.8363 | 112.854 | 304.7467 | 6156.8722 | 147.2936 | 320.084 | 596.3065 | 9.5105 | 35.7975 | 1165.5902 | 92.9498 | 35.1847
|  | 447 | 3779.2944 | 113.0172 | 305.1875 | 6158.072 | 147.3223 | 320.1463 | 505.9913 | 8.07 | 30.3757 | 1164.3904 | 92.8541 | 35.1485
|  | 448 | 3784.7278 | 113.1797 | 305.6262 | 6159.4364 | 147.3549 | 320.2173 | 415.7008 | 6.63 | 24.9554 | 1163.0259 | 92.7453 | 35.1073
|  | 449 | 3790.1371 | 113.3414 | 306.063 | 6160.9651 | 147.3915 | 320.2967 | 325.4344 | 5.1903 | 19.5365 | 1161.4973 | 92.6234 | 35.0612
|  | 450 | 3795.5226 | 113.5025 | 306.4979 | 6162.6575 | 147.432 | 320.3847 | 235.1917 | 3.7511 | 14.119 | 1159.8048 | 92.4884 | 35.0101
|  | 451 | 3800.8848 | 113.6628 | 306.9309 | 6164.5134 | 147.4764 | 320.4812 | 144.9724 | 2.3122 | 8.703 | 1157.949 | 92.3404 | 34.9541
|  | 452 | 3806.2241 | 113.8225 | 307.3621 | 6166.5321 | 147.5247 | 320.5862 | 54.7759 | 0.87362 | 3.2883 | 1155.9302 | 92.1794 | 34.8931
|  | 453 | 3811.5409 | 113.9815 | 307.7914 | 6168.4557 | 147.5707 | 320.6862 | 346.4591 | 5.5257 | 20.7987 | 1154.0066 | 92.026 | 34.8351
|  | 454 | 3712.5 | 111.0197 | 299.7936 | 6170.5112 | 147.6199 | 320.793 | 0 | 0 | 0 | 1151.9511 | 91.8621 | 34.773
|  | 455 | 3267 | 97.6974 | 263.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 456 | 2821.5 | 84.375 | 227.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 457 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 458 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 459 | 2545.7143 | 76.1278 | 205.5728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 460 | 2715.4286 | 81.203 | 219.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 461 | 2885.1429 | 86.2782 | 232.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 462 | 3054.8571 | 91.3534 | 246.6873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 463 | 3224.5714 | 96.4286 | 260.3922 | 6181.4071 | 147.8806 | 321.3595 | 0 | 0 | 0 | 1141.0552 | 90.9932 | 34.4441
|  | 464 | 3394.2857 | 101.5038 | 274.0971 | 6184.0528 | 147.9438 | 321.497 | 0 | 0 | 0 | 1138.4096 | 90.7823 | 34.3643
|  | 465 | 3564 | 106.5789 | 287.8019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 466 | 3733.7143 | 111.6541 | 301.5068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 467 | 3759.1954 | 112.4161 | 303.5644 | 0 | 0 | 0 | 144.2331 | 2.3004 | 8.6586 | 0 | 0 | 0
|  | 468 | 3749.962 | 112.14 | 302.8188 | 0 | 0 | 0 | 323.1808 | 5.1544 | 19.4012 | 0 | 0 | 0
|  | 469 | 3740.7663 | 111.865 | 302.0762 | 0 | 0 | 0 | 417.2337 | 6.6544 | 25.0474 | 0 | 0 | 0
|  | 470 | 3731.6081 | 111.5912 | 301.3367 | 0 | 0 | 0 | 426.3919 | 6.8005 | 25.5972 | 0 | 0 | 0
|  | 471 | 3723.2812 | 111.3421 | 300.6643 | 0 | 0 | 0 | 859.0045 | 13.7002 | 51.5678 | 0 | 0 | 0
|  | 472 | 3722.7273 | 111.3256 | 300.6195 | 6193.624 | 148.1728 | 321.9946 | 1029.2727 | 16.4158 | 61.7894 | 1128.8384 | 90.019 | 34.0753
|  | 473 | 3730.1976 | 111.549 | 301.2228 | 6195.3134 | 148.2132 | 322.0824 | 784.2024 | 12.5072 | 47.0773 | 1127.149 | 89.8843 | 34.0243
|  | 474 | 3737.6402 | 111.7715 | 301.8238 | 6197.2806 | 148.2603 | 322.1847 | 539.1598 | 8.599 | 32.3669 | 1125.1817 | 89.7274 | 33.965
|  | 475 | 3745.056 | 111.9933 | 302.4226 | 6199.4742 | 148.3128 | 322.2988 | 412.944 | 6.586 | 24.7899 | 1122.9881 | 89.5525 | 33.8987
|  | 476 | 3752.4455 | 112.2143 | 303.0193 | 6201.9739 | 148.3726 | 322.4287 | 49.1545 | 0.78396 | 2.9508 | 1120.4884 | 89.3531 | 33.8233
|  | 477 | 3564 | 106.5789 | 287.8019 | 6204.7534 | 148.4391 | 322.5732 | 0 | 0 | 0 | 1117.7089 | 89.1315 | 33.7394
|  | 478 | 3326.4 | 99.4737 | 268.6151 | 6207.5137 | 148.5051 | 322.7167 | 0 | 0 | 0 | 1114.9486 | 88.9114 | 33.6561
|  | 479 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 480 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 481 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 482 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 483 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 484 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 485 | 2821.5 | 84.375 | 227.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 486 | 2970 | 88.8158 | 239.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 487 | 3118.5 | 93.2566 | 251.8267 | 6220.5405 | 148.8168 | 323.394 | 0 | 0 | 0 | 1101.9218 | 87.8726 | 33.2628
|  | 488 | 3267 | 97.6974 | 263.8184 | 6223.0517 | 148.8768 | 323.5245 | 0 | 0 | 0 | 1099.4107 | 87.6723 | 33.187
|  | 489 | 3415.5 | 102.1382 | 275.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 490 | 3564 | 106.5789 | 287.8019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 491 | 3712.5 | 111.0197 | 299.7936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 492 | 3722.3563 | 111.3145 | 300.5896 | 0 | 0 | 0 | 138.6437 | 2.2112 | 8.3231 | 0 | 0 | 0
|  | 493 | 3716.8262 | 111.1491 | 300.143 | 0 | 0 | 0 | 292.6738 | 4.6678 | 17.5698 | 0 | 0 | 0
|  | 494 | 3711.3265 | 110.9846 | 299.6989 | 0 | 0 | 0 | 446.6735 | 7.124 | 26.8147 | 0 | 0 | 0
|  | 495 | 3705.857 | 110.8211 | 299.2572 | 0 | 0 | 0 | 303.643 | 4.8428 | 18.2283 | 0 | 0 | 0
|  | 496 | 3706.3757 | 110.8366 | 299.2991 | 6231.2357 | 149.0726 | 323.95 | 451.6243 | 7.2029 | 27.1119 | 1091.2266 | 87.0197 | 32.94
|  | 497 | 3714.9289 | 111.0924 | 299.9898 | 6232.5126 | 149.1032 | 324.0164 | 1037.0711 | 16.5402 | 62.2575 | 1089.9497 | 86.9178 | 32.9014
|  | 498 | 3723.4502 | 111.3472 | 300.6779 | 6233.4745 | 149.1262 | 324.0664 | 880.0498 | 14.0359 | 52.8312 | 1088.9879 | 86.8411 | 32.8724
|  | 499 | 3731.9396 | 111.6011 | 301.3634 | 6234.3218 | 149.1465 | 324.1104 | 1168.5604 | 18.6373 | 70.1511 | 1088.1405 | 86.7736 | 32.8468
|  | 500 | 3740.3968 | 111.854 | 302.0464 | 6235.1751 | 149.1669 | 324.1548 | 833.4032 | 13.2919 | 50.0309 | 1087.2872 | 86.7055 | 32.8211
|  | 501 | 3748.8225 | 112.1059 | 302.7268 | 6236.4547 | 149.1975 | 324.2213 | 498.2775 | 7.947 | 29.9126 | 1086.0076 | 86.6035 | 32.7824
|  | 502 | 3757.2178 | 112.357 | 303.4047 | 6238.1599 | 149.2383 | 324.31 | 163.1822 | 2.6026 | 9.7962 | 1084.3024 | 86.4675 | 32.731
|  | 503 | 3593.7 | 107.4671 | 290.2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 504 | 3267 | 97.6974 | 263.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 505 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 506 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 507 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 508 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 509 | 3044.25 | 91.0362 | 245.8308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 510 | 3267 | 97.6974 | 263.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 511 | 3489.75 | 104.3586 | 281.806 | 6245.854 | 149.4223 | 324.71 | 0 | 0 | 0 | 1076.6084 | 85.8539 | 32.4987
|  | 512 | 3712.5 | 111.0197 | 299.7936 | 6247.7401 | 149.4675 | 324.808 | 0 | 0 | 0 | 1074.7222 | 85.7035 | 32.4418
|  | 513 | 3743.526 | 111.9475 | 302.2991 | 0 | 0 | 0 | 191.724 | 3.0578 | 11.5096 | 0 | 0 | 0
|  | 514 | 3738.0022 | 111.7824 | 301.853 | 0 | 0 | 0 | 419.9978 | 6.6985 | 25.2133 | 0 | 0 | 0
|  | 515 | 3732.5087 | 111.6181 | 301.4094 | 0 | 0 | 0 | 648.2413 | 10.3388 | 38.9153 | 0 | 0 | 0
|  | 516 | 3727.0453 | 111.4547 | 300.9682 | 0 | 0 | 0 | 876.4547 | 13.9785 | 52.6154 | 0 | 0 | 0
|  | 517 | 3721.612 | 111.2922 | 300.5295 | 0 | 0 | 0 | 1104.638 | 17.6178 | 66.3137 | 0 | 0 | 0
|  | 518 | 3716.2085 | 111.1306 | 300.0931 | 0 | 0 | 0 | 1332.7915 | 21.2566 | 80.0102 | 0 | 0 | 0
|  | 519 | 3710.8349 | 110.9699 | 299.6592 | 0 | 0 | 0 | 1189.6651 | 18.9739 | 71.4181 | 0 | 0 | 0
|  | 520 | 3711.4752 | 110.9891 | 299.7109 | 6244.2774 | 149.3846 | 324.628 | 1387.0248 | 22.1216 | 83.266 | 1078.185 | 85.9797 | 32.5463
|  | 521 | 3720.1502 | 111.2485 | 300.4114 | 6243.603 | 149.3685 | 324.5929 | 2071.3498 | 33.0359 | 124.3474 | 1078.8593 | 86.0334 | 32.5667
|  | 522 | 3728.7884 | 111.5068 | 301.109 | 6242.5491 | 149.3433 | 324.5381 | 1914.2116 | 30.5297 | 114.9141 | 1079.9133 | 86.1175 | 32.5985
|  | 523 | 3737.3895 | 111.764 | 301.8035 | 6241.3829 | 149.3154 | 324.4775 | 2202.6105 | 35.1294 | 132.2273 | 1081.0794 | 86.2105 | 32.6337
|  | 524 | 3745.9533 | 112.0201 | 302.4951 | 6240.2052 | 149.2872 | 324.4163 | 1897.0467 | 30.2559 | 113.8837 | 1082.2571 | 86.3044 | 32.6692
|  | 525 | 3754.4801 | 112.2751 | 303.1836 | 6238.9156 | 149.2564 | 324.3492 | 2334.0199 | 37.2252 | 140.1161 | 1083.5468 | 86.4072 | 32.7082
|  | 526 | 3762.9697 | 112.529 | 303.8692 | 6237.8151 | 149.23 | 324.292 | 1583.0303 | 25.2477 | 95.0326 | 1084.6472 | 86.495 | 32.7414
|  | 527 | 3760.7366 | 112.4622 | 303.6889 | 0 | 0 | 0 | 842.7634 | 13.4412 | 50.5928 | 0 | 0 | 0
|  | 528 | 3752.5513 | 112.2174 | 303.0279 | 0 | 0 | 0 | 108.4487 | 1.7296 | 6.5104 | 0 | 0 | 0
|  | 529 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 530 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 531 | 2554.2 | 76.3816 | 206.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 532 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 533 | 2948.7857 | 88.1814 | 238.1218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 534 | 3139.7143 | 93.891 | 253.5398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 535 | 3330.6429 | 99.6006 | 268.9577 | 6237.8529 | 149.2309 | 324.294 | 0 | 0 | 0 | 1084.6094 | 86.492 | 32.7402
|  | 536 | 3521.5714 | 105.3102 | 284.3757 | 6239.1495 | 149.2619 | 324.3614 | 0 | 0 | 0 | 1083.3128 | 86.3886 | 32.7011
|  | 537 | 3712.5 | 111.0197 | 299.7936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 538 | 3722.1511 | 111.3083 | 300.573 | 0 | 0 | 0 | 181.2775 | 2.8912 | 10.8825 | 0 | 0 | 0
|  | 539 | 3715.9065 | 111.1216 | 300.0687 | 0 | 0 | 0 | 378.4507 | 6.0359 | 22.7192 | 0 | 0 | 0
|  | 540 | 3709.6932 | 110.9358 | 299.567 | 0 | 0 | 0 | 575.5925 | 9.1801 | 34.554 | 0 | 0 | 0
|  | 541 | 3703.5111 | 110.7509 | 299.0678 | 0 | 0 | 0 | 772.7032 | 12.3238 | 46.387 | 0 | 0 | 0
|  | 542 | 3697.3601 | 110.567 | 298.5711 | 0 | 0 | 0 | 969.7828 | 15.467 | 58.2181 | 0 | 0 | 0
|  | 543 | 3691.2401 | 110.384 | 298.0769 | 0 | 0 | 0 | 1166.8313 | 18.6098 | 70.0473 | 0 | 0 | 0
|  | 544 | 3691.1147 | 110.3802 | 298.0667 | 6233.2669 | 149.1212 | 324.0556 | 1357.8853 | 21.6569 | 81.5167 | 1089.1955 | 86.8577 | 32.8787
|  | 545 | 3699.0209 | 110.6167 | 298.7052 | 6232.6222 | 149.1058 | 324.0221 | 1201.4791 | 19.1623 | 72.1273 | 1089.8402 | 86.9091 | 32.8981
|  | 546 | 3706.8921 | 110.852 | 299.3408 | 6231.8646 | 149.0877 | 323.9827 | 1490.6079 | 23.7737 | 89.4843 | 1090.5978 | 86.9695 | 32.921
|  | 547 | 3714.7278 | 111.0864 | 299.9736 | 6230.6939 | 149.0597 | 323.9218 | 1779.7722 | 28.3855 | 106.8434 | 1091.7684 | 87.0629 | 32.9563
|  | 548 | 3722.5273 | 111.3196 | 300.6034 | 6229.2111 | 149.0242 | 323.8447 | 1920.4727 | 30.6295 | 115.29 | 1093.2512 | 87.1811 | 33.0011
|  | 549 | 3730.2899 | 111.5517 | 301.2302 | 6227.3164 | 148.9789 | 323.7462 | 2358.2101 | 37.611 | 141.5683 | 1095.1459 | 87.3322 | 33.0583
|  | 550 | 3738.0151 | 111.7827 | 301.8541 | 6225.6118 | 148.9381 | 323.6576 | 1607.9849 | 25.6457 | 96.5307 | 1096.8505 | 87.4681 | 33.1098
|  | 551 | 3737.6664 | 111.7723 | 301.8259 | 0 | 0 | 0 | 865.8336 | 13.8091 | 51.9778 | 0 | 0 | 0
|  | 552 | 3731.3857 | 111.5845 | 301.3187 | 0 | 0 | 0 | 129.6143 | 2.0672 | 7.781 | 0 | 0 | 0
|  | 553 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 554 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 555 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 556 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 557 | 2992.8462 | 89.499 | 241.6798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 558 | 3198.4615 | 95.6478 | 258.2838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 559 | 3404.0769 | 101.7966 | 274.8877 | 6220.3963 | 148.8133 | 323.3865 | 0 | 0 | 0 | 1102.0661 | 87.8841 | 33.2672
|  | 560 | 3609.6923 | 107.9453 | 291.4917 | 6221.1443 | 148.8312 | 323.4253 | 0 | 0 | 0 | 1101.318 | 87.8244 | 33.2446
|  | 561 | 3715.8668 | 111.1204 | 300.0655 | 0 | 0 | 0 | 99.4409 | 1.586 | 5.9696 | 0 | 0 | 0
|  | 562 | 3709.7126 | 110.9364 | 299.5686 | 0 | 0 | 0 | 311.2104 | 4.9635 | 18.6826 | 0 | 0 | 0
|  | 563 | 3703.5894 | 110.7533 | 299.0741 | 0 | 0 | 0 | 522.9491 | 8.3405 | 31.3937 | 0 | 0 | 0
|  | 564 | 3697.497 | 110.5711 | 298.5821 | 0 | 0 | 0 | 734.6569 | 11.717 | 44.103 | 0 | 0 | 0
|  | 565 | 3691.4353 | 110.3898 | 298.0926 | 0 | 0 | 0 | 946.334 | 15.093 | 56.8104 | 0 | 0 | 0
|  | 566 | 3685.4042 | 110.2095 | 297.6056 | 0 | 0 | 0 | 1157.9805 | 18.4686 | 69.516 | 0 | 0 | 0
|  | 567 | 3679.4036 | 110.03 | 297.121 | 0 | 0 | 0 | 1369.5964 | 21.8436 | 82.2197 | 0 | 0 | 0
|  | 568 | 3679.3522 | 110.0285 | 297.1169 | 6209.4349 | 148.5511 | 322.8166 | 1221.1478 | 19.476 | 73.308 | 1113.0275 | 88.7582 | 33.5981
|  | 569 | 3687.323 | 110.2668 | 297.7605 | 6208.1724 | 148.5209 | 322.751 | 1480.477 | 23.6121 | 88.8761 | 1114.2899 | 88.8588 | 33.6362
|  | 570 | 3695.2569 | 110.5041 | 298.4012 | 6206.54 | 148.4818 | 322.6661 | 1739.8431 | 27.7487 | 104.4464 | 1115.9223 | 88.989 | 33.6855
|  | 571 | 3703.1529 | 110.7402 | 299.0388 | 6204.378 | 148.4301 | 322.5537 | 2236.8471 | 35.6754 | 134.2826 | 1118.0843 | 89.1614 | 33.7507
|  | 572 | 3711.0102 | 110.9752 | 299.6733 | 6201.8678 | 148.37 | 322.4232 | 2228.9898 | 35.5501 | 133.8109 | 1120.5945 | 89.3616 | 33.8265
|  | 573 | 3718.8283 | 111.209 | 300.3047 | 6199.1502 | 148.305 | 322.2819 | 2518.1717 | 40.1622 | 151.1711 | 1123.3121 | 89.5783 | 33.9085
|  | 574 | 3726.7836 | 111.4469 | 300.9471 | 6196.7468 | 148.2475 | 322.157 | 1738.0164 | 27.7196 | 104.3367 | 1125.7156 | 89.77 | 33.9811
|  | 575 | 3727.3777 | 111.4646 | 300.9951 | 0 | 0 | 0 | 965.2223 | 15.3943 | 57.9443 | 0 | 0 | 0
|  | 576 | 3722.0938 | 111.3066 | 300.5684 | 0 | 0 | 0 | 198.3062 | 3.1628 | 11.9047 | 0 | 0 | 0
|  | 577 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 578 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 579 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 580 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 581 | 2970 | 88.8158 | 239.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 582 | 3168 | 94.7368 | 255.8239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 583 | 3366 | 100.6579 | 271.8129 | 6186.5809 | 148.0043 | 321.6285 | 0 | 0 | 0 | 1135.8815 | 90.5807 | 34.2879
|  | 584 | 3564 | 106.5789 | 287.8019 | 6186.8631 | 148.0111 | 321.6431 | 0 | 0 | 0 | 1135.5992 | 90.5581 | 34.2794
|  | 585 | 3723.4546 | 111.3473 | 300.6783 | 6187.1196 | 148.0172 | 321.6565 | 38.5454 | 0.61476 | 2.314 | 1135.3427 | 90.5377 | 34.2717
|  | 586 | 3732.1285 | 111.6067 | 301.3787 | 6187.1813 | 148.0187 | 321.6597 | 227.8715 | 3.6343 | 13.6796 | 1135.2811 | 90.5328 | 34.2698
|  | 587 | 3740.7674 | 111.8651 | 302.0763 | 6186.9674 | 148.0136 | 321.6486 | 417.2326 | 6.6544 | 25.0473 | 1135.495 | 90.5498 | 34.2763
|  | 588 | 3749.3708 | 112.1223 | 302.7711 | 6186.4782 | 148.0019 | 321.6231 | 606.6292 | 9.6751 | 36.4172 | 1135.9841 | 90.5888 | 34.291
|  | 589 | 3757.9382 | 112.3785 | 303.4629 | 6185.7143 | 147.9836 | 321.5834 | 796.0618 | 12.6964 | 47.7892 | 1136.748 | 90.6498 | 34.3141
|  | 590 | 3765.4106 | 112.602 | 304.0663 | 6184.6758 | 147.9588 | 321.5294 | 986.5894 | 15.7351 | 59.227 | 1137.7865 | 90.7326 | 34.3455
|  | 591 | 3771.2621 | 112.777 | 304.5388 | 6183.5943 | 147.9329 | 321.4732 | 832.2379 | 13.2733 | 49.961 | 1138.8681 | 90.8188 | 34.3781
|  | 592 | 3777.0819 | 112.951 | 305.0088 | 6182.3689 | 147.9036 | 321.4095 | 1172.9181 | 18.7068 | 70.4127 | 1140.0935 | 90.9165 | 34.4151
|  | 593 | 3782.8692 | 113.1241 | 305.4761 | 6180.6661 | 147.8628 | 321.321 | 1513.6308 | 24.1408 | 90.8664 | 1141.7963 | 91.0523 | 34.4665
|  | 594 | 3788.6231 | 113.2961 | 305.9408 | 6178.4868 | 147.8107 | 321.2077 | 1854.3769 | 29.5754 | 111.3221 | 1143.9756 | 91.2261 | 34.5323
|  | 595 | 3794.343 | 113.4672 | 306.4027 | 6176.3411 | 147.7594 | 321.0961 | 1440.282 | 22.971 | 86.4631 | 1146.1213 | 91.3972 | 34.597
|  | 596 | 3800.03 | 113.6373 | 306.8619 | 6174.7381 | 147.721 | 321.0128 | 1026.22 | 16.3671 | 61.6061 | 1147.7242 | 91.5251 | 34.6454
|  | 597 | 3805.6852 | 113.8064 | 307.3186 | 6173.6772 | 147.6956 | 320.9576 | 612.1898 | 9.7638 | 36.751 | 1148.7851 | 91.6097 | 34.6775
|  | 598 | 3811.3101 | 113.9746 | 307.7728 | 6173.1576 | 147.6832 | 320.9306 | 198.1899 | 3.1609 | 11.8978 | 1149.3048 | 91.6511 | 34.6931
|  | 599 | 3601.125 | 107.6891 | 290.7998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 600 | 2970 | 88.8158 | 239.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 601 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 602 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 603 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 604 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 605 | 2943 | 88.0084 | 237.6546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 606 | 3132 | 93.6603 | 252.9168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 607 | 3321 | 99.3122 | 268.179 | 6163.6939 | 147.4568 | 320.4386 | 0 | 0 | 0 | 1158.7684 | 92.4058 | 34.9788
|  | 608 | 3510 | 104.9641 | 283.4413 | 6164.1253 | 147.4671 | 320.461 | 0 | 0 | 0 | 1158.337 | 92.3714 | 34.9658
|  | 609 | 3699 | 110.616 | 298.7035 | 6164.6001 | 147.4785 | 320.4857 | 0 | 0 | 0 | 1157.8622 | 92.3335 | 34.9515
|  | 610 | 3785.1332 | 113.1918 | 305.659 | 6165.0792 | 147.4899 | 320.5106 | 102.8668 | 1.6406 | 6.1753 | 1157.3831 | 92.2953 | 34.937
|  | 611 | 3790.8012 | 113.3613 | 306.1167 | 6165.3782 | 147.4971 | 320.5262 | 286.1988 | 4.5646 | 17.1811 | 1157.0842 | 92.2715 | 34.928
|  | 612 | 3796.4411 | 113.5299 | 306.5721 | 6165.4732 | 147.4994 | 320.5311 | 469.5589 | 7.489 | 28.1886 | 1156.9891 | 92.2639 | 34.9251
|  | 613 | 3802.0525 | 113.6977 | 307.0252 | 6165.3648 | 147.4968 | 320.5255 | 652.9475 | 10.4138 | 39.1978 | 1157.0976 | 92.2725 | 34.9284
|  | 614 | 3807.6352 | 113.8647 | 307.4761 | 6165.2378 | 147.4937 | 320.5189 | 562.5077 | 8.9714 | 33.7685 | 1157.2246 | 92.2827 | 34.9322
|  | 615 | 3813.1895 | 114.0308 | 307.9246 | 6165.2769 | 147.4947 | 320.5209 | 472.0962 | 7.5294 | 28.3409 | 1157.1854 | 92.2795 | 34.931
|  | 616 | 3818.7159 | 114.1961 | 308.3709 | 6165.4819 | 147.4996 | 320.5316 | 381.7126 | 6.0879 | 22.915 | 1156.9804 | 92.2632 | 34.9248
|  | 617 | 3824.215 | 114.3605 | 308.8149 | 6165.8525 | 147.5084 | 320.5508 | 291.3565 | 4.6468 | 17.4907 | 1156.6099 | 92.2336 | 34.9137
|  | 618 | 3829.687 | 114.5241 | 309.2568 | 6166.3882 | 147.5212 | 320.5787 | 201.0273 | 3.2062 | 12.0681 | 1156.0741 | 92.1909 | 34.8975
|  | 619 | 3835.1326 | 114.687 | 309.6965 | 6167.0889 | 147.538 | 320.6151 | 110.7246 | 1.7659 | 6.647 | 1155.3735 | 92.135 | 34.8763
|  | 620 | 3840.5521 | 114.849 | 310.1342 | 6167.9541 | 147.5587 | 320.6601 | 20.4479 | 0.32612 | 1.2275 | 1154.5083 | 92.0661 | 34.8502
|  | 621 | 3845.9458 | 115.0103 | 310.5697 | 6168.7258 | 147.5772 | 320.7002 | 312.0542 | 4.9769 | 18.7333 | 1153.7365 | 92.0045 | 34.8269
|  | 622 | 3712.5 | 111.0197 | 299.7936 | 6169.6187 | 147.5985 | 320.7466 | 0 | 0 | 0 | 1152.8436 | 91.9333 | 34.8
|  | 623 | 3267 | 97.6974 | 263.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 624 | 2821.5 | 84.375 | 227.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 625 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 626 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 627 | 2545.7143 | 76.1278 | 205.5728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 628 | 2715.4286 | 81.203 | 219.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 629 | 2885.1429 | 86.2782 | 232.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 630 | 3054.8571 | 91.3534 | 246.6873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 631 | 3224.5714 | 96.4286 | 260.3922 | 6169.7817 | 147.6024 | 320.7551 | 0 | 0 | 0 | 1152.6806 | 91.9203 | 34.7951
|  | 632 | 3394.2857 | 101.5038 | 274.0971 | 6171.2545 | 147.6377 | 320.8317 | 0 | 0 | 0 | 1151.2078 | 91.8029 | 34.7506
|  | 633 | 3564 | 106.5789 | 287.8019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 634 | 3733.7143 | 111.6541 | 301.5068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 635 | 3795.3094 | 113.4961 | 306.4807 | 0 | 0 | 0 | 108.1191 | 1.7244 | 6.4906 | 0 | 0 | 0
|  | 636 | 3786.1391 | 113.2219 | 305.7402 | 0 | 0 | 0 | 287.0038 | 4.5774 | 17.2294 | 0 | 0 | 0
|  | 637 | 3777.0059 | 112.9487 | 305.0027 | 0 | 0 | 0 | 380.9941 | 6.0765 | 22.8719 | 0 | 0 | 0
|  | 638 | 3767.9097 | 112.6767 | 304.2681 | 0 | 0 | 0 | 390.0903 | 6.2215 | 23.4179 | 0 | 0 | 0
|  | 639 | 3758.8505 | 112.4058 | 303.5366 | 0 | 0 | 0 | 823.4352 | 13.1329 | 49.4325 | 0 | 0 | 0
|  | 640 | 3755.6738 | 112.3108 | 303.28 | 6171.6851 | 147.648 | 320.8541 | 996.3262 | 15.8904 | 59.8115 | 1150.7772 | 91.7685 | 34.7376
|  | 641 | 3760.5163 | 112.4556 | 303.6711 | 6172.3647 | 147.6642 | 320.8894 | 753.8837 | 12.0237 | 45.2572 | 1150.0976 | 91.7143 | 34.7171
|  | 642 | 3765.3338 | 112.5997 | 304.0601 | 6173.4136 | 147.6893 | 320.9439 | 511.4662 | 8.1574 | 30.7044 | 1149.0487 | 91.6307 | 34.6854
|  | 643 | 3770.1271 | 112.743 | 304.4472 | 6174.751 | 147.7213 | 321.0134 | 387.8729 | 6.1862 | 23.2848 | 1147.7113 | 91.524 | 34.645
|  | 644 | 3774.897 | 112.8857 | 304.8324 | 6176.4565 | 147.7621 | 321.1021 | 26.703 | 0.42588 | 1.603 | 1146.0058 | 91.388 | 34.5936
|  | 645 | 3564 | 106.5789 | 287.8019 | 6178.4799 | 147.8105 | 321.2073 | 0 | 0 | 0 | 1143.9824 | 91.2267 | 34.5325
|  | 646 | 3326.4 | 99.4737 | 268.6151 | 6180.545 | 147.8599 | 321.3147 | 0 | 0 | 0 | 1141.9173 | 91.062 | 34.4701
|  | 647 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 648 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 649 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 650 | 2376 | 71.0526 | 191.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 651 | 2524.5 | 75.4934 | 203.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 652 | 2673 | 79.9342 | 215.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 653 | 2821.5 | 84.375 | 227.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 654 | 2970 | 88.8158 | 239.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 655 | 3118.5 | 93.2566 | 251.8267 | 6189.9722 | 148.0855 | 321.8048 | 0 | 0 | 0 | 1132.4901 | 90.3102 | 34.1856
|  | 656 | 3267 | 97.6974 | 263.8184 | 6192.4416 | 148.1445 | 321.9331 | 0 | 0 | 0 | 1130.0207 | 90.1133 | 34.111
|  | 657 | 3415.5 | 102.1382 | 275.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 658 | 3564 | 106.5789 | 287.8019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 659 | 3712.5 | 111.0197 | 299.7936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 660 | 3717.5011 | 111.1693 | 300.1975 | 0 | 0 | 0 | 143.4989 | 2.2887 | 8.6145 | 0 | 0 | 0
|  | 661 | 3711.2215 | 110.9815 | 299.6904 | 0 | 0 | 0 | 298.2785 | 4.7572 | 17.9063 | 0 | 0 | 0
|  | 662 | 3704.9734 | 110.7947 | 299.1859 | 0 | 0 | 0 | 453.0266 | 7.2253 | 27.1961 | 0 | 0 | 0
|  | 663 | 3698.7567 | 110.6088 | 298.6838 | 0 | 0 | 0 | 310.7433 | 4.956 | 18.6546 | 0 | 0 | 0
|  | 664 | 3698.4697 | 110.6002 | 298.6607 | 6199.8904 | 148.3227 | 322.3204 | 459.5303 | 7.329 | 27.5866 | 1122.572 | 89.5193 | 33.8862
|  | 665 | 3706.2076 | 110.8316 | 299.2855 | 6201.1079 | 148.3519 | 322.3837 | 1045.7924 | 16.6793 | 62.7811 | 1121.3544 | 89.4222 | 33.8494
|  | 666 | 3713.915 | 111.0621 | 299.9079 | 6202.0124 | 148.3735 | 322.4307 | 889.585 | 14.188 | 53.4036 | 1120.45 | 89.3501 | 33.8221
|  | 667 | 3721.5917 | 111.2916 | 300.5278 | 6202.8042 | 148.3924 | 322.4719 | 1178.9083 | 18.8024 | 70.7723 | 1119.6581 | 89.2869 | 33.7982
|  | 668 | 3729.2375 | 111.5203 | 301.1452 | 6203.6038 | 148.4116 | 322.5134 | 844.5625 | 13.4699 | 50.7008 | 1118.8585 | 89.2232 | 33.7741
|  | 669 | 3736.8531 | 111.748 | 301.7602 | 6204.8316 | 148.4409 | 322.5773 | 510.2469 | 8.1379 | 30.6312 | 1117.6307 | 89.1253 | 33.737
|  | 670 | 3744.4395 | 111.9749 | 302.3728 | 6206.4869 | 148.4805 | 322.6633 | 175.9605 | 2.8064 | 10.5633 | 1115.9754 | 88.9933 | 33.6871
|  | 671 | 3593.7 | 107.4671 | 290.2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 672 | 3267 | 97.6974 | 263.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 2286226.9586 |  | 184618.5382 | 1909080.9577 |  | 99249.4526 | 339293.6997 |  | 20368.5074 | 346237.4417 |  | 10451.5937
Note on C8: Peter North: (Sat-Toutlet = 2 to 5K) Condenser refrig sat temp (30ºC) minus 2ºC approach temp. Needs to be written-up and justified. Sat temp - outlet temp btw 2 to 5K. 2K taken to max deltaT and min mass flowrate.
Note on C9: Peter North: (Toutlet - sat = 5K) Evaporator refrig sat temp (5ºC) plus 5K or 2K approach temp. Needs to be written-up and justified.

## Spring_Autumn
T0 | K | 273
cp water | kJ/kg.K | 4.18
Tcond.sat | ºC | 30
T evap.sat | ºC | 5
Thot sink | ºC | 20 | 293 | K
Tcold sink | ºC | 10 | 283 | K | Approach Temp
Tcond.hot, out | ºC | 28 | 301 | K | 2 | K
Thp.hot, out | ºC | 10 | 283 | K | 5 | K
Tcond.cold, out | ºC | 25 | 298 | K | 5 | K
Thp.cold, out | ºC | 7 | 280 | K | 2 | K
Spring/Autumn
|  |  | Hot Sink | [5 empty] | Cold Sink
|  |  | Condenser |  |  | HP Evaporator |  |  | Condenser |  |  | HP Evaporator
|  |  | Qcond, hot | ṁcond, hot | Edest cond, hot | Qhp, hot | ṁhp, hot | Edest hp, hot | Qcond, cold | ṁcond, cold | Edest cond, cold | Qhp, cold | ṁhp, cold | Edest hp, cold
|  |  | kW | kg/s | kW | kW | kg/s | kW | kW | kg/s | kW | kW | kg/s | kW
|  | Total | 2182261.1703 |  | 176223.0411 | 879763.2791 |  | 45737.2033 | 640290.5163 |  | 38437.9732 | 341510.382 |  | 10308.9017 | 270707.1193
Hours
|  | 1 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 3 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 4 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 5 | 3272.7044 | 97.868 | 264.2791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 6 | 3512.1706 | 105.029 | 283.6165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 7 | 3718.4927 | 111.1989 | 300.2776 | 2837.8677 | 67.8916 | 147.5353 | 33.144 | 0.52861 | 1.9897 | 1127.3066 | 89.8969 | 34.0291
|  | 8 | 3717.5067 | 111.1695 | 300.198 | 2839.1798 | 67.923 | 147.6035 | 273.5962 | 4.3636 | 16.4246 | 1125.9945 | 89.7922 | 33.9895
|  | 9 | 3712.4356 | 111.0178 | 299.7884 | 0 | 0 | 0 | 518.1335 | 8.2637 | 31.1046 | 0 | 0 | 0
|  | 10 | 3705.1105 | 110.7988 | 299.1969 | 0 | 0 | 0 | 764.9247 | 12.1998 | 45.92 | 0 | 0 | 0
|  | 11 | 3697.8219 | 110.5808 | 298.6084 | 0 | 0 | 0 | 1011.6796 | 16.1352 | 60.7332 | 0 | 0 | 0
|  | 12 | 3690.5694 | 110.3639 | 298.0227 | 0 | 0 | 0 | 1258.3982 | 20.0701 | 75.5443 | 0 | 0 | 0
|  | 13 | 3683.353 | 110.1481 | 297.44 | 0 | 0 | 0 | 1505.0808 | 24.0045 | 90.3531 | 0 | 0 | 0
|  | 14 | 3676.1725 | 109.9334 | 296.8601 | 0 | 0 | 0 | 1751.7274 | 27.9382 | 105.1598 | 0 | 0 | 0
|  | 15 | 3669.0279 | 109.7197 | 296.2832 | 0 | 0 | 0 | 1599.2279 | 25.506 | 96.005 | 0 | 0 | 0
|  | 16 | 3664.1878 | 109.575 | 295.8923 | 2829.0195 | 67.6799 | 147.0753 | 1816.9269 | 28.9781 | 109.0739 | 1136.1548 | 90.6025 | 34.2962
|  | 17 | 3663.4534 | 109.553 | 295.833 | 2827.5987 | 67.6459 | 147.0014 | 2562.6671 | 40.8719 | 153.8422 | 1137.5755 | 90.7157 | 34.3391
|  | 18 | 3662.7215 | 109.5311 | 295.7739 | 2825.7853 | 67.6025 | 146.9072 | 2403.7549 | 38.3374 | 144.3024 | 1139.3889 | 90.8604 | 34.3938
|  | 19 | 3661.9919 | 109.5093 | 295.715 | 2823.8669 | 67.5566 | 146.8074 | 2723.7728 | 43.4414 | 163.5138 | 1141.3073 | 91.0133 | 34.4517
|  | 20 | 3661.2642 | 109.4876 | 295.6562 | 2821.9516 | 67.5108 | 146.7078 | 2405.2123 | 38.3606 | 144.3899 | 1143.2226 | 91.1661 | 34.5095
|  | 21 | 3660.5386 | 109.4659 | 295.5976 | 2819.9318 | 67.4625 | 146.6028 | 2884.8702 | 46.0107 | 173.1848 | 1145.2424 | 91.3271 | 34.5705
|  | 22 | 3659.8147 | 109.4442 | 295.5392 | 2818.1311 | 67.4194 | 146.5092 | 2087.3735 | 33.2914 | 125.3094 | 1147.0431 | 91.4707 | 34.6249
|  | 23 | 3655.0143 | 109.3007 | 295.1515 | 0 | 0 | 0 | 1293.9533 | 20.6372 | 77.6787 | 0 | 0 | 0
|  | 24 | 3647.9938 | 109.0907 | 294.5846 | 0 | 0 | 0 | 502.7532 | 8.0184 | 30.1813 | 0 | 0 | 0
|  | 25 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 26 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 27 | 2745.8788 | 82.1136 | 221.7366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 28 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 29 | 3170.076 | 94.7989 | 255.9916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 30 | 3375.3327 | 100.937 | 272.5666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 31 | 3580.5895 | 107.075 | 289.1415 | 2817.3272 | 67.4002 | 146.4674 | 0 | 0 | 0 | 1147.8471 | 91.5349 | 34.6491
|  | 32 | 3610.8818 | 107.9809 | 291.5877 | 2818.802 | 67.4355 | 146.5441 | 174.9644 | 2.7905 | 10.5035 | 1146.3722 | 91.4172 | 34.6046
|  | 33 | 3606.9574 | 107.8636 | 291.2708 | 0 | 0 | 0 | 384.1455 | 6.1267 | 23.0611 | 0 | 0 | 0
|  | 34 | 3601.0728 | 107.6876 | 290.7956 | 0 | 0 | 0 | 595.2868 | 9.4942 | 35.7363 | 0 | 0 | 0
|  | 35 | 3595.221 | 107.5126 | 290.3231 | 0 | 0 | 0 | 806.3953 | 12.8612 | 48.4096 | 0 | 0 | 0
|  | 36 | 3589.4018 | 107.3386 | 289.8532 | 0 | 0 | 0 | 1017.4712 | 16.2276 | 61.0809 | 0 | 0 | 0
|  | 37 | 3583.6152 | 107.1655 | 289.3859 | 0 | 0 | 0 | 1228.5146 | 19.5935 | 73.7503 | 0 | 0 | 0
|  | 38 | 3577.8609 | 106.9934 | 288.9212 | 0 | 0 | 0 | 1439.5256 | 22.9589 | 86.4177 | 0 | 0 | 0
|  | 39 | 3572.0508 | 106.8197 | 288.452 | 0 | 0 | 0 | 1650.5925 | 26.3252 | 99.0885 | 0 | 0 | 0
|  | 40 | 3567.7202 | 106.6902 | 288.1023 | 2810.9872 | 67.2485 | 146.1378 | 1860.1798 | 29.6679 | 111.6705 | 1154.1871 | 92.0404 | 34.8405
|  | 41 | 3567.482 | 106.6831 | 288.0831 | 2810.3662 | 67.2336 | 146.1055 | 1700.7738 | 27.1256 | 102.101 | 1154.808 | 92.09 | 34.8593
|  | 42 | 3567.2472 | 106.6761 | 288.0641 | 2809.6819 | 67.2173 | 146.07 | 2020.2969 | 32.2216 | 121.2826 | 1155.4924 | 92.1445 | 34.8799
|  | 43 | 3567.0151 | 106.6691 | 288.0454 | 2808.6113 | 67.1917 | 146.0143 | 2339.8172 | 37.3177 | 140.4641 | 1156.5629 | 92.2299 | 34.9122
|  | 44 | 3566.7849 | 106.6622 | 288.0268 | 2807.263 | 67.1594 | 145.9442 | 2499.6915 | 39.8675 | 150.0617 | 1157.9112 | 92.3374 | 34.9529
|  | 45 | 3566.556 | 106.6554 | 288.0083 | 2805.5297 | 67.1179 | 145.8541 | 2978.8528 | 47.5096 | 178.8267 | 1159.6445 | 92.4756 | 35.0053
|  | 46 | 3566.3279 | 106.6486 | 287.9899 | 2804.0584 | 67.0827 | 145.7776 | 2180.8603 | 34.7825 | 130.9216 | 1161.1158 | 92.593 | 35.0497
|  | 47 | 3562.0313 | 106.5201 | 287.6429 | 0 | 0 | 0 | 1386.9363 | 22.1202 | 83.2607 | 0 | 0 | 0
|  | 48 | 3555.535 | 106.3258 | 287.1183 | 0 | 0 | 0 | 595.212 | 9.493 | 35.7318 | 0 | 0 | 0
|  | 49 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 50 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 51 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 52 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 53 | 3217.443 | 96.2154 | 259.8166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 54 | 3438.4887 | 102.8256 | 277.6665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 55 | 3520.985 | 105.2926 | 284.3283 | 2808.761 | 67.1952 | 146.0221 | 138.5494 | 2.2097 | 8.3174 | 1156.4132 | 92.218 | 34.9077
|  | 56 | 3521.0149 | 105.2935 | 284.3307 | 2810.8715 | 67.2457 | 146.1318 | 359.5652 | 5.7347 | 21.5854 | 1154.3028 | 92.0497 | 34.844
|  | 57 | 3516.9762 | 105.1727 | 284.0046 | 0 | 0 | 0 | 584.6496 | 9.3246 | 35.0977 | 0 | 0 | 0
|  | 58 | 3510.7247 | 104.9858 | 283.4998 | 0 | 0 | 0 | 811.9467 | 12.9497 | 48.7429 | 0 | 0 | 0
|  | 59 | 3504.5058 | 104.7998 | 282.9976 | 0 | 0 | 0 | 1039.2113 | 16.5743 | 62.386 | 0 | 0 | 0
|  | 60 | 3498.3195 | 104.6148 | 282.498 | 0 | 0 | 0 | 1266.4434 | 20.1985 | 76.0272 | 0 | 0 | 0
|  | 61 | 3492.1655 | 104.4308 | 282.0011 | 0 | 0 | 0 | 1493.643 | 23.8221 | 89.6665 | 0 | 0 | 0
|  | 62 | 3486.0439 | 104.2477 | 281.5068 | 0 | 0 | 0 | 1720.8104 | 27.4451 | 103.3038 | 0 | 0 | 0
|  | 63 | 3479.9544 | 104.0656 | 281.015 | 0 | 0 | 0 | 1947.9455 | 31.0677 | 116.9392 | 0 | 0 | 0
|  | 64 | 3476.1335 | 103.9514 | 280.7065 | 2808.7819 | 67.1957 | 146.0232 | 1792.1224 | 28.5825 | 107.5848 | 1156.3923 | 92.2163 | 34.9071
|  | 65 | 3476.4034 | 103.9594 | 280.7283 | 2809.0104 | 67.2012 | 146.0351 | 2079.2119 | 33.1613 | 124.8194 | 1156.1638 | 92.1981 | 34.9002
|  | 66 | 3476.6763 | 103.9676 | 280.7503 | 2808.8952 | 67.1984 | 146.0291 | 2366.2983 | 37.74 | 142.0538 | 1156.279 | 92.2073 | 34.9037
|  | 67 | 3476.9515 | 103.9758 | 280.7725 | 2808.2644 | 67.1834 | 145.9963 | 2908.8132 | 46.3926 | 174.6221 | 1156.9098 | 92.2576 | 34.9227
|  | 68 | 3477.2276 | 103.9841 | 280.7948 | 2807.3128 | 67.1606 | 145.9468 | 2908.537 | 46.3882 | 174.6055 | 1157.8614 | 92.3334 | 34.9514
|  | 69 | 3477.5044 | 103.9924 | 280.8172 | 2806.1917 | 67.1338 | 145.8885 | 3227.5485 | 51.4761 | 193.7565 | 1158.9825 | 92.4228 | 34.9853
|  | 70 | 3477.7818 | 104.0007 | 280.8396 | 2805.4616 | 67.1163 | 145.8506 | 2397.1217 | 38.2316 | 143.9042 | 1159.7127 | 92.4811 | 35.0073
|  | 71 | 3473.9893 | 103.8872 | 280.5333 | 0 | 0 | 0 | 1570.7648 | 25.0521 | 94.2963 | 0 | 0 | 0
|  | 72 | 3467.9927 | 103.7079 | 280.0491 | 0 | 0 | 0 | 746.612 | 11.9077 | 44.8207 | 0 | 0 | 0
|  | 73 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 74 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 75 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 76 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 77 | 3192.8823 | 95.4809 | 257.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 78 | 3405.7411 | 101.8463 | 275.0221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 79 | 3435.8879 | 102.7478 | 277.4565 | 2819.01 | 67.4404 | 146.5549 | 182.7121 | 2.9141 | 10.9686 | 1146.1642 | 91.4007 | 34.5983
|  | 80 | 3436.4325 | 102.7641 | 277.5005 | 2822.1018 | 67.5144 | 146.7157 | 395.0263 | 6.3003 | 23.7143 | 1143.0724 | 91.1541 | 34.505
|  | 81 | 3436.9856 | 102.7807 | 277.5452 | 2824.9453 | 67.5824 | 146.8635 | 607.332 | 9.6863 | 36.4594 | 1140.2289 | 90.9273 | 34.4192
|  | 82 | 3437.5468 | 102.7975 | 277.5905 | 2827.5405 | 67.6445 | 146.9984 | 819.6296 | 13.0722 | 49.2041 | 1137.6338 | 90.7204 | 34.3408
|  | 83 | 3438.1154 | 102.8145 | 277.6364 | 2829.8875 | 67.7007 | 147.1204 | 1031.9199 | 16.4581 | 61.9483 | 1135.2867 | 90.5332 | 34.27
|  | 84 | 3438.6907 | 102.8317 | 277.6829 | 2831.9867 | 67.7509 | 147.2295 | 1244.2033 | 19.8438 | 74.6921 | 1133.1876 | 90.3658 | 34.2066
|  | 85 | 3439.2723 | 102.8491 | 277.7298 | 2833.838 | 67.7952 | 147.3258 | 1456.4806 | 23.2294 | 87.4356 | 1131.3362 | 90.2182 | 34.1507
|  | 86 | 3439.8596 | 102.8666 | 277.7773 | 2835.4418 | 67.8335 | 147.4092 | 1668.7522 | 26.6149 | 100.1787 | 1129.7324 | 90.0903 | 34.1023
|  | 87 | 3440.452 | 102.8843 | 277.8251 | 2837.0269 | 67.8715 | 147.4916 | 1508.5156 | 24.0593 | 90.5593 | 1128.1473 | 89.9639 | 34.0545
|  | 88 | 3441.0496 | 102.9022 | 277.8734 | 2838.38 | 67.9038 | 147.5619 | 1880.4209 | 29.9908 | 112.8856 | 1126.7943 | 89.856 | 34.0136
|  | 89 | 3441.6513 | 102.9202 | 277.9219 | 2839.2084 | 67.9236 | 147.605 | 2252.3222 | 35.9222 | 135.2116 | 1125.9658 | 89.7899 | 33.9886
|  | 90 | 3442.2559 | 102.9383 | 277.9708 | 2839.513 | 67.9309 | 147.6208 | 2624.2205 | 41.8536 | 157.5374 | 1125.6612 | 89.7656 | 33.9794
|  | 91 | 3442.8626 | 102.9564 | 278.0198 | 2839.8421 | 67.9388 | 147.6379 | 2184.5925 | 34.842 | 131.1456 | 1125.3321 | 89.7394 | 33.9695
|  | 92 | 3443.4723 | 102.9747 | 278.069 | 2840.7427 | 67.9604 | 147.6848 | 1744.9614 | 27.8303 | 104.7537 | 1124.4315 | 89.6676 | 33.9423
|  | 93 | 3444.0863 | 102.993 | 278.1186 | 2842.214 | 67.9955 | 147.7612 | 1305.3261 | 20.8186 | 78.3614 | 1122.9603 | 89.5503 | 33.8979
|  | 94 | 3444.7058 | 103.0115 | 278.1686 | 2844.2549 | 68.0444 | 147.8673 | 865.6853 | 13.8068 | 51.9689 | 1120.9194 | 89.3875 | 33.8363
|  | 95 | 3441.2331 | 102.9077 | 277.8882 | 0 | 0 | 0 | 430.1368 | 6.8602 | 25.822 | 0 | 0 | 0
|  | 96 | 3192.8823 | 95.4809 | 257.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 97 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 98 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 99 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 100 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 101 | 3163.8561 | 94.6129 | 255.4893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 102 | 3367.0395 | 100.689 | 271.8969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 103 | 3405.718 | 101.8456 | 275.0202 | 2862.614 | 68.4836 | 148.8218 | 164.505 | 2.6237 | 9.8756 | 1102.5602 | 87.9235 | 33.2821
|  | 104 | 3406.6054 | 101.8722 | 275.0919 | 2865.508 | 68.5528 | 148.9723 | 366.801 | 5.8501 | 22.0198 | 1099.6662 | 87.6927 | 33.1947
|  | 105 | 3407.4995 | 101.8989 | 275.1641 | 2868.1015 | 68.6149 | 149.1071 | 569.0903 | 9.0764 | 34.1637 | 1097.0727 | 87.4859 | 33.1165
|  | 106 | 3408.3996 | 101.9258 | 275.2368 | 2870.3946 | 68.6697 | 149.2263 | 771.3736 | 12.3026 | 46.3072 | 1094.7796 | 87.303 | 33.0472
|  | 107 | 3409.305 | 101.9529 | 275.3099 | 2872.3876 | 68.7174 | 149.3299 | 973.6516 | 15.5287 | 58.4503 | 1092.7866 | 87.1441 | 32.9871
|  | 108 | 3410.215 | 101.9801 | 275.3834 | 2874.0808 | 68.7579 | 149.4179 | 1175.925 | 18.7548 | 70.5932 | 1091.0934 | 87.009 | 32.936
|  | 109 | 3411.1289 | 102.0074 | 275.4572 | 2875.4745 | 68.7913 | 149.4904 | 1378.1946 | 21.9808 | 82.7359 | 1089.6998 | 86.8979 | 32.8939
|  | 110 | 3412.0462 | 102.0349 | 275.5313 | 2876.7676 | 68.8222 | 149.5576 | 1286.0521 | 20.5112 | 77.2044 | 1088.4067 | 86.7948 | 32.8549
|  | 111 | 3412.9668 | 102.0624 | 275.6056 | 2878.1587 | 68.8555 | 149.6299 | 1193.9062 | 19.0416 | 71.6727 | 1087.0156 | 86.6839 | 32.8129
|  | 112 | 3413.8911 | 102.09 | 275.6802 | 2879.6475 | 68.8911 | 149.7073 | 1101.7568 | 17.5719 | 66.1408 | 1085.5268 | 86.5651 | 32.7679
|  | 113 | 3414.8191 | 102.1178 | 275.7552 | 2881.2337 | 68.929 | 149.7898 | 1009.6035 | 16.1021 | 60.6086 | 1083.9405 | 86.4386 | 32.72
|  | 114 | 3415.7511 | 102.1457 | 275.8304 | 2882.9172 | 68.9693 | 149.8773 | 917.4463 | 14.6323 | 55.0762 | 1082.2571 | 86.3044 | 32.6692
|  | 115 | 3416.6873 | 102.1737 | 275.906 | 2884.6974 | 69.0119 | 149.9699 | 825.2849 | 13.1624 | 49.5436 | 1080.4768 | 86.1624 | 32.6155
|  | 116 | 3417.6279 | 102.2018 | 275.982 | 2886.5743 | 69.0568 | 150.0675 | 733.1191 | 11.6925 | 44.0107 | 1078.5999 | 86.0128 | 32.5588
|  | 117 | 3418.5728 | 102.23 | 276.0583 | 2888.2704 | 69.0974 | 150.1556 | 1051.4624 | 16.7697 | 63.1215 | 1076.9038 | 85.8775 | 32.5076
|  | 118 | 3419.5217 | 102.2584 | 276.1349 | 2890.0477 | 69.1399 | 150.248 | 571.5812 | 9.1161 | 34.3132 | 1075.1265 | 85.7358 | 32.454
|  | 119 | 3416.3466 | 102.1635 | 275.8785 | 0 | 0 | 0 | 95.824 | 1.5283 | 5.7525 | 0 | 0 | 0
|  | 120 | 3033.2382 | 90.7069 | 244.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 121 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 122 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 123 | 2736.7563 | 81.8408 | 220.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 124 | 2919.2067 | 87.2969 | 235.7332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 125 | 3101.6571 | 92.7529 | 250.4666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 126 | 3284.1075 | 98.209 | 265.1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 127 | 3383.5081 | 101.1815 | 273.2267 | 2903.6572 | 69.4655 | 150.9556 | 83.0498 | 1.3246 | 4.9857 | 1061.517 | 84.6505 | 32.0432
|  | 128 | 3385.5819 | 101.2435 | 273.3942 | 2906.0103 | 69.5218 | 151.0779 | 263.4265 | 4.2014 | 15.814 | 1059.1639 | 84.4628 | 31.9721
|  | 129 | 3383.5204 | 101.1818 | 273.2277 | 0 | 0 | 0 | 447.9384 | 7.1442 | 26.8907 | 0 | 0 | 0
|  | 130 | 3379.0875 | 101.0493 | 272.8698 | 0 | 0 | 0 | 634.8218 | 10.1247 | 38.1097 | 0 | 0 | 0
|  | 131 | 3374.682 | 100.9175 | 272.514 | 0 | 0 | 0 | 821.6776 | 13.1049 | 49.327 | 0 | 0 | 0
|  | 132 | 3370.304 | 100.7866 | 272.1605 | 0 | 0 | 0 | 1008.5061 | 16.0846 | 60.5427 | 0 | 0 | 0
|  | 133 | 3365.9532 | 100.6565 | 271.8091 | 0 | 0 | 0 | 1104.082 | 17.609 | 66.2803 | 0 | 0 | 0
|  | 134 | 3361.6297 | 100.5272 | 271.46 | 0 | 0 | 0 | 1108.4056 | 17.6779 | 66.5399 | 0 | 0 | 0
|  | 135 | 3357.3333 | 100.3987 | 271.113 | 0 | 0 | 0 | 1568.828 | 25.0212 | 94.18 | 0 | 0 | 0
|  | 136 | 3355.4579 | 100.3426 | 270.9616 | 2906.3506 | 69.5299 | 151.0956 | 1753.1538 | 27.961 | 105.2455 | 1058.8237 | 84.4357 | 31.9619
|  | 137 | 3357.7288 | 100.4106 | 271.145 | 2906.4977 | 69.5334 | 151.1032 | 1495.4523 | 23.8509 | 89.7751 | 1058.6765 | 84.424 | 31.9574
|  | 138 | 3359.9973 | 100.4784 | 271.3282 | 2906.9653 | 69.5446 | 151.1275 | 1237.7532 | 19.7409 | 74.3049 | 1058.209 | 84.3867 | 31.9433
|  | 139 | 3362.2641 | 100.5462 | 271.5112 | 2907.6664 | 69.5614 | 151.164 | 1107.7712 | 17.6678 | 66.5018 | 1057.5078 | 84.3308 | 31.9221
|  | 140 | 3364.5295 | 100.6139 | 271.6942 | 2908.687 | 69.5858 | 151.217 | 722.3598 | 11.5209 | 43.3648 | 1056.4872 | 84.2494 | 31.8913
|  | 141 | 3366.7947 | 100.6817 | 271.8771 | 2910.1125 | 69.6199 | 151.2912 | 464.6641 | 7.4109 | 27.8948 | 1055.0617 | 84.1357 | 31.8483
|  | 142 | 3369.0603 | 100.7494 | 272.06 | 2911.856 | 69.6616 | 151.3818 | 206.9679 | 3.3009 | 12.4247 | 1053.3182 | 83.9967 | 31.7957
|  | 143 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 144 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 145 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 146 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 147 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 148 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 149 | 3033.2382 | 90.7069 | 244.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 150 | 3192.8823 | 95.4809 | 257.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 151 | 3345.6978 | 100.0508 | 270.1735 | 2919.976 | 69.8559 | 151.8039 | 6.8287 | 0.10891 | 0.40994 | 1045.1982 | 83.3491 | 31.5506
|  | 152 | 3348.1555 | 100.1243 | 270.3719 | 2921.7629 | 69.8986 | 151.8968 | 164.0151 | 2.6159 | 9.8462 | 1043.4114 | 83.2066 | 31.4966
|  | 153 | 3346.4667 | 100.0738 | 270.2355 | 0 | 0 | 0 | 325.348 | 5.189 | 19.5313 | 0 | 0 | 0
|  | 154 | 3342.3787 | 99.9515 | 269.9054 | 0 | 0 | 0 | 489.0801 | 7.8003 | 29.3605 | 0 | 0 | 0
|  | 155 | 3338.3169 | 99.83 | 269.5774 | 0 | 0 | 0 | 652.7861 | 10.4113 | 39.1881 | 0 | 0 | 0
|  | 156 | 3334.2811 | 99.7094 | 269.2515 | 0 | 0 | 0 | 816.466 | 13.0218 | 49.0142 | 0 | 0 | 0
|  | 157 | 3330.2712 | 99.5895 | 268.9277 | 0 | 0 | 0 | 980.1199 | 15.6319 | 58.8386 | 0 | 0 | 0
|  | 158 | 3326.2873 | 99.4703 | 268.606 | 0 | 0 | 0 | 1143.748 | 18.2416 | 68.6616 | 0 | 0 | 0
|  | 159 | 3322.3291 | 99.3519 | 268.2864 | 0 | 0 | 0 | 988.062 | 15.7586 | 59.3154 | 0 | 0 | 0
|  | 160 | 3320.8117 | 99.3066 | 268.1638 | 2918.9523 | 69.8314 | 151.7507 | 1149.2235 | 18.3289 | 68.9903 | 1046.2219 | 83.4308 | 31.5815
|  | 161 | 3323.4461 | 99.3853 | 268.3766 | 2918.6208 | 69.8235 | 151.7335 | 1785.1656 | 28.4715 | 107.1672 | 1046.5535 | 83.4572 | 31.5915
|  | 162 | 3326.0746 | 99.464 | 268.5888 | 2917.9422 | 69.8072 | 151.6982 | 1622.893 | 25.8835 | 97.4256 | 1047.232 | 83.5113 | 31.612
|  | 163 | 3328.6969 | 99.5424 | 268.8006 | 2917.1323 | 69.7879 | 151.6561 | 1939.5589 | 30.934 | 116.4358 | 1048.042 | 83.5759 | 31.6364
|  | 164 | 3331.3128 | 99.6206 | 269.0118 | 2916.3207 | 69.7684 | 151.6139 | 1585.726 | 25.2907 | 95.1944 | 1048.8535 | 83.6406 | 31.6609
|  | 165 | 3333.9229 | 99.6987 | 269.2226 | 2915.9597 | 69.7598 | 151.5951 | 1231.8989 | 19.6475 | 73.9535 | 1049.2145 | 83.6694 | 31.6718
|  | 166 | 3336.5281 | 99.7766 | 269.433 | 2916.0486 | 69.7619 | 151.5998 | 878.0766 | 14.0044 | 52.7128 | 1049.1256 | 83.6623 | 31.6691
|  | 167 | 3334.9869 | 99.7305 | 269.3085 | 0 | 0 | 0 | 528.4007 | 8.4274 | 31.721 | 0 | 0 | 0
|  | 168 | 3331.0563 | 99.6129 | 268.9911 | 0 | 0 | 0 | 181.1143 | 2.8886 | 10.8727 | 0 | 0 | 0
|  | 169 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 170 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 171 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 172 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 173 | 3272.7044 | 97.868 | 264.2791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 174 | 3313.3102 | 99.0822 | 267.5581 | 0 | 0 | 0 | 198.8603 | 3.1716 | 11.938 | 0 | 0 | 0
|  | 175 | 3311.9417 | 99.0413 | 267.4476 | 2916.1215 | 69.7637 | 151.6036 | 439.695 | 7.0127 | 26.3958 | 1049.0527 | 83.6565 | 31.6669
|  | 176 | 3314.7239 | 99.1245 | 267.6722 | 2916.601 | 69.7751 | 151.6285 | 676.379 | 10.7875 | 40.6044 | 1048.5732 | 83.6183 | 31.6524
|  | 177 | 3313.3589 | 99.0837 | 267.562 | 0 | 0 | 0 | 917.2102 | 14.6286 | 55.062 | 0 | 0 | 0
|  | 178 | 3309.6029 | 98.9714 | 267.2587 | 0 | 0 | 0 | 1160.4323 | 18.5077 | 69.6632 | 0 | 0 | 0
|  | 179 | 3305.4308 | 98.8466 | 266.9218 | 0 | 0 | 0 | 1404.0706 | 22.3935 | 84.2893 | 0 | 0 | 0
|  | 180 | 3300.8438 | 98.7094 | 266.5514 | 0 | 0 | 0 | 1648.1238 | 26.2859 | 98.9403 | 0 | 0 | 0
|  | 181 | 3296.2831 | 98.5731 | 266.1831 | 0 | 0 | 0 | 1892.1507 | 30.1778 | 113.5897 | 0 | 0 | 0
|  | 182 | 3291.7486 | 98.4375 | 265.8169 | 0 | 0 | 0 | 2136.1514 | 34.0694 | 128.2376 | 0 | 0 | 0
|  | 183 | 3287.2402 | 98.3026 | 265.4529 | 0 | 0 | 0 | 1981.0156 | 31.5951 | 118.9245 | 0 | 0 | 0
|  | 184 | 3285.142 | 98.2399 | 265.2834 | 2899.6441 | 69.3695 | 150.7469 | 2195.9727 | 35.0235 | 131.8288 | 1065.5301 | 84.9705 | 32.1643
|  | 185 | 3287.1813 | 98.3009 | 265.4481 | 2897.1916 | 69.3108 | 150.6194 | 2938.9392 | 46.873 | 176.4306 | 1067.9827 | 85.1661 | 32.2383
|  | 186 | 3289.2105 | 98.3616 | 265.612 | 2894.3245 | 69.2422 | 150.4704 | 2777.2659 | 44.2945 | 166.7251 | 1070.8497 | 85.3947 | 32.3249
|  | 187 | 3291.2294 | 98.4219 | 265.775 | 2891.3309 | 69.1706 | 150.3147 | 3094.5353 | 49.3546 | 185.7714 | 1073.8434 | 85.6334 | 32.4153
|  | 188 | 3293.2374 | 98.482 | 265.9371 | 2888.3188 | 69.0985 | 150.1581 | 2773.2391 | 44.2303 | 166.4833 | 1076.8554 | 85.8736 | 32.5062
|  | 189 | 3295.2348 | 98.5417 | 266.0984 | 2885.1808 | 69.0235 | 149.995 | 3250.174 | 51.8369 | 195.1147 | 1079.9934 | 86.1239 | 32.6009
|  | 190 | 3297.2213 | 98.6011 | 266.2589 | 2882.2407 | 68.9531 | 149.8422 | 2449.9669 | 39.0744 | 147.0766 | 1082.9335 | 86.3583 | 32.6897
|  | 191 | 3295.0772 | 98.537 | 266.0857 | 0 | 0 | 0 | 1653.8904 | 26.3778 | 99.2865 | 0 | 0 | 0
|  | 192 | 3290.6017 | 98.4032 | 265.7243 | 0 | 0 | 0 | 860.1453 | 13.7184 | 51.6363 | 0 | 0 | 0
|  | 193 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 194 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 195 | 2745.8788 | 82.1136 | 221.7366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 196 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 197 | 3170.076 | 94.7989 | 255.9916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 198 | 3269.0402 | 97.7584 | 263.9832 | 0 | 0 | 0 | 106.2926 | 1.6953 | 6.381 | 0 | 0 | 0
|  | 199 | 3267.0611 | 97.6992 | 263.8233 | 2873.5743 | 68.7458 | 149.3916 | 313.5284 | 5.0005 | 18.8218 | 1091.5999 | 87.0494 | 32.9513
|  | 200 | 3269.2085 | 97.7634 | 263.9967 | 2873.6929 | 68.7486 | 149.3978 | 516.6377 | 8.2398 | 31.0148 | 1091.4813 | 87.04 | 32.9477
|  | 201 | 3267.2347 | 97.7044 | 263.8374 | 0 | 0 | 0 | 723.8682 | 11.5449 | 43.4553 | 0 | 0 | 0
|  | 202 | 3262.9414 | 97.576 | 263.4907 | 0 | 0 | 0 | 933.4183 | 14.8871 | 56.035 | 0 | 0 | 0
|  | 203 | 3258.6733 | 97.4484 | 263.146 | 0 | 0 | 0 | 1142.9431 | 18.2288 | 68.6133 | 0 | 0 | 0
|  | 204 | 3254.4303 | 97.3215 | 262.8034 | 0 | 0 | 0 | 1352.4428 | 21.5701 | 81.19 | 0 | 0 | 0
|  | 205 | 3250.2124 | 97.1953 | 262.4628 | 0 | 0 | 0 | 1561.9174 | 24.911 | 93.7652 | 0 | 0 | 0
|  | 206 | 3246.0194 | 97.07 | 262.1242 | 0 | 0 | 0 | 1771.3671 | 28.2515 | 106.3389 | 0 | 0 | 0
|  | 207 | 3241.8513 | 96.9453 | 261.7876 | 0 | 0 | 0 | 1980.7919 | 31.5916 | 118.9111 | 0 | 0 | 0
|  | 208 | 3240.0166 | 96.8904 | 261.6394 | 2854.4477 | 68.2882 | 148.3973 | 2187.8834 | 34.8945 | 131.3432 | 1110.7265 | 88.5747 | 33.5286
|  | 209 | 3242.2925 | 96.9585 | 261.8232 | 2852.1031 | 68.2321 | 148.2754 | 2025.9634 | 32.312 | 121.6228 | 1113.0712 | 88.7617 | 33.5994
|  | 210 | 3244.5583 | 97.0263 | 262.0062 | 2849.6352 | 68.1731 | 148.1471 | 2342.9858 | 37.3682 | 140.6543 | 1115.5391 | 88.9585 | 33.6739
|  | 211 | 3246.8133 | 97.0937 | 262.1883 | 2846.7215 | 68.1034 | 147.9956 | 2660.019 | 42.4245 | 159.6865 | 1118.4528 | 89.1908 | 33.7618
|  | 212 | 3249.0566 | 97.1608 | 262.3694 | 2843.4706 | 68.0256 | 147.8266 | 2817.4198 | 44.9349 | 169.1356 | 1121.7036 | 89.4501 | 33.86
|  | 213 | 3251.2876 | 97.2275 | 262.5496 | 2839.7756 | 67.9372 | 147.6345 | 3294.1212 | 52.5378 | 197.753 | 1125.3987 | 89.7447 | 33.9715
|  | 214 | 3253.5056 | 97.2938 | 262.7287 | 2836.2837 | 67.8537 | 147.4529 | 2493.6826 | 39.7717 | 149.701 | 1128.8905 | 90.0232 | 34.0769
|  | 215 | 3251.6213 | 97.2375 | 262.5765 | 0 | 0 | 0 | 1697.3463 | 27.0709 | 101.8952 | 0 | 0 | 0
|  | 216 | 3247.4782 | 97.1136 | 262.242 | 0 | 0 | 0 | 903.2688 | 14.4062 | 54.2251 | 0 | 0 | 0
|  | 217 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 218 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 219 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 220 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 221 | 3217.443 | 96.2154 | 259.8166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 222 | 3227.434 | 96.5142 | 260.6234 | 0 | 0 | 0 | 211.0547 | 3.3661 | 12.6701 | 0 | 0 | 0
|  | 223 | 3225.7001 | 96.4623 | 260.4833 | 2822.52 | 67.5244 | 146.7374 | 433.8342 | 6.9192 | 26.044 | 1142.6542 | 91.1207 | 34.4924
|  | 224 | 3228.0571 | 96.5328 | 260.6737 | 2822.0262 | 67.5126 | 146.7117 | 652.523 | 10.4071 | 39.1723 | 1143.148 | 91.1601 | 34.5073
|  | 225 | 3226.3249 | 96.481 | 260.5338 | 0 | 0 | 0 | 875.3008 | 13.9601 | 52.5461 | 0 | 0 | 0
|  | 226 | 3222.355 | 96.3623 | 260.2132 | 0 | 0 | 0 | 1100.3165 | 17.5489 | 66.0543 | 0 | 0 | 0
|  | 227 | 3218.409 | 96.2443 | 259.8946 | 0 | 0 | 0 | 1325.3082 | 21.1373 | 79.561 | 0 | 0 | 0
|  | 228 | 3214.4869 | 96.127 | 259.5778 | 0 | 0 | 0 | 1550.276 | 24.7253 | 93.0663 | 0 | 0 | 0
|  | 229 | 3210.5886 | 96.0104 | 259.2631 | 0 | 0 | 0 | 1775.2199 | 28.3129 | 106.5701 | 0 | 0 | 0
|  | 230 | 3206.7141 | 95.8946 | 258.9502 | 0 | 0 | 0 | 2000.1402 | 31.9002 | 120.0726 | 0 | 0 | 0
|  | 231 | 3202.8632 | 95.7794 | 258.6392 | 0 | 0 | 0 | 2225.0367 | 35.487 | 133.5736 | 0 | 0 | 0
|  | 232 | 3201.2569 | 95.7314 | 258.5095 | 2798.2244 | 66.9432 | 145.4743 | 2066.9989 | 32.9665 | 124.0863 | 1166.9499 | 93.0582 | 35.2258
|  | 233 | 3203.7218 | 95.8051 | 258.7085 | 2795.7718 | 66.8845 | 145.3468 | 2351.8935 | 37.5103 | 141.1891 | 1169.4025 | 93.2538 | 35.2998
|  | 234 | 3206.1753 | 95.8784 | 258.9067 | 2792.9836 | 66.8178 | 145.2019 | 2636.7993 | 42.0542 | 158.2926 | 1172.1906 | 93.4761 | 35.384
|  | 235 | 3208.6168 | 95.9515 | 259.1038 | 2789.6883 | 66.739 | 145.0305 | 3177.1479 | 50.6722 | 190.7308 | 1175.4859 | 93.7389 | 35.4835
|  | 236 | 3211.045 | 96.0241 | 259.2999 | 2786.0809 | 66.6527 | 144.843 | 3174.7196 | 50.6335 | 190.585 | 1179.0933 | 94.0266 | 35.5923
|  | 237 | 3213.4598 | 96.0963 | 259.4949 | 2782.3128 | 66.5625 | 144.6471 | 3491.5931 | 55.6873 | 209.6076 | 1182.8614 | 94.3271 | 35.7061
|  | 238 | 3215.861 | 96.1681 | 259.6888 | 2778.9447 | 66.4819 | 144.472 | 2659.0424 | 42.409 | 159.6279 | 1186.2295 | 94.5957 | 35.8078
|  | 239 | 3214.1972 | 96.1183 | 259.5545 | 0 | 0 | 0 | 1830.5568 | 29.1955 | 109.8921 | 0 | 0 | 0
|  | 240 | 3210.3649 | 96.0037 | 259.245 | 0 | 0 | 0 | 1004.2397 | 16.0166 | 60.2866 | 0 | 0 | 0
|  | 241 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 242 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 243 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 244 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 245 | 3192.8823 | 95.4809 | 257.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 246 | 3191.8276 | 95.4494 | 257.7481 | 0 | 0 | 0 | 213.9136 | 3.4117 | 12.8417 | 0 | 0 | 0
|  | 247 | 3190.3144 | 95.4041 | 257.6259 | 2770.4911 | 66.2797 | 144.0325 | 428.2856 | 6.8307 | 25.7109 | 1194.6831 | 95.2698 | 36.0629
|  | 248 | 3192.859 | 95.4802 | 257.8313 | 2771.0415 | 66.2929 | 144.0611 | 638.5998 | 10.185 | 38.3365 | 1194.1327 | 95.2259 | 36.0463
|  | 249 | 3195.3989 | 95.5562 | 258.0364 | 2771.3547 | 66.3004 | 144.0774 | 848.9187 | 13.5394 | 50.9624 | 1193.8196 | 95.2009 | 36.0369
|  | 250 | 3197.9335 | 95.632 | 258.2411 | 2771.431 | 66.3022 | 144.0814 | 1059.2429 | 16.8938 | 63.5886 | 1193.7433 | 95.1948 | 36.0346
|  | 251 | 3200.4624 | 95.7076 | 258.4453 | 2771.2707 | 66.2983 | 144.073 | 1269.5729 | 20.2484 | 76.2151 | 1193.9035 | 95.2076 | 36.0394
|  | 252 | 3202.9849 | 95.783 | 258.649 | 2770.8744 | 66.2889 | 144.0524 | 1479.9091 | 23.603 | 88.842 | 1194.2999 | 95.2392 | 36.0514
|  | 253 | 3205.5007 | 95.8583 | 258.8522 | 2770.2422 | 66.2737 | 144.0196 | 1690.2522 | 26.9578 | 101.4694 | 1194.932 | 95.2896 | 36.0705
|  | 254 | 3208.0091 | 95.9333 | 259.0548 | 2769.3746 | 66.253 | 143.9745 | 1900.6026 | 30.3126 | 114.0971 | 1195.7996 | 95.3588 | 36.0966
|  | 255 | 3210.5099 | 96.0081 | 259.2567 | 2768.5235 | 66.2326 | 143.9302 | 1738.4577 | 27.7266 | 104.3632 | 1196.6508 | 95.4267 | 36.1223
|  | 256 | 3213.0032 | 96.0826 | 259.458 | 2767.5808 | 66.2101 | 143.8812 | 2108.4673 | 33.6279 | 126.5757 | 1197.5934 | 95.5019 | 36.1508
|  | 257 | 3215.4883 | 96.1569 | 259.6587 | 2766.1882 | 66.1768 | 143.8088 | 2478.4852 | 39.5293 | 148.7886 | 1198.986 | 95.6129 | 36.1928
|  | 258 | 3217.9642 | 96.231 | 259.8586 | 2764.3463 | 66.1327 | 143.7131 | 2848.5122 | 45.4308 | 171.0021 | 1200.828 | 95.7598 | 36.2484
|  | 259 | 3220.4304 | 96.3047 | 260.0578 | 2762.6034 | 66.091 | 143.6224 | 2407.0247 | 38.3895 | 144.4987 | 1202.5708 | 95.8988 | 36.301
|  | 260 | 3222.8878 | 96.3782 | 260.2562 | 2761.5069 | 66.0648 | 143.5654 | 1965.546 | 31.3484 | 117.9958 | 1203.6674 | 95.9862 | 36.3341
|  | 261 | 3225.3381 | 96.4515 | 260.4541 | 2761.0557 | 66.054 | 143.542 | 1524.0744 | 24.3074 | 91.4934 | 1204.1185 | 96.0222 | 36.3478
|  | 262 | 3227.7825 | 96.5246 | 260.6515 | 2761.2491 | 66.0586 | 143.552 | 1082.6086 | 17.2665 | 64.9912 | 1203.9251 | 96.0068 | 36.3419
|  | 263 | 3226.1797 | 96.4767 | 260.5221 | 0 | 0 | 0 | 645.1902 | 10.2901 | 38.7321 | 0 | 0 | 0
|  | 264 | 3192.8823 | 95.4809 | 257.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 265 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 266 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 267 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 268 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 269 | 3163.8561 | 94.6129 | 255.4893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 270 | 3204.971 | 95.8424 | 258.8094 | 0 | 0 | 0 | 162.0685 | 2.5848 | 9.7293 | 0 | 0 | 0
|  | 271 | 3203.5322 | 95.7994 | 258.6932 | 2767.0863 | 66.1982 | 143.8555 | 366.6907 | 5.8483 | 22.0132 | 1198.0879 | 95.5413 | 36.1657
|  | 272 | 3206.1505 | 95.8777 | 258.9047 | 2768.8791 | 66.2411 | 143.9487 | 567.2559 | 9.0471 | 34.0536 | 1196.2951 | 95.3983 | 36.1116
|  | 273 | 3208.7664 | 95.9559 | 259.1159 | 2770.4462 | 66.2786 | 144.0302 | 767.8234 | 12.246 | 46.094 | 1194.728 | 95.2734 | 36.0643
|  | 274 | 3211.3795 | 96.0341 | 259.3269 | 2771.7878 | 66.3107 | 144.0999 | 968.3937 | 15.4449 | 58.1347 | 1193.3864 | 95.1664 | 36.0238
|  | 275 | 3213.9892 | 96.1121 | 259.5377 | 2772.9041 | 66.3374 | 144.158 | 1168.9675 | 18.6438 | 70.1756 | 1192.2701 | 95.0774 | 35.9901
|  | 276 | 3216.595 | 96.19 | 259.7481 | 2773.7953 | 66.3587 | 144.2043 | 1369.545 | 21.8428 | 82.2166 | 1191.3789 | 95.0063 | 35.9632
|  | 277 | 3219.1965 | 96.2678 | 259.9582 | 2774.4617 | 66.3747 | 144.2389 | 1570.127 | 25.0419 | 94.258 | 1190.7125 | 94.9532 | 35.9431
|  | 278 | 3221.7932 | 96.3455 | 260.1679 | 2775.1021 | 66.39 | 144.2722 | 1476.3051 | 23.5455 | 88.6257 | 1190.0721 | 94.9021 | 35.9238
|  | 279 | 3224.3855 | 96.423 | 260.3772 | 2775.9152 | 66.4095 | 144.3145 | 1382.4876 | 22.0492 | 82.9936 | 1189.2591 | 94.8372 | 35.8992
|  | 280 | 3226.9736 | 96.5004 | 260.5862 | 2776.9004 | 66.433 | 144.3657 | 1288.6742 | 20.553 | 77.3618 | 1188.2738 | 94.7587 | 35.8695
|  | 281 | 3229.5581 | 96.5777 | 260.7949 | 2778.0576 | 66.4607 | 144.4259 | 1194.8646 | 19.0569 | 71.7302 | 1187.1167 | 94.6664 | 35.8345
|  | 282 | 3232.1392 | 96.6549 | 261.0033 | 2779.3862 | 66.4925 | 144.495 | 1101.0582 | 17.5607 | 66.0988 | 1185.788 | 94.5604 | 35.7944
|  | 283 | 3235.599 | 96.7583 | 261.2827 | 2780.8866 | 66.5284 | 144.573 | 1006.3733 | 16.0506 | 60.4147 | 1184.2877 | 94.4408 | 35.7491
|  | 284 | 3239.0545 | 96.8617 | 261.5617 | 2782.5588 | 66.5684 | 144.6599 | 911.6926 | 14.5406 | 54.7308 | 1182.6154 | 94.3074 | 35.6987
|  | 285 | 3242.5059 | 96.9649 | 261.8405 | 2784.1256 | 66.6059 | 144.7413 | 1227.5293 | 19.5778 | 73.6911 | 1181.0486 | 94.1825 | 35.6514
|  | 286 | 3245.9531 | 97.068 | 262.1188 | 2785.8487 | 66.6471 | 144.8309 | 745.1498 | 11.8844 | 44.7329 | 1179.3255 | 94.0451 | 35.5994
|  | 287 | 3245.3364 | 97.0495 | 262.069 | 0 | 0 | 0 | 266.8342 | 4.2557 | 16.0186 | 0 | 0 | 0
|  | 288 | 3033.2382 | 90.7069 | 244.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 289 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 290 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 291 | 2736.7563 | 81.8408 | 220.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 292 | 2919.2067 | 87.2969 | 235.7332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 293 | 3101.6571 | 92.7529 | 250.4666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 294 | 3231.59 | 96.6385 | 260.959 | 0 | 0 | 0 | 52.5175 | 0.8376 | 3.1527 | 0 | 0 | 0
|  | 295 | 3231.1331 | 96.6248 | 260.9221 | 2802.7455 | 67.0513 | 145.7094 | 235.4248 | 3.7548 | 14.133 | 1162.4287 | 92.6977 | 35.0893
|  | 296 | 3234.7565 | 96.7331 | 261.2147 | 2805.7854 | 67.1241 | 145.8674 | 414.2518 | 6.6069 | 24.8684 | 1159.3889 | 92.4553 | 34.9975
|  | 297 | 3234.304 | 96.7196 | 261.1781 | 0 | 0 | 0 | 597.1548 | 9.524 | 35.8484 | 0 | 0 | 0
|  | 298 | 3231.6338 | 96.6398 | 260.9625 | 0 | 0 | 0 | 782.2754 | 12.4765 | 46.9616 | 0 | 0 | 0
|  | 299 | 3228.9841 | 96.5605 | 260.7485 | 0 | 0 | 0 | 967.3756 | 15.4286 | 58.0736 | 0 | 0 | 0
|  | 300 | 3226.3545 | 96.4819 | 260.5362 | 0 | 0 | 0 | 1152.4555 | 18.3805 | 69.1843 | 0 | 0 | 0
|  | 301 | 3223.7452 | 96.4039 | 260.3255 | 0 | 0 | 0 | 1246.29 | 19.877 | 74.8174 | 0 | 0 | 0
|  | 302 | 3221.1561 | 96.3264 | 260.1164 | 0 | 0 | 0 | 1248.8792 | 19.9183 | 74.9728 | 0 | 0 | 0
|  | 303 | 3218.5869 | 96.2496 | 259.9089 | 0 | 0 | 0 | 1707.5744 | 27.234 | 102.5092 | 0 | 0 | 0
|  | 304 | 3218.2809 | 96.2405 | 259.8842 | 2813.3583 | 67.3052 | 146.2611 | 1890.3308 | 30.1488 | 113.4805 | 1151.8159 | 91.8513 | 34.7689
|  | 305 | 3222.0584 | 96.3534 | 260.1893 | 2814.839 | 67.3406 | 146.3381 | 1631.1227 | 26.0147 | 97.9197 | 1150.3353 | 91.7333 | 34.7243
|  | 306 | 3225.8306 | 96.4662 | 260.4939 | 2816.7104 | 67.3854 | 146.4354 | 1371.92 | 21.8807 | 82.3592 | 1148.4639 | 91.584 | 34.6678
|  | 307 | 3229.5982 | 96.5789 | 260.7981 | 2818.8856 | 67.4375 | 146.5484 | 1240.4371 | 19.7837 | 74.466 | 1146.2886 | 91.4106 | 34.6021
|  | 308 | 3233.3618 | 96.6914 | 261.102 | 2821.4502 | 67.4988 | 146.6818 | 853.5275 | 13.6129 | 51.239 | 1143.724 | 91.2061 | 34.5247
|  | 309 | 3237.1227 | 96.8039 | 261.4057 | 2824.4895 | 67.5715 | 146.8398 | 594.3361 | 9.479 | 35.6792 | 1140.6848 | 90.9637 | 34.4329
|  | 310 | 3240.8816 | 96.9163 | 261.7093 | 2827.9162 | 67.6535 | 147.0179 | 335.1466 | 5.3452 | 20.1195 | 1137.258 | 90.6904 | 34.3295
|  | 311 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 312 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 313 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 314 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 315 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 316 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 317 | 3033.2382 | 90.7069 | 244.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 318 | 3192.8823 | 95.4809 | 257.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 319 | 3229.9261 | 96.5887 | 260.8246 | 2854.842 | 68.2977 | 148.4178 | 122.6003 | 1.9553 | 7.36 | 1110.3322 | 88.5432 | 33.5167
|  | 320 | 3233.8679 | 96.7066 | 261.1429 | 2858.9888 | 68.3969 | 148.6333 | 278.3026 | 4.4386 | 16.7071 | 1106.1855 | 88.2126 | 33.3915
|  | 321 | 3233.6993 | 96.7015 | 261.1293 | 0 | 0 | 0 | 438.1153 | 6.9875 | 26.301 | 0 | 0 | 0
|  | 322 | 3231.2267 | 96.6276 | 260.9296 | 0 | 0 | 0 | 600.2321 | 9.5731 | 36.0332 | 0 | 0 | 0
|  | 323 | 3228.7734 | 96.5542 | 260.7315 | 0 | 0 | 0 | 762.3295 | 12.1584 | 45.7642 | 0 | 0 | 0
|  | 324 | 3226.3396 | 96.4814 | 260.535 | 0 | 0 | 0 | 924.4074 | 14.7433 | 55.4941 | 0 | 0 | 0
|  | 325 | 3223.9251 | 96.4092 | 260.34 | 0 | 0 | 0 | 1086.4661 | 17.328 | 65.2228 | 0 | 0 | 0
|  | 326 | 3221.5297 | 96.3376 | 260.1466 | 0 | 0 | 0 | 1248.5055 | 19.9124 | 74.9504 | 0 | 0 | 0
|  | 327 | 3219.1536 | 96.2666 | 259.9547 | 0 | 0 | 0 | 1091.2376 | 17.4041 | 65.5093 | 0 | 0 | 0
|  | 328 | 3219.135 | 96.266 | 259.9532 | 2874.1154 | 68.7587 | 149.4197 | 1250.9002 | 19.9506 | 75.0941 | 1091.0588 | 87.0063 | 32.9349
|  | 329 | 3223.2405 | 96.3888 | 260.2847 | 2876.1001 | 68.8062 | 149.5229 | 1885.3712 | 30.0697 | 113.1828 | 1089.0741 | 86.848 | 32.875
|  | 330 | 3227.3392 | 96.5113 | 260.6157 | 2877.7401 | 68.8455 | 149.6082 | 1721.6284 | 27.4582 | 103.3529 | 1087.4341 | 86.7172 | 32.8255
|  | 331 | 3231.431 | 96.6337 | 260.9461 | 2879.251 | 68.8816 | 149.6867 | 2036.8249 | 32.4852 | 122.2748 | 1085.9232 | 86.5967 | 32.7799
|  | 332 | 3235.5152 | 96.7558 | 261.2759 | 2880.7623 | 68.9178 | 149.7653 | 1681.5235 | 26.8186 | 100.9454 | 1084.412 | 86.4762 | 32.7343
|  | 333 | 3239.5928 | 96.8778 | 261.6052 | 2882.7258 | 68.9647 | 149.8674 | 1326.229 | 21.152 | 79.6163 | 1082.4485 | 86.3197 | 32.675
|  | 334 | 3243.6646 | 96.9995 | 261.934 | 2885.1407 | 69.0225 | 149.9929 | 970.9401 | 15.4855 | 58.2876 | 1080.0336 | 86.1271 | 32.6021
|  | 335 | 3243.6058 | 96.9978 | 261.9293 | 0 | 0 | 0 | 619.7818 | 9.8849 | 37.2068 | 0 | 0 | 0
|  | 336 | 3241.2014 | 96.9259 | 261.7351 | 0 | 0 | 0 | 270.9692 | 4.3217 | 16.2668 | 0 | 0 | 0
|  | 337 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 338 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 339 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 340 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 341 | 3233.8835 | 96.707 | 261.1442 | 0 | 0 | 0 | 38.8209 | 0.61915 | 2.3305 | 0 | 0 | 0
|  | 342 | 3231.5721 | 96.6379 | 260.9575 | 0 | 0 | 0 | 280.5984 | 4.4753 | 16.8449 | 0 | 0 | 0
|  | 343 | 3231.6719 | 96.6409 | 260.9656 | 2906.5216 | 69.534 | 151.1045 | 519.9648 | 8.2929 | 31.2146 | 1058.6526 | 84.4221 | 31.9567
|  | 344 | 3235.9147 | 96.7678 | 261.3082 | 2909.329 | 69.6012 | 151.2504 | 755.1882 | 12.0445 | 45.3355 | 1055.8452 | 84.1982 | 31.872
|  | 345 | 3236.0123 | 96.7707 | 261.3161 | 0 | 0 | 0 | 994.5568 | 15.8622 | 59.7053 | 0 | 0 | 0
|  | 346 | 3233.7235 | 96.7023 | 261.1312 | 0 | 0 | 0 | 1236.3118 | 19.7179 | 74.2184 | 0 | 0 | 0
|  | 347 | 3231.4533 | 96.6344 | 260.9479 | 0 | 0 | 0 | 1478.0482 | 23.5733 | 88.7303 | 0 | 0 | 0
|  | 348 | 3229.2016 | 96.567 | 260.7661 | 0 | 0 | 0 | 1719.766 | 27.4285 | 103.2411 | 0 | 0 | 0
|  | 349 | 3226.9684 | 96.5002 | 260.5858 | 0 | 0 | 0 | 1961.4654 | 31.2833 | 117.7509 | 0 | 0 | 0
|  | 350 | 3224.7535 | 96.434 | 260.4069 | 0 | 0 | 0 | 2203.1465 | 35.1379 | 132.2595 | 0 | 0 | 0
|  | 351 | 3222.5569 | 96.3683 | 260.2295 | 0 | 0 | 0 | 2045.6989 | 32.6268 | 122.8076 | 0 | 0 | 0
|  | 352 | 3222.7802 | 96.375 | 260.2476 | 2910.982 | 69.6407 | 151.3364 | 2258.3344 | 36.0181 | 135.5725 | 1054.1922 | 84.0664 | 31.8221
|  | 353 | 3227.1438 | 96.5055 | 260.5999 | 2910.8488 | 69.6375 | 151.3294 | 2998.9768 | 47.8306 | 180.0348 | 1054.3254 | 84.077 | 31.8261
|  | 354 | 3231.4944 | 96.6356 | 260.9512 | 2910.2996 | 69.6244 | 151.3009 | 2834.982 | 45.215 | 170.1899 | 1054.8746 | 84.1208 | 31.8427
|  | 355 | 3235.832 | 96.7653 | 261.3015 | 2909.6219 | 69.6082 | 151.2657 | 3149.9326 | 50.2382 | 189.097 | 1055.5523 | 84.1748 | 31.8631
|  | 356 | 3240.1561 | 96.8946 | 261.6507 | 2908.9239 | 69.5915 | 151.2294 | 2826.3203 | 45.0769 | 169.6699 | 1056.2504 | 84.2305 | 31.8842
|  | 357 | 3244.4669 | 97.0235 | 261.9988 | 2908.0975 | 69.5717 | 151.1864 | 3300.9419 | 52.6466 | 198.1624 | 1057.0767 | 84.2964 | 31.9091
|  | 358 | 3248.764 | 97.152 | 262.3458 | 2907.4666 | 69.5566 | 151.1536 | 2498.4242 | 39.8473 | 149.9856 | 1057.7076 | 84.3467 | 31.9282
|  | 359 | 3248.9114 | 97.1564 | 262.3577 | 0 | 0 | 0 | 1700.0562 | 27.1141 | 102.0579 | 0 | 0 | 0
|  | 360 | 3246.6768 | 97.0896 | 262.1773 | 0 | 0 | 0 | 904.0702 | 14.419 | 54.2732 | 0 | 0 | 0
|  | 361 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 362 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 363 | 2745.8788 | 82.1136 | 221.7366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 364 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 365 | 3170.076 | 94.7989 | 255.9916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 366 | 3238.0019 | 96.8302 | 261.4767 | 0 | 0 | 0 | 137.3308 | 2.1903 | 8.2443 | 0 | 0 | 0
|  | 367 | 3238.289 | 96.8388 | 261.4999 | 2920.0345 | 69.8573 | 151.807 | 342.3004 | 5.4593 | 20.549 | 1045.1398 | 83.3445 | 31.5488
|  | 368 | 3242.7252 | 96.9714 | 261.8582 | 2922.4236 | 69.9144 | 151.9312 | 543.121 | 8.6622 | 32.6047 | 1042.7506 | 83.154 | 31.4767
|  | 369 | 3243.0072 | 96.9799 | 261.8809 | 0 | 0 | 0 | 748.0957 | 11.9314 | 44.9097 | 0 | 0 | 0
|  | 370 | 3240.8801 | 96.9163 | 261.7092 | 0 | 0 | 0 | 955.4795 | 15.2389 | 57.3594 | 0 | 0 | 0
|  | 371 | 3238.7708 | 96.8532 | 261.5388 | 0 | 0 | 0 | 1162.8455 | 18.5462 | 69.808 | 0 | 0 | 0
|  | 372 | 3236.6793 | 96.7906 | 261.3699 | 0 | 0 | 0 | 1370.1938 | 21.8532 | 82.2556 | 0 | 0 | 0
|  | 373 | 3234.6054 | 96.7286 | 261.2025 | 0 | 0 | 0 | 1577.5244 | 25.1599 | 94.7021 | 0 | 0 | 0
|  | 374 | 3232.5491 | 96.6671 | 261.0364 | 0 | 0 | 0 | 1784.8375 | 28.4663 | 107.1475 | 0 | 0 | 0
|  | 375 | 3230.5103 | 96.6062 | 260.8718 | 0 | 0 | 0 | 1992.133 | 31.7725 | 119.5919 | 0 | 0 | 0
|  | 376 | 3230.9088 | 96.6181 | 260.904 | 2921.6554 | 69.8961 | 151.8913 | 2196.9911 | 35.0397 | 131.89 | 1043.5188 | 83.2152 | 31.4999
|  | 377 | 3235.4523 | 96.754 | 261.2709 | 2921.5288 | 69.893 | 151.8847 | 2032.8036 | 32.4211 | 122.0334 | 1043.6455 | 83.2253 | 31.5037
|  | 378 | 3239.9826 | 96.8894 | 261.6367 | 2921.2722 | 69.8869 | 151.8713 | 2347.5614 | 37.4412 | 140.929 | 1043.902 | 83.2458 | 31.5114
|  | 379 | 3244.4992 | 97.0245 | 262.0014 | 2920.563 | 69.8699 | 151.8345 | 2662.3331 | 42.4615 | 159.8254 | 1044.6112 | 83.3023 | 31.5328
|  | 380 | 3249.0011 | 97.1591 | 262.365 | 2919.5096 | 69.8447 | 151.7797 | 2817.4753 | 44.9358 | 169.1389 | 1045.6646 | 83.3863 | 31.5646
|  | 381 | 3253.4875 | 97.2933 | 262.7272 | 2918.0048 | 69.8087 | 151.7015 | 3291.9212 | 52.5027 | 197.6209 | 1047.1694 | 83.5063 | 31.6101
|  | 382 | 3257.9579 | 97.427 | 263.0882 | 2916.6957 | 69.7774 | 151.6334 | 2489.2303 | 39.7006 | 149.4337 | 1048.4785 | 83.6107 | 31.6496
|  | 383 | 3258.2714 | 97.4363 | 263.1136 | 0 | 0 | 0 | 1690.6962 | 26.9649 | 101.496 | 0 | 0 | 0
|  | 384 | 3256.1869 | 97.374 | 262.9452 | 0 | 0 | 0 | 894.5601 | 14.2673 | 53.7023 | 0 | 0 | 0
|  | 385 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 386 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 387 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 388 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 389 | 3217.443 | 96.2154 | 259.8166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 390 | 3248.4914 | 97.1439 | 262.3238 | 0 | 0 | 0 | 189.9973 | 3.0303 | 11.4059 | 0 | 0 | 0
|  | 391 | 3248.9285 | 97.157 | 262.3591 | 2923.0314 | 69.929 | 151.9628 | 410.6059 | 6.5487 | 24.6495 | 1042.1429 | 83.1055 | 31.4583
|  | 392 | 3253.5143 | 97.2941 | 262.7294 | 2924.6322 | 69.9673 | 152.046 | 627.0658 | 10.001 | 37.6441 | 1040.542 | 82.9778 | 31.41
|  | 393 | 3253.9425 | 97.3069 | 262.764 | 0 | 0 | 0 | 847.6833 | 13.5197 | 50.8882 | 0 | 0 | 0
|  | 394 | 3251.9576 | 97.2475 | 262.6037 | 0 | 0 | 0 | 1070.7139 | 17.0768 | 64.2772 | 0 | 0 | 0
|  | 395 | 3249.9898 | 97.1887 | 262.4448 | 0 | 0 | 0 | 1293.7273 | 20.6336 | 77.6651 | 0 | 0 | 0
|  | 396 | 3248.0391 | 97.1304 | 262.2873 | 0 | 0 | 0 | 1516.7238 | 24.1902 | 91.0521 | 0 | 0 | 0
|  | 397 | 3246.1052 | 97.0725 | 262.1311 | 0 | 0 | 0 | 1739.7033 | 27.7465 | 104.438 | 0 | 0 | 0
|  | 398 | 3244.1883 | 97.0152 | 261.9763 | 0 | 0 | 0 | 1962.6659 | 31.3025 | 117.8229 | 0 | 0 | 0
|  | 399 | 3242.2882 | 96.9584 | 261.8229 | 0 | 0 | 0 | 2185.6118 | 34.8582 | 131.2068 | 0 | 0 | 0
|  | 400 | 3242.8174 | 96.9742 | 261.8656 | 2917.0884 | 69.7868 | 151.6538 | 2025.4385 | 32.3036 | 121.5913 | 1048.0859 | 83.5794 | 31.6377
|  | 401 | 3247.4871 | 97.1138 | 262.2427 | 2916.2184 | 69.766 | 151.6086 | 2308.1281 | 36.8123 | 138.5617 | 1048.9558 | 83.6488 | 31.664
|  | 402 | 3252.141 | 97.253 | 262.6185 | 2914.9404 | 69.7354 | 151.5422 | 2590.8336 | 41.3211 | 155.5331 | 1050.2338 | 83.7507 | 31.7026
|  | 403 | 3256.7781 | 97.3917 | 262.993 | 2913.0828 | 69.691 | 151.4456 | 3128.9865 | 49.9041 | 187.8396 | 1052.0914 | 83.8988 | 31.7586
|  | 404 | 3261.3972 | 97.5298 | 263.366 | 2910.8405 | 69.6373 | 151.329 | 3124.3675 | 49.8304 | 187.5623 | 1054.3337 | 84.0776 | 31.8263
|  | 405 | 3265.9978 | 97.6674 | 263.7375 | 2908.365 | 69.5781 | 151.2003 | 3439.0551 | 54.8494 | 206.4536 | 1056.8093 | 84.2751 | 31.9011
|  | 406 | 3270.5797 | 97.8044 | 264.1075 | 2906.2169 | 69.5267 | 151.0886 | 2604.3238 | 41.5363 | 156.343 | 1058.9574 | 84.4464 | 31.9659
|  | 407 | 3271.0084 | 97.8172 | 264.1421 | 0 | 0 | 0 | 1773.7456 | 28.2894 | 106.4816 | 0 | 0 | 0
|  | 408 | 3269.0569 | 97.7589 | 263.9845 | 0 | 0 | 0 | 945.5478 | 15.0805 | 56.7632 | 0 | 0 | 0
|  | 409 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 410 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 411 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 412 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 413 | 3192.8823 | 95.4809 | 257.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 414 | 3262.3117 | 97.5572 | 263.4398 | 0 | 0 | 0 | 143.4294 | 2.2876 | 8.6104 | 0 | 0 | 0
|  | 415 | 3262.8487 | 97.5732 | 263.4832 | 2906.4186 | 69.5315 | 151.0991 | 355.7512 | 5.6739 | 21.3565 | 1058.7556 | 84.4303 | 31.9598
|  | 416 | 3267.5234 | 97.713 | 263.8607 | 2907.4599 | 69.5565 | 151.1533 | 563.9354 | 8.9942 | 33.8542 | 1057.7143 | 84.3472 | 31.9284
|  | 417 | 3272.1865 | 97.8525 | 264.2372 | 2908.1916 | 69.574 | 151.1913 | 772.1311 | 12.3147 | 46.3526 | 1056.9827 | 84.2889 | 31.9063
|  | 418 | 3276.8374 | 97.9915 | 264.6128 | 2908.6141 | 69.5841 | 151.2133 | 980.339 | 15.6354 | 58.8518 | 1056.5602 | 84.2552 | 31.8935
|  | 419 | 3281.4754 | 98.1302 | 264.9873 | 2908.7278 | 69.5868 | 151.2192 | 1188.5599 | 18.9563 | 71.3517 | 1056.4465 | 84.2461 | 31.8901
|  | 420 | 3286.0998 | 98.2685 | 265.3608 | 2908.5331 | 69.5821 | 151.2091 | 1396.7943 | 22.2774 | 83.8525 | 1056.6411 | 84.2617 | 31.896
|  | 421 | 3290.71 | 98.4064 | 265.7331 | 2908.0306 | 69.5701 | 151.1829 | 1605.0429 | 25.5988 | 96.3541 | 1057.1436 | 84.3017 | 31.9112
|  | 422 | 3295.3053 | 98.5438 | 266.1041 | 2907.2207 | 69.5507 | 151.1408 | 1813.3064 | 28.9204 | 108.8566 | 1057.9535 | 84.3663 | 31.9356
|  | 423 | 3299.8853 | 98.6808 | 266.474 | 2906.3552 | 69.53 | 151.0958 | 1649.0823 | 26.3012 | 98.9978 | 1058.819 | 84.4353 | 31.9617
|  | 424 | 3304.45 | 98.8173 | 266.8426 | 2905.3265 | 69.5054 | 151.0423 | 2017.0205 | 32.1694 | 121.0859 | 1059.8478 | 84.5174 | 31.9928
|  | 425 | 3308.9985 | 98.9533 | 267.2099 | 2903.776 | 69.4683 | 150.9617 | 2384.975 | 38.0379 | 143.175 | 1061.3983 | 84.641 | 32.0396
|  | 426 | 3313.5297 | 99.0888 | 267.5758 | 2901.7046 | 69.4188 | 150.854 | 2752.9467 | 43.9066 | 165.2651 | 1063.4696 | 84.8062 | 32.1021
|  | 427 | 3318.0429 | 99.2238 | 267.9403 | 2899.6608 | 69.3699 | 150.7478 | 2309.4122 | 36.8327 | 138.6388 | 1065.5134 | 84.9692 | 32.1638
|  | 428 | 3322.539 | 99.3582 | 268.3033 | 2898.192 | 69.3347 | 150.6714 | 1865.8948 | 29.7591 | 112.0136 | 1066.9823 | 85.0863 | 32.2081
|  | 429 | 3327.0194 | 99.4922 | 268.6651 | 2897.2973 | 69.3133 | 150.6249 | 1422.3931 | 22.6857 | 85.3892 | 1067.8769 | 85.1576 | 32.2351
|  | 430 | 3331.4853 | 99.6258 | 269.0258 | 2896.976 | 69.3056 | 150.6082 | 978.9058 | 15.6125 | 58.7658 | 1068.1982 | 85.1833 | 32.2448
|  | 431 | 3331.8063 | 99.6354 | 269.0517 | 0 | 0 | 0 | 539.5635 | 8.6055 | 32.3911 | 0 | 0 | 0
|  | 432 | 3192.8823 | 95.4809 | 257.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 433 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 434 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 435 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 436 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 437 | 3163.8561 | 94.6129 | 255.4893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 438 | 3323.7844 | 99.3955 | 268.4039 | 0 | 0 | 0 | 43.2551 | 0.68987 | 2.5967 | 0 | 0 | 0
|  | 439 | 3324.2047 | 99.408 | 268.4378 | 2895.5002 | 69.2703 | 150.5315 | 246.0183 | 3.9237 | 14.769 | 1069.674 | 85.301 | 32.2894
|  | 440 | 3328.7557 | 99.5441 | 268.8053 | 2896.0742 | 69.2841 | 150.5613 | 444.6507 | 7.0917 | 26.6933 | 1069.1001 | 85.2552 | 32.2721
|  | 441 | 3333.2943 | 99.6799 | 269.1718 | 2896.3532 | 69.2907 | 150.5758 | 643.2955 | 10.2599 | 38.6184 | 1068.821 | 85.2329 | 32.2636
|  | 442 | 3337.8198 | 99.8152 | 269.5373 | 2896.3377 | 69.2904 | 150.575 | 841.9534 | 13.4283 | 50.5442 | 1068.8366 | 85.2342 | 32.2641
|  | 443 | 3342.3317 | 99.9501 | 269.9016 | 2896.028 | 69.283 | 150.5589 | 1040.6249 | 16.5969 | 62.4709 | 1069.1462 | 85.2589 | 32.2735
|  | 444 | 3346.8293 | 100.0846 | 270.2648 | 2895.4247 | 69.2685 | 150.5276 | 1239.3108 | 19.7657 | 74.3984 | 1069.7495 | 85.307 | 32.2917
|  | 445 | 3351.3119 | 100.2187 | 270.6268 | 2894.5282 | 69.2471 | 150.481 | 1438.0116 | 22.9348 | 86.3268 | 1070.646 | 85.3785 | 32.3187
|  | 446 | 3355.7792 | 100.3522 | 270.9876 | 2893.5376 | 69.2234 | 150.4295 | 1342.3191 | 21.4086 | 80.5822 | 1071.6366 | 85.4575 | 32.3486
|  | 447 | 3360.2312 | 100.4854 | 271.3471 | 2892.6518 | 69.2022 | 150.3834 | 1246.6419 | 19.8826 | 74.8385 | 1072.5225 | 85.5281 | 32.3754
|  | 448 | 3364.6682 | 100.6181 | 271.7054 | 2891.8705 | 69.1835 | 150.3428 | 1150.9797 | 18.3569 | 69.0957 | 1073.3038 | 85.5904 | 32.399
|  | 449 | 3369.0905 | 100.7503 | 272.0625 | 2891.1936 | 69.1673 | 150.3076 | 1055.3322 | 16.8315 | 63.3538 | 1073.9806 | 85.6444 | 32.4194
|  | 450 | 3373.4983 | 100.8821 | 272.4184 | 2890.6212 | 69.1536 | 150.2778 | 959.6991 | 15.3062 | 57.6127 | 1074.553 | 85.69 | 32.4367
|  | 451 | 3377.892 | 101.0135 | 272.7732 | 2890.153 | 69.1424 | 150.2535 | 864.0803 | 13.7812 | 51.8725 | 1075.0213 | 85.7274 | 32.4508
|  | 452 | 3382.2718 | 101.1445 | 273.1269 | 2889.7888 | 69.1337 | 150.2346 | 768.4753 | 12.2564 | 46.1332 | 1075.3854 | 85.7564 | 32.4618
|  | 453 | 3386.6377 | 101.2751 | 273.4795 | 2889.2517 | 69.1209 | 150.2066 | 1083.3975 | 17.2791 | 65.0386 | 1075.9225 | 85.7992 | 32.478
|  | 454 | 3390.9895 | 101.4052 | 273.8309 | 2888.8036 | 69.1101 | 150.1834 | 600.1134 | 9.5712 | 36.0261 | 1076.3706 | 85.835 | 32.4915
|  | 455 | 3391.2013 | 101.4115 | 273.848 | 0 | 0 | 0 | 120.9693 | 1.9293 | 7.262 | 0 | 0 | 0
|  | 456 | 3033.2382 | 90.7069 | 244.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 457 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 458 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 459 | 2736.7563 | 81.8408 | 220.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 460 | 2919.2067 | 87.2969 | 235.7332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 461 | 3101.6571 | 92.7529 | 250.4666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 462 | 3284.1075 | 98.209 | 265.1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 463 | 3384.5242 | 101.2118 | 273.3088 | 2882.7739 | 68.9659 | 149.8699 | 82.0337 | 1.3084 | 4.9247 | 1082.4003 | 86.3158 | 32.6736
|  | 464 | 3388.9432 | 101.344 | 273.6656 | 2882.9884 | 68.971 | 149.881 | 260.0651 | 4.1478 | 15.6123 | 1082.1858 | 86.2987 | 32.6671
|  | 465 | 3389.2264 | 101.3525 | 273.6885 | 0 | 0 | 0 | 442.2324 | 7.0531 | 26.5481 | 0 | 0 | 0
|  | 466 | 3387.1664 | 101.2909 | 273.5222 | 0 | 0 | 0 | 626.7428 | 9.9959 | 37.6247 | 0 | 0 | 0
|  | 467 | 3385.123 | 101.2298 | 273.3571 | 0 | 0 | 0 | 811.2366 | 12.9384 | 48.7002 | 0 | 0 | 0
|  | 468 | 3383.0962 | 101.1691 | 273.1935 | 0 | 0 | 0 | 995.7139 | 15.8806 | 59.7748 | 0 | 0 | 0
|  | 469 | 3381.0857 | 101.109 | 273.0311 | 0 | 0 | 0 | 1088.9495 | 17.3676 | 65.3719 | 0 | 0 | 0
|  | 470 | 3379.0917 | 101.0494 | 272.8701 | 0 | 0 | 0 | 1090.9436 | 17.3994 | 65.4916 | 0 | 0 | 0
|  | 471 | 3377.1139 | 100.9902 | 272.7104 | 0 | 0 | 0 | 1549.0474 | 24.7057 | 92.9925 | 0 | 0 | 0
|  | 472 | 3377.4806 | 101.0012 | 272.74 | 2866.2655 | 68.5709 | 149.0116 | 1731.1311 | 27.6097 | 103.9234 | 1098.9087 | 87.6323 | 33.1719
|  | 473 | 3381.9567 | 101.1351 | 273.1015 | 2864.3574 | 68.5253 | 148.9124 | 1471.2244 | 23.4645 | 88.3207 | 1100.8168 | 87.7844 | 33.2295
|  | 474 | 3386.4156 | 101.2684 | 273.4615 | 2862.7796 | 68.4875 | 148.8304 | 1211.335 | 19.3195 | 72.719 | 1102.3947 | 87.9103 | 33.2771
|  | 475 | 3390.8579 | 101.4013 | 273.8202 | 2861.4454 | 68.4556 | 148.7611 | 1079.1774 | 17.2118 | 64.7853 | 1103.7288 | 88.0167 | 33.3174
|  | 476 | 3395.2842 | 101.5336 | 274.1777 | 2860.4409 | 68.4316 | 148.7088 | 691.6052 | 11.0304 | 41.5185 | 1104.7333 | 88.0968 | 33.3477
|  | 477 | 3399.6956 | 101.6655 | 274.5339 | 2859.8518 | 68.4175 | 148.6782 | 431.7632 | 6.8862 | 25.9196 | 1105.3225 | 88.1437 | 33.3655
|  | 478 | 3404.0928 | 101.797 | 274.889 | 2859.5912 | 68.4113 | 148.6647 | 171.9354 | 2.7422 | 10.3216 | 1105.5831 | 88.1645 | 33.3734
|  | 479 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 480 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 481 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 482 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 483 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 484 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 485 | 3033.2382 | 90.7069 | 244.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 486 | 3192.8823 | 95.4809 | 257.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 487 | 3352.5264 | 100.255 | 270.7249 | 2849.0266 | 68.1585 | 148.1154 | 0 | 0 | 0 | 1116.1476 | 89.007 | 33.6923
|  | 488 | 3405.6189 | 101.8427 | 275.0122 | 2848.917 | 68.1559 | 148.1097 | 106.5516 | 1.6994 | 6.3965 | 1116.2572 | 89.0157 | 33.6956
|  | 489 | 3405.9413 | 101.8523 | 275.0383 | 0 | 0 | 0 | 265.8734 | 4.2404 | 15.9609 | 0 | 0 | 0
|  | 490 | 3403.9746 | 101.7935 | 274.8794 | 0 | 0 | 0 | 427.4842 | 6.8179 | 25.6628 | 0 | 0 | 0
|  | 491 | 3402.0239 | 101.7352 | 274.7219 | 0 | 0 | 0 | 589.079 | 9.3952 | 35.3636 | 0 | 0 | 0
|  | 492 | 3400.0892 | 101.6773 | 274.5657 | 0 | 0 | 0 | 750.6578 | 11.9722 | 45.0636 | 0 | 0 | 0
|  | 493 | 3398.1704 | 101.6199 | 274.4108 | 0 | 0 | 0 | 912.2207 | 14.549 | 54.7625 | 0 | 0 | 0
|  | 494 | 3396.2675 | 101.563 | 274.2571 | 0 | 0 | 0 | 1073.7678 | 17.1255 | 64.4605 | 0 | 0 | 0
|  | 495 | 3394.3804 | 101.5066 | 274.1047 | 0 | 0 | 0 | 916.0108 | 14.6094 | 54.99 | 0 | 0 | 0
|  | 496 | 3394.7812 | 101.5186 | 274.1371 | 2831.1522 | 67.7309 | 147.1862 | 1075.254 | 17.1492 | 64.5497 | 1134.022 | 90.4324 | 34.2318
|  | 497 | 3399.2687 | 101.6528 | 274.4994 | 2829.326 | 67.6872 | 147.0912 | 1709.3431 | 27.2622 | 102.6154 | 1135.8482 | 90.578 | 34.2869
|  | 498 | 3403.7379 | 101.7864 | 274.8603 | 2827.2277 | 67.637 | 146.9821 | 1545.2297 | 24.6448 | 92.7634 | 1137.9465 | 90.7453 | 34.3503
|  | 499 | 3408.1891 | 101.9195 | 275.2198 | 2825.0731 | 67.5855 | 146.8701 | 1860.0668 | 29.6661 | 111.6637 | 1140.1011 | 90.9172 | 34.4153
|  | 500 | 3412.6219 | 102.0521 | 275.5777 | 2822.9917 | 67.5357 | 146.7619 | 1504.4169 | 23.9939 | 90.3133 | 1142.1825 | 91.0831 | 34.4782
|  | 501 | 3417.0373 | 102.1841 | 275.9343 | 2821.4358 | 67.4985 | 146.681 | 1148.7845 | 18.3219 | 68.9639 | 1143.7384 | 91.2072 | 34.5251
|  | 502 | 3421.4364 | 102.3157 | 276.2895 | 2820.4047 | 67.4738 | 146.6274 | 793.1682 | 12.6502 | 47.6155 | 1144.7695 | 91.2894 | 34.5562
|  | 503 | 3421.7389 | 102.3247 | 276.314 | 0 | 0 | 0 | 441.6487 | 7.0438 | 26.5131 | 0 | 0 | 0
|  | 504 | 3419.7979 | 102.2667 | 276.1572 | 0 | 0 | 0 | 92.3726 | 1.4732 | 5.5453 | 0 | 0 | 0
|  | 505 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 506 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 507 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 508 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 509 | 3272.7044 | 97.868 | 264.2791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 510 | 3414.884 | 102.1197 | 275.7604 | 0 | 0 | 0 | 97.2866 | 1.5516 | 5.8403 | 0 | 0 | 0
|  | 511 | 3415.2647 | 102.1311 | 275.7912 | 2812.0993 | 67.2751 | 146.1956 | 336.3721 | 5.3648 | 20.1931 | 1153.0749 | 91.9517 | 34.807
|  | 512 | 3419.7217 | 102.2644 | 276.1511 | 2812.2124 | 67.2778 | 146.2015 | 571.3812 | 9.1129 | 34.3012 | 1152.9619 | 91.9427 | 34.8035
|  | 513 | 3420.0886 | 102.2754 | 276.1807 | 0 | 0 | 0 | 810.4805 | 12.9263 | 48.6548 | 0 | 0 | 0
|  | 514 | 3418.2245 | 102.2196 | 276.0302 | 0 | 0 | 0 | 1051.8108 | 16.7753 | 63.1424 | 0 | 0 | 0
|  | 515 | 3416.3759 | 102.1643 | 275.8809 | 0 | 0 | 0 | 1293.1256 | 20.624 | 77.629 | 0 | 0 | 0
|  | 516 | 3414.5426 | 102.1095 | 275.7328 | 0 | 0 | 0 | 1534.425 | 24.4725 | 92.1147 | 0 | 0 | 0
|  | 517 | 3412.7247 | 102.0552 | 275.586 | 0 | 0 | 0 | 1775.709 | 28.3207 | 106.5995 | 0 | 0 | 0
|  | 518 | 3410.9222 | 102.0013 | 275.4405 | 0 | 0 | 0 | 2016.9778 | 32.1687 | 121.0834 | 0 | 0 | 0
|  | 519 | 3409.1348 | 101.9478 | 275.2962 | 0 | 0 | 0 | 1859.121 | 29.6511 | 111.6069 | 0 | 0 | 0
|  | 520 | 3409.5766 | 101.961 | 275.3318 | 2794.0911 | 66.8443 | 145.2594 | 2071.538 | 33.0389 | 124.3587 | 1171.0831 | 93.3878 | 35.3506
|  | 521 | 3414.0795 | 102.0957 | 275.6954 | 2791.9484 | 66.793 | 145.148 | 2812.041 | 44.8491 | 168.8127 | 1173.2258 | 93.5587 | 35.4152
|  | 522 | 3418.5632 | 102.2298 | 276.0575 | 2789.4658 | 66.7336 | 145.019 | 2647.9132 | 42.2315 | 158.9597 | 1175.7084 | 93.7567 | 35.4902
|  | 523 | 3423.0278 | 102.3633 | 276.418 | 2786.9309 | 66.673 | 144.8872 | 2962.7368 | 47.2526 | 177.8593 | 1178.2433 | 93.9588 | 35.5667
|  | 524 | 3427.4731 | 102.4962 | 276.777 | 2784.4518 | 66.6137 | 144.7583 | 2639.0034 | 42.0894 | 158.4249 | 1180.7224 | 94.1565 | 35.6415
|  | 525 | 3431.8994 | 102.6286 | 277.1344 | 2781.9208 | 66.5531 | 144.6267 | 3113.5094 | 49.6572 | 186.9105 | 1183.2535 | 94.3583 | 35.7179
|  | 526 | 3436.3065 | 102.7604 | 277.4903 | 2779.6614 | 66.4991 | 144.5093 | 2310.8817 | 36.8562 | 138.727 | 1185.5128 | 94.5385 | 35.7861
|  | 527 | 3436.6418 | 102.7704 | 277.5174 | 0 | 0 | 0 | 1512.3258 | 24.12 | 90.7881 | 0 | 0 | 0
|  | 528 | 3434.7986 | 102.7153 | 277.3686 | 0 | 0 | 0 | 715.9484 | 11.4186 | 42.9799 | 0 | 0 | 0
|  | 529 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 530 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 531 | 2745.8788 | 82.1136 | 221.7366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 532 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 533 | 3170.076 | 94.7989 | 255.9916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 534 | 3375.3327 | 100.937 | 272.5666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 535 | 3431.0453 | 102.603 | 277.0655 | 2778.3251 | 66.4671 | 144.4398 | 149.5441 | 2.3851 | 8.9774 | 1186.8491 | 94.6451 | 35.8265
|  | 536 | 3435.5212 | 102.7369 | 277.4269 | 2779.8604 | 66.5038 | 144.5196 | 350.325 | 5.5873 | 21.0307 | 1185.3139 | 94.5226 | 35.7801
|  | 537 | 3435.9303 | 102.7491 | 277.46 | 0 | 0 | 0 | 555.1726 | 8.8544 | 33.3282 | 0 | 0 | 0
|  | 538 | 3434.1587 | 102.6961 | 277.3169 | 0 | 0 | 0 | 762.2009 | 12.1563 | 45.7565 | 0 | 0 | 0
|  | 539 | 3432.4021 | 102.6436 | 277.175 | 0 | 0 | 0 | 969.2143 | 15.458 | 58.184 | 0 | 0 | 0
|  | 540 | 3430.6603 | 102.5915 | 277.0344 | 0 | 0 | 0 | 1176.2127 | 18.7594 | 70.6105 | 0 | 0 | 0
|  | 541 | 3428.9334 | 102.5399 | 276.8949 | 0 | 0 | 0 | 1383.1964 | 22.0605 | 83.0362 | 0 | 0 | 0
|  | 542 | 3427.2213 | 102.4887 | 276.7567 | 0 | 0 | 0 | 1590.1652 | 25.3615 | 95.4609 | 0 | 0 | 0
|  | 543 | 3425.5239 | 102.4379 | 276.6196 | 0 | 0 | 0 | 1797.1193 | 28.6622 | 107.8848 | 0 | 0 | 0
|  | 544 | 3426.0219 | 102.4528 | 276.6598 | 2773.7364 | 66.3573 | 144.2012 | 2001.8781 | 31.9279 | 120.1769 | 1191.4378 | 95.011 | 35.965
|  | 545 | 3430.57 | 102.5888 | 277.0271 | 2773.4466 | 66.3504 | 144.1862 | 1837.6859 | 29.3092 | 110.3201 | 1191.7276 | 95.0341 | 35.9737
|  | 546 | 3435.1034 | 102.7244 | 277.3932 | 2773.1027 | 66.3422 | 144.1683 | 2152.4406 | 34.3292 | 129.2155 | 1192.0715 | 95.0615 | 35.9841
|  | 547 | 3439.6218 | 102.8595 | 277.758 | 2772.3819 | 66.3249 | 144.1308 | 2467.2105 | 39.3495 | 148.1118 | 1192.7924 | 95.119 | 36.0059
|  | 548 | 3444.1242 | 102.9941 | 278.1216 | 2771.3924 | 66.3013 | 144.0794 | 2622.3522 | 41.8238 | 157.4253 | 1193.7818 | 95.1979 | 36.0357
|  | 549 | 3448.6102 | 103.1283 | 278.4839 | 2770.0271 | 66.2686 | 144.0084 | 3096.7986 | 49.3907 | 185.9073 | 1195.1471 | 95.3068 | 36.077
|  | 550 | 3453.0793 | 103.2619 | 278.8448 | 2768.9329 | 66.2424 | 143.9515 | 2294.1089 | 36.5887 | 137.7201 | 1196.2413 | 95.394 | 36.11
|  | 551 | 3453.4854 | 103.2741 | 278.8776 | 0 | 0 | 0 | 1495.4822 | 23.8514 | 89.7769 | 0 | 0 | 0
|  | 552 | 3451.7287 | 103.2216 | 278.7357 | 0 | 0 | 0 | 699.0183 | 11.1486 | 41.9635 | 0 | 0 | 0
|  | 553 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 554 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 555 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 556 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 557 | 3217.443 | 96.2154 | 259.8166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 558 | 3438.4887 | 102.8256 | 277.6665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 559 | 3448.6547 | 103.1296 | 278.4875 | 2777.7703 | 66.4538 | 144.4109 | 210.8796 | 3.3633 | 12.6595 | 1187.4039 | 94.6893 | 35.8432
|  | 560 | 3453.2126 | 103.2659 | 278.8555 | 2780.3429 | 66.5154 | 144.5447 | 427.3674 | 6.8161 | 25.6558 | 1184.8314 | 94.4842 | 35.7656
|  | 561 | 3453.7047 | 103.2806 | 278.8953 | 0 | 0 | 0 | 647.9211 | 10.3337 | 38.8961 | 0 | 0 | 0
|  | 562 | 3452.0142 | 103.2301 | 278.7588 | 0 | 0 | 0 | 870.6572 | 13.8861 | 52.2674 | 0 | 0 | 0
|  | 563 | 3450.3383 | 103.18 | 278.6234 | 0 | 0 | 0 | 1093.3789 | 17.4383 | 65.6378 | 0 | 0 | 0
|  | 564 | 3448.6767 | 103.1303 | 278.4893 | 0 | 0 | 0 | 1316.0862 | 20.9902 | 79.0074 | 0 | 0 | 0
|  | 565 | 3447.0295 | 103.081 | 278.3562 | 0 | 0 | 0 | 1538.7791 | 24.5419 | 92.3761 | 0 | 0 | 0
|  | 566 | 3445.3965 | 103.0322 | 278.2244 | 0 | 0 | 0 | 1761.4577 | 28.0934 | 105.744 | 0 | 0 | 0
|  | 567 | 3443.7778 | 102.9838 | 278.0937 | 0 | 0 | 0 | 1984.1221 | 31.6447 | 119.111 | 0 | 0 | 0
|  | 568 | 3444.3665 | 103.0014 | 278.1412 | 2781.9872 | 66.5547 | 144.6302 | 1823.8893 | 29.0891 | 109.4919 | 1183.1871 | 94.353 | 35.7159
|  | 569 | 3449.0121 | 103.1403 | 278.5163 | 2782.7496 | 66.573 | 144.6698 | 2106.6031 | 33.5981 | 126.4638 | 1182.4246 | 94.2922 | 35.6929
|  | 570 | 3453.6445 | 103.2788 | 278.8904 | 2783.1759 | 66.5832 | 144.692 | 2389.3302 | 38.1073 | 143.4365 | 1181.9984 | 94.2582 | 35.68
|  | 571 | 3458.2628 | 103.4169 | 279.2634 | 2783.094 | 66.5812 | 144.6877 | 2927.5019 | 46.6906 | 175.744 | 1182.0803 | 94.2648 | 35.6825
|  | 572 | 3462.8659 | 103.5546 | 279.6351 | 2782.6986 | 66.5717 | 144.6672 | 2922.8988 | 46.6172 | 175.4677 | 1182.4756 | 94.2963 | 35.6944
|  | 573 | 3467.4535 | 103.6918 | 280.0055 | 2782.141 | 66.5584 | 144.6382 | 3237.5994 | 51.6364 | 194.3598 | 1183.0333 | 94.3408 | 35.7113
|  | 574 | 3472.0257 | 103.8285 | 280.3747 | 2781.9814 | 66.5546 | 144.6299 | 2402.8778 | 38.3234 | 144.2498 | 1183.1928 | 94.3535 | 35.7161
|  | 575 | 3472.527 | 103.8435 | 280.4152 | 0 | 0 | 0 | 1572.227 | 25.0754 | 94.3841 | 0 | 0 | 0
|  | 576 | 3470.844 | 103.7932 | 280.2793 | 0 | 0 | 0 | 743.7606 | 11.8622 | 44.6495 | 0 | 0 | 0
|  | 577 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 578 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 579 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 580 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 581 | 3192.8823 | 95.4809 | 257.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 582 | 3405.7411 | 101.8463 | 275.0221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 583 | 3468.6394 | 103.7273 | 280.1013 | 2800.6308 | 67.0007 | 145.5994 | 149.9606 | 2.3917 | 9.0024 | 1164.5434 | 92.8663 | 35.1531
|  | 584 | 3473.3183 | 103.8672 | 280.4791 | 2804.3616 | 67.09 | 145.7934 | 358.1405 | 5.712 | 21.4999 | 1160.8127 | 92.5688 | 35.0405
|  | 585 | 3477.9904 | 104.0069 | 280.8564 | 2807.8501 | 67.1734 | 145.9747 | 566.3272 | 9.0323 | 33.9978 | 1157.3241 | 92.2906 | 34.9352
|  | 586 | 3482.6551 | 104.1464 | 281.2331 | 2811.0966 | 67.2511 | 146.1435 | 774.5213 | 12.3528 | 46.4961 | 1154.0777 | 92.0317 | 34.8372
|  | 587 | 3487.3121 | 104.2856 | 281.6092 | 2814.1009 | 67.323 | 146.2997 | 982.7232 | 15.6734 | 58.9949 | 1151.0733 | 91.7921 | 34.7465
|  | 588 | 3491.9606 | 104.4247 | 281.9845 | 2816.8633 | 67.3891 | 146.4433 | 1190.9335 | 18.9942 | 71.4942 | 1148.3109 | 91.5718 | 34.6631
|  | 589 | 3496.6003 | 104.5634 | 282.3592 | 2819.3838 | 67.4494 | 146.5743 | 1399.1526 | 22.315 | 83.994 | 1145.7904 | 91.3708 | 34.5871
|  | 590 | 3501.2304 | 104.7019 | 282.7331 | 2821.6625 | 67.5039 | 146.6928 | 1607.3813 | 25.6361 | 96.4944 | 1143.5117 | 91.1891 | 34.5183
|  | 591 | 3505.8508 | 104.84 | 283.1062 | 2823.951 | 67.5586 | 146.8118 | 1443.1168 | 23.0162 | 86.6333 | 1141.2233 | 91.0066 | 34.4492
|  | 592 | 3510.4615 | 104.9779 | 283.4785 | 2826.141 | 67.611 | 146.9256 | 1811.009 | 28.8837 | 108.7186 | 1139.0332 | 90.832 | 34.3831
|  | 593 | 3515.0619 | 105.1155 | 283.85 | 2827.8738 | 67.6525 | 147.0157 | 2178.9116 | 34.7514 | 130.8046 | 1137.3005 | 90.6938 | 34.3308
|  | 594 | 3519.6508 | 105.2527 | 284.2206 | 2829.1497 | 67.683 | 147.0821 | 2546.8256 | 40.6192 | 152.8912 | 1136.0245 | 90.5921 | 34.2923
|  | 595 | 3524.2278 | 105.3896 | 284.5902 | 2830.517 | 67.7157 | 147.1531 | 2103.2273 | 33.5443 | 126.2611 | 1134.6572 | 90.483 | 34.251
|  | 596 | 3528.7938 | 105.5261 | 284.9589 | 2832.5225 | 67.7637 | 147.2574 | 1659.64 | 26.4695 | 99.6316 | 1132.6517 | 90.3231 | 34.1905
|  | 597 | 3533.3503 | 105.6624 | 285.3269 | 2835.1651 | 67.8269 | 147.3948 | 1216.0622 | 19.3949 | 73.0027 | 1130.0091 | 90.1124 | 34.1107
|  | 598 | 3537.8988 | 105.7984 | 285.6942 | 2838.4436 | 67.9053 | 147.5652 | 772.4924 | 12.3205 | 46.3743 | 1126.7306 | 89.8509 | 34.0117
|  | 599 | 3538.3447 | 105.8117 | 285.7302 | 0 | 0 | 0 | 333.0251 | 5.3114 | 19.9922 | 0 | 0 | 0
|  | 600 | 3192.8823 | 95.4809 | 257.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 601 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 602 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 603 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 604 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 605 | 3163.8561 | 94.6129 | 255.4893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 606 | 3367.0395 | 100.689 | 271.8969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 607 | 3535.4216 | 105.7243 | 285.4941 | 2869.29 | 68.6433 | 149.1689 | 34.8014 | 0.55505 | 2.0892 | 1095.8842 | 87.3911 | 33.0806
|  | 608 | 3540.1005 | 105.8643 | 285.872 | 2873.7632 | 68.7503 | 149.4014 | 233.3059 | 3.721 | 14.0058 | 1091.411 | 87.0344 | 32.9456
|  | 609 | 3544.7738 | 106.004 | 286.2493 | 2877.9378 | 68.8502 | 149.6185 | 431.816 | 6.887 | 25.9228 | 1087.2364 | 86.7015 | 32.8195
|  | 610 | 3549.4409 | 106.1436 | 286.6262 | 2881.8139 | 68.9429 | 149.82 | 630.3323 | 10.0531 | 37.8402 | 1083.3604 | 86.3924 | 32.7025
|  | 611 | 3554.101 | 106.2829 | 287.0025 | 2885.3914 | 69.0285 | 150.006 | 828.8556 | 13.2194 | 49.7579 | 1079.7828 | 86.1071 | 32.5945
|  | 612 | 3558.7536 | 106.4221 | 287.3782 | 2888.6707 | 69.107 | 150.1764 | 1027.3865 | 16.3857 | 61.6762 | 1076.5035 | 85.8456 | 32.4956
|  | 613 | 3563.3978 | 106.5609 | 287.7533 | 2891.6517 | 69.1783 | 150.3314 | 1225.9257 | 19.5522 | 73.5949 | 1073.5225 | 85.6079 | 32.4056
|  | 614 | 3568.0333 | 106.6996 | 288.1276 | 2894.5333 | 69.2472 | 150.4812 | 1130.065 | 18.0234 | 67.8402 | 1070.6409 | 85.3781 | 32.3186
|  | 615 | 3572.6601 | 106.8379 | 288.5012 | 2897.5139 | 69.3185 | 150.6362 | 1034.213 | 16.4946 | 62.086 | 1067.6603 | 85.1404 | 32.2286
|  | 616 | 3577.2785 | 106.976 | 288.8742 | 2900.5931 | 69.3922 | 150.7963 | 938.3694 | 14.966 | 56.3323 | 1064.5812 | 84.8948 | 32.1357
|  | 617 | 3581.8886 | 107.1139 | 289.2464 | 2903.7703 | 69.4682 | 150.9614 | 842.5341 | 13.4375 | 50.5791 | 1061.4039 | 84.6415 | 32.0398
|  | 618 | 3586.4907 | 107.2515 | 289.6181 | 2907.0452 | 69.5465 | 151.1317 | 746.7068 | 11.9092 | 44.8264 | 1058.129 | 84.3803 | 31.9409
|  | 619 | 3591.085 | 107.3889 | 289.9891 | 2910.4173 | 69.6272 | 151.307 | 650.8872 | 10.381 | 39.0741 | 1054.7569 | 84.1114 | 31.8391
|  | 620 | 3595.6718 | 107.5261 | 290.3595 | 2913.8861 | 69.7102 | 151.4873 | 555.0752 | 8.8529 | 33.3223 | 1051.2881 | 83.8348 | 31.7344
|  | 621 | 3600.251 | 107.663 | 290.7293 | 2917.1743 | 69.7889 | 151.6583 | 869.7842 | 13.8722 | 52.215 | 1047.9999 | 83.5726 | 31.6351
|  | 622 | 3604.8223 | 107.7997 | 291.0984 | 2920.5434 | 69.8695 | 151.8334 | 386.2806 | 6.1608 | 23.1892 | 1044.6308 | 83.3039 | 31.5334
|  | 623 | 3512.1706 | 105.029 | 283.6165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 624 | 3033.2382 | 90.7069 | 244.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 625 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 626 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 627 | 2736.7563 | 81.8408 | 220.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 628 | 2919.2067 | 87.2969 | 235.7332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 629 | 3101.6571 | 92.7529 | 250.4666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 630 | 3284.1075 | 98.209 | 265.1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 631 | 3466.558 | 103.665 | 279.9332 | 2946.6638 | 70.4943 | 153.1914 | 0 | 0 | 0 | 1018.5104 | 81.2209 | 30.745
|  | 632 | 3608.3644 | 107.9056 | 291.3844 | 2950.5336 | 70.5869 | 153.3926 | 40.644 | 0.64823 | 2.4399 | 1014.6406 | 80.9123 | 30.6281
|  | 633 | 3608.8739 | 107.9209 | 291.4256 | 0 | 0 | 0 | 222.5849 | 3.55 | 13.3622 | 0 | 0 | 0
|  | 634 | 3606.9224 | 107.8625 | 291.268 | 0 | 0 | 0 | 406.9868 | 6.491 | 24.4323 | 0 | 0 | 0
|  | 635 | 3604.9856 | 107.8046 | 291.1116 | 0 | 0 | 0 | 591.374 | 9.4318 | 35.5014 | 0 | 0 | 0
|  | 636 | 3603.0634 | 107.7471 | 290.9564 | 0 | 0 | 0 | 775.7466 | 12.3724 | 46.5697 | 0 | 0 | 0
|  | 637 | 3601.1558 | 107.6901 | 290.8023 | 0 | 0 | 0 | 868.8794 | 13.8577 | 52.1606 | 0 | 0 | 0
|  | 638 | 3599.2627 | 107.6335 | 290.6495 | 0 | 0 | 0 | 870.7725 | 13.8879 | 52.2743 | 0 | 0 | 0
|  | 639 | 3597.3841 | 107.5773 | 290.4978 | 0 | 0 | 0 | 1328.7772 | 21.1926 | 79.7693 | 0 | 0 | 0
|  | 640 | 3598.0094 | 107.596 | 290.5482 | 2963.9009 | 70.9067 | 154.0875 | 1510.6023 | 24.0925 | 90.6846 | 1001.2733 | 79.8464 | 30.2246
|  | 641 | 3602.8035 | 107.7393 | 290.9354 | 2965.6022 | 70.9474 | 154.176 | 1250.3777 | 19.9422 | 75.0628 | 999.572 | 79.7107 | 30.1733
|  | 642 | 3607.5854 | 107.8823 | 291.3215 | 2967.6196 | 70.9957 | 154.2808 | 990.1651 | 15.7921 | 59.4417 | 997.5546 | 79.5498 | 30.1124
|  | 643 | 3612.3561 | 108.025 | 291.7068 | 2969.866 | 71.0494 | 154.3976 | 857.6792 | 13.6791 | 51.4883 | 995.3082 | 79.3707 | 30.0446
|  | 644 | 3617.1158 | 108.1673 | 292.0911 | 2972.4273 | 71.1107 | 154.5308 | 469.7735 | 7.4924 | 28.2015 | 992.747 | 79.1664 | 29.9673
|  | 645 | 3621.8657 | 108.3094 | 292.4747 | 2975.3886 | 71.1815 | 154.6847 | 209.5931 | 3.3428 | 12.5823 | 989.7856 | 78.9303 | 29.8779
|  | 646 | 3576.0282 | 106.9386 | 288.7732 | 2978.6565 | 71.2597 | 154.8546 | 0 | 0 | 0 | 986.5178 | 78.6697 | 29.7792
|  | 647 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 648 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 649 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 650 | 2554.3059 | 76.3847 | 206.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 651 | 2713.95 | 81.1588 | 219.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 652 | 2873.5941 | 85.9328 | 232.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 653 | 3033.2382 | 90.7069 | 244.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 654 | 3192.8823 | 95.4809 | 257.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 655 | 3352.5264 | 100.255 | 270.7249 | 2997.8394 | 71.7186 | 155.8519 | 0 | 0 | 0 | 967.3348 | 77.1399 | 29.2002
|  | 656 | 3512.1706 | 105.029 | 283.6165 | 3000.8414 | 71.7905 | 156.008 | 0 | 0 | 0 | 964.3329 | 76.9005 | 29.1095
|  | 657 | 3635.162 | 108.707 | 293.5484 | 0 | 0 | 0 | 36.6527 | 0.58457 | 2.2003 | 0 | 0 | 0
|  | 658 | 3633.226 | 108.6491 | 293.3921 | 0 | 0 | 0 | 198.2328 | 3.1616 | 11.9003 | 0 | 0 | 0
|  | 659 | 3631.3044 | 108.5916 | 293.2369 | 0 | 0 | 0 | 359.7985 | 5.7384 | 21.5995 | 0 | 0 | 0
|  | 660 | 3629.3973 | 108.5346 | 293.0829 | 0 | 0 | 0 | 521.3498 | 8.315 | 31.2977 | 0 | 0 | 0
|  | 661 | 3627.5044 | 108.478 | 292.93 | 0 | 0 | 0 | 682.8867 | 10.8913 | 40.9951 | 0 | 0 | 0
|  | 662 | 3625.6259 | 108.4218 | 292.7783 | 0 | 0 | 0 | 844.4094 | 13.4675 | 50.6917 | 0 | 0 | 0
|  | 663 | 3623.7616 | 108.3661 | 292.6278 | 0 | 0 | 0 | 686.6296 | 10.951 | 41.2198 | 0 | 0 | 0
|  | 664 | 3624.4788 | 108.3875 | 292.6857 | 3010.3453 | 72.0178 | 156.5021 | 845.5564 | 13.4857 | 50.7605 | 954.8289 | 76.1427 | 28.8227
|  | 665 | 3629.3901 | 108.5344 | 293.0823 | 3011.4342 | 72.0439 | 156.5587 | 1479.2216 | 23.5921 | 88.8008 | 953.7401 | 76.0558 | 28.7898
|  | 666 | 3634.2864 | 108.6808 | 293.4777 | 3012.1684 | 72.0614 | 156.5968 | 1314.6812 | 20.9678 | 78.9231 | 953.0058 | 75.9973 | 28.7676
|  | 667 | 3639.1674 | 108.8268 | 293.8719 | 3012.7636 | 72.0757 | 156.6278 | 1629.0885 | 25.9823 | 97.7976 | 952.4106 | 75.9498 | 28.7497
|  | 668 | 3644.0326 | 108.9723 | 294.2647 | 3013.3493 | 72.0897 | 156.6582 | 1273.0061 | 20.3031 | 76.4212 | 951.8249 | 75.9031 | 28.732
|  | 669 | 3648.8829 | 109.1173 | 294.6564 | 3014.3776 | 72.1143 | 156.7117 | 916.9388 | 14.6242 | 55.0457 | 950.7966 | 75.8211 | 28.7009
|  | 670 | 3653.7193 | 109.2619 | 295.047 | 3015.8477 | 72.1495 | 156.7881 | 560.8854 | 8.9455 | 33.6711 | 949.3265 | 75.7039 | 28.6566
|  | 671 | 3654.3441 | 109.2806 | 295.0974 | 0 | 0 | 0 | 209.0435 | 3.334 | 12.5493 | 0 | 0 | 0
|  | 672 | 3512.1706 | 105.029 | 283.6165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 2182261.1703 |  | 176223.0411 | 879763.2791 |  | 45737.2033 | 640290.5163 |  | 38437.9732 | 341510.382 |  | 10308.9017
Note on C8: Peter North: (Sat-Toutlet = 2 to 5K) Condenser refrig sat temp (30ºC) minus 2ºC approach temp. Needs to be written-up and justified. Sat temp - outlet temp btw 2 to 5K. 2K taken to max deltaT and min mass flowrate.
Note on C9: Peter North: (Toutlet - sat = 5K) Evaporator refrig sat temp (5ºC) plus 5K or 2K approach temp. Needs to be written-up and justified.

## Summer
T0 | K | 273
cp water | kJ/kg.K | 4.18
Tcond.sat | ºC | 30
T evap.sat | ºC | 5
Thot sink | ºC | 20 | 293 | K
Tcold sink | ºC | 10 | 283 | K | Approach Temp
Tcond.hot, out | ºC | 28 | 301 | K | 2 | K
Thp.hot, out | ºC | 10 | 283 | K | 5 | K
Tcond.cold, out | ºC | 25 | 298 | K | 5 | K
Thp.cold, out | ºC | 7 | 280 | K | 2 | K
Summer
|  |  | Hot Sink | [5 empty] | Cold Sink
|  |  | Condenser |  |  | HP Evaporator |  |  | Condenser |  |  | HP Evaporator
|  |  | Qcond, hot | ṁcond, hot | Edest cond, hot | Qhp, hot | ṁhp, hot | Edest hp, hot | Qcond, cold | ṁcond, cold | Edest cond, cold | Qhp, cold | ṁhp, cold | Edest hp, hot
|  |  | kW | kg/s | kW | kW | kg/s | kW | kW | kg/s | kW | kW | kg/s | kW
|  | Total | 1999013.7215 |  | 161425.3519 | 0 |  | 0 | 1028260.9548 |  | 61728.6467 | 209555.2669 |  | 6325.6778 | 229479.6763
Hours
|  | 1 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 3 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 4 | 3082.0192 | 92.1656 | 248.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 5 | 3510.0775 | 104.9664 | 283.4475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 6 | 3720.8569 | 111.2696 | 300.4685 | 0 | 0 | 0 | 46.0556 | 0.73454 | 2.7648 | 0 | 0 | 0
|  | 7 | 3713.486 | 111.0492 | 299.8733 | 0 | 0 | 0 | 310.2613 | 4.9483 | 18.6256 | 680.3742 | 54.2563 | 20.5379
|  | 8 | 3706.1516 | 110.8299 | 299.281 | 0 | 0 | 0 | 574.4306 | 9.1616 | 34.4843 | 680.3742 | 54.2563 | 20.5379
|  | 9 | 3698.8536 | 110.6117 | 298.6917 | 0 | 0 | 0 | 838.5636 | 13.3742 | 50.3407 | 0 | 0 | 0
|  | 10 | 3691.5919 | 110.3945 | 298.1053 | 0 | 0 | 0 | 1102.6603 | 17.5863 | 66.195 | 0 | 0 | 0
|  | 11 | 3684.3662 | 110.1784 | 297.5218 | 0 | 0 | 0 | 1366.7209 | 21.7978 | 82.0471 | 0 | 0 | 0
|  | 12 | 3677.1765 | 109.9634 | 296.9412 | 0 | 0 | 0 | 1630.7455 | 26.0087 | 97.897 | 0 | 0 | 0
|  | 13 | 3670.0228 | 109.7495 | 296.3635 | 0 | 0 | 0 | 1894.7342 | 30.219 | 113.7448 | 0 | 0 | 0
|  | 14 | 3662.9047 | 109.5366 | 295.7887 | 0 | 0 | 0 | 2158.6872 | 34.4288 | 129.5905 | 0 | 0 | 0
|  | 15 | 3655.8223 | 109.3248 | 295.2168 | 0 | 0 | 0 | 1994.5463 | 31.8109 | 119.7368 | 0 | 0 | 0
|  | 16 | 3648.7755 | 109.1141 | 294.6477 | 0 | 0 | 0 | 2229.8909 | 35.5644 | 133.865 | 680.3742 | 54.2563 | 20.5379
|  | 17 | 3642.5575 | 108.9282 | 294.1456 | 0 | 0 | 0 | 3035.1509 | 48.4075 | 182.2064 | 680.3742 | 54.2563 | 20.5379
|  | 18 | 3636.4613 | 108.7459 | 293.6533 | 0 | 0 | 0 | 2870.0238 | 45.7739 | 172.2935 | 680.3742 | 54.2563 | 20.5379
|  | 19 | 3630.3986 | 108.5646 | 293.1638 | 0 | 0 | 0 | 3218.5331 | 51.3323 | 193.2152 | 680.3742 | 54.2563 | 20.5379
|  | 20 | 3624.3693 | 108.3842 | 292.6769 | 0 | 0 | 0 | 2882.1158 | 45.9668 | 173.0194 | 680.3742 | 54.2563 | 20.5379
|  | 21 | 3618.3733 | 108.2049 | 292.1927 | 0 | 0 | 0 | 3401.7817 | 54.2549 | 204.216 | 680.3742 | 54.2563 | 20.5379
|  | 22 | 3612.4104 | 108.0266 | 291.7112 | 0 | 0 | 0 | 2551.6281 | 40.6958 | 153.1795 | 680.3742 | 54.2563 | 20.5379
|  | 23 | 3605.9515 | 107.8335 | 291.1896 | 0 | 0 | 0 | 1701.9705 | 27.1447 | 102.1728 | 0 | 0 | 0
|  | 24 | 3599.1741 | 107.6308 | 290.6423 | 0 | 0 | 0 | 852.6315 | 13.5986 | 51.1852 | 0 | 0 | 0
|  | 25 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 26 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 27 | 2945.0406 | 88.0694 | 237.8194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 28 | 3082.0192 | 92.1656 | 248.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 29 | 3400.0054 | 101.6748 | 274.5589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 30 | 3565.0445 | 106.6102 | 287.8863 | 0 | 0 | 0 | 55.1051 | 0.87887 | 3.3081 | 0 | 0 | 0
|  | 31 | 3558.4792 | 106.4139 | 287.3561 | 0 | 0 | 0 | 281.8146 | 4.4947 | 16.9179 | 680.3742 | 54.2563 | 20.5379
|  | 32 | 3551.9478 | 106.2185 | 286.8287 | 0 | 0 | 0 | 508.4903 | 8.1099 | 30.5257 | 680.3742 | 54.2563 | 20.5379
|  | 33 | 3545.4499 | 106.0242 | 286.3039 | 0 | 0 | 0 | 735.1324 | 11.7246 | 44.1315 | 0 | 0 | 0
|  | 34 | 3538.9856 | 105.8309 | 285.7819 | 0 | 0 | 0 | 961.7409 | 15.3388 | 57.7353 | 0 | 0 | 0
|  | 35 | 3532.5547 | 105.6386 | 285.2626 | 0 | 0 | 0 | 1188.316 | 18.9524 | 71.3371 | 0 | 0 | 0
|  | 36 | 3526.1572 | 105.4473 | 284.746 | 0 | 0 | 0 | 1414.8578 | 22.5655 | 84.9369 | 0 | 0 | 0
|  | 37 | 3519.7928 | 105.257 | 284.2321 | 0 | 0 | 0 | 1641.3664 | 26.1781 | 98.5346 | 0 | 0 | 0
|  | 38 | 3513.4615 | 105.0676 | 283.7208 | 0 | 0 | 0 | 1867.8419 | 29.7901 | 112.1304 | 0 | 0 | 0
|  | 39 | 3507.1632 | 104.8793 | 283.2122 | 0 | 0 | 0 | 2094.2845 | 33.4017 | 125.7243 | 0 | 0 | 0
|  | 40 | 3500.8978 | 104.6919 | 282.7062 | 0 | 0 | 0 | 2320.6941 | 37.0127 | 139.3161 | 680.3742 | 54.2563 | 20.5379
|  | 41 | 3494.9297 | 104.5134 | 282.2243 | 0 | 0 | 0 | 2155.4389 | 34.377 | 129.3955 | 680.3742 | 54.2563 | 20.5379
|  | 42 | 3489.6107 | 104.3544 | 281.7948 | 0 | 0 | 0 | 2503.2045 | 39.9235 | 150.2726 | 680.3742 | 54.2563 | 20.5379
|  | 43 | 3484.3225 | 104.1962 | 281.3677 | 0 | 0 | 0 | 2850.9393 | 45.4695 | 171.1478 | 680.3742 | 54.2563 | 20.5379
|  | 44 | 3479.0651 | 104.039 | 280.9432 | 0 | 0 | 0 | 3027.42 | 48.2842 | 181.7423 | 680.3742 | 54.2563 | 20.5379
|  | 45 | 3473.8383 | 103.8827 | 280.5211 | 0 | 0 | 0 | 3546.3166 | 56.5601 | 212.8928 | 680.3742 | 54.2563 | 20.5379
|  | 46 | 3468.6421 | 103.7273 | 280.1015 | 0 | 0 | 0 | 2695.3964 | 42.9888 | 161.8103 | 680.3742 | 54.2563 | 20.5379
|  | 47 | 3463.4763 | 103.5729 | 279.6844 | 0 | 0 | 0 | 1844.4457 | 29.417 | 110.7259 | 0 | 0 | 0
|  | 48 | 3458.2526 | 103.4166 | 279.2625 | 0 | 0 | 0 | 993.5529 | 15.8461 | 59.6451 | 0 | 0 | 0
|  | 49 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 50 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 51 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 52 | 3082.0192 | 92.1656 | 248.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 53 | 3432.9858 | 102.6611 | 277.2222 | 0 | 0 | 0 | 17.8221 | 0.28424 | 1.0699 | 0 | 0 | 0
|  | 54 | 3427.137 | 102.4862 | 276.7499 | 0 | 0 | 0 | 260.7493 | 4.1587 | 15.6533 | 0 | 0 | 0
|  | 55 | 3421.3195 | 102.3122 | 276.2801 | 0 | 0 | 0 | 503.6451 | 8.0326 | 30.2349 | 680.3742 | 54.2563 | 20.5379
|  | 56 | 3416.3267 | 102.1629 | 275.8769 | 0 | 0 | 0 | 745.7164 | 11.8934 | 44.7669 | 680.3742 | 54.2563 | 20.5379
|  | 57 | 3411.4516 | 102.0171 | 275.4832 | 0 | 0 | 0 | 987.6699 | 15.7523 | 59.2919 | 0 | 0 | 0
|  | 58 | 3406.6057 | 101.8722 | 275.0919 | 0 | 0 | 0 | 1229.5942 | 19.6108 | 73.8151 | 0 | 0 | 0
|  | 59 | 3401.7891 | 101.7281 | 274.703 | 0 | 0 | 0 | 1471.4892 | 23.4687 | 88.3366 | 0 | 0 | 0
|  | 60 | 3397.0016 | 101.585 | 274.3164 | 0 | 0 | 0 | 1713.3551 | 27.3262 | 102.8563 | 0 | 0 | 0
|  | 61 | 3392.2431 | 101.4427 | 273.9321 | 0 | 0 | 0 | 1955.192 | 31.1833 | 117.3742 | 0 | 0 | 0
|  | 62 | 3387.5136 | 101.3012 | 273.5502 | 0 | 0 | 0 | 2196.9999 | 35.0399 | 131.8905 | 0 | 0 | 0
|  | 63 | 3382.8128 | 101.1607 | 273.1706 | 0 | 0 | 0 | 2438.7791 | 38.896 | 146.405 | 0 | 0 | 0
|  | 64 | 3377.2592 | 100.9946 | 272.7221 | 0 | 0 | 0 | 2273.1094 | 36.2537 | 136.4595 | 680.3742 | 54.2563 | 20.5379
|  | 65 | 3371.7359 | 100.8294 | 272.2761 | 0 | 0 | 0 | 2586.8346 | 41.2573 | 155.2931 | 680.3742 | 54.2563 | 20.5379
|  | 66 | 3366.2428 | 100.6652 | 271.8325 | 0 | 0 | 0 | 2900.5297 | 46.2604 | 174.1248 | 680.3742 | 54.2563 | 20.5379
|  | 67 | 3360.7797 | 100.5018 | 271.3914 | 0 | 0 | 0 | 3488.1519 | 55.6324 | 209.401 | 680.3742 | 54.2563 | 20.5379
|  | 68 | 3355.3466 | 100.3393 | 270.9526 | 0 | 0 | 0 | 3493.585 | 55.7191 | 209.7272 | 680.3742 | 54.2563 | 20.5379
|  | 69 | 3349.9434 | 100.1777 | 270.5163 | 0 | 0 | 0 | 3841.4349 | 61.2669 | 230.6093 | 680.3742 | 54.2563 | 20.5379
|  | 70 | 3344.6581 | 100.0197 | 270.0895 | 0 | 0 | 0 | 2956.359 | 47.1509 | 177.4764 | 680.3742 | 54.2563 | 20.5379
|  | 71 | 3340.1956 | 99.8862 | 269.7291 | 0 | 0 | 0 | 2070.4604 | 33.0217 | 124.294 | 0 | 0 | 0
|  | 72 | 3335.761 | 99.7536 | 269.371 | 0 | 0 | 0 | 1184.5339 | 18.8921 | 71.11 | 0 | 0 | 0
|  | 73 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 74 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 75 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 76 | 3082.0192 | 92.1656 | 248.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 77 | 3317.2726 | 99.2007 | 267.878 | 0 | 0 | 0 | 107.1932 | 1.7096 | 6.435 | 0 | 0 | 0
|  | 78 | 3312.9881 | 99.0726 | 267.5321 | 0 | 0 | 0 | 339.7754 | 5.4191 | 20.3974 | 0 | 0 | 0
|  | 79 | 3308.7309 | 98.9453 | 267.1883 | 0 | 0 | 0 | 572.3304 | 9.1281 | 34.3582 | 680.3742 | 54.2563 | 20.5379
|  | 80 | 3304.5008 | 98.8188 | 266.8467 | 0 | 0 | 0 | 804.8582 | 12.8367 | 48.3173 | 680.3742 | 54.2563 | 20.5379
|  | 81 | 3300.2977 | 98.6931 | 266.5073 | 0 | 0 | 0 | 1037.359 | 16.5448 | 62.2748 | 680.3742 | 54.2563 | 20.5379
|  | 82 | 3296.1216 | 98.5682 | 266.1701 | 0 | 0 | 0 | 1269.8328 | 20.2525 | 76.2307 | 680.3742 | 54.2563 | 20.5379
|  | 83 | 3291.9724 | 98.4442 | 265.835 | 0 | 0 | 0 | 1502.2798 | 23.9598 | 90.185 | 680.3742 | 54.2563 | 20.5379
|  | 84 | 3287.8499 | 98.3209 | 265.5021 | 0 | 0 | 0 | 1734.7 | 27.6667 | 104.1377 | 680.3742 | 54.2563 | 20.5379
|  | 85 | 3283.754 | 98.1984 | 265.1713 | 0 | 0 | 0 | 1967.0936 | 31.3731 | 118.0887 | 680.3742 | 54.2563 | 20.5379
|  | 86 | 3279.6847 | 98.0767 | 264.8427 | 0 | 0 | 0 | 2199.4606 | 35.0791 | 132.0382 | 680.3742 | 54.2563 | 20.5379
|  | 87 | 3275.6419 | 97.9558 | 264.5163 | 0 | 0 | 0 | 2032.2802 | 32.4128 | 122.002 | 680.3742 | 54.2563 | 20.5379
|  | 88 | 3271.6254 | 97.8357 | 264.1919 | 0 | 0 | 0 | 2435.8176 | 38.8488 | 146.2272 | 680.3742 | 54.2563 | 20.5379
|  | 89 | 3267.6352 | 97.7164 | 263.8697 | 0 | 0 | 0 | 2839.3289 | 45.2844 | 170.4508 | 680.3742 | 54.2563 | 20.5379
|  | 90 | 3263.6712 | 97.5978 | 263.5496 | 0 | 0 | 0 | 3242.8139 | 51.7195 | 194.6729 | 680.3742 | 54.2563 | 20.5379
|  | 91 | 3259.7332 | 97.4801 | 263.2316 | 0 | 0 | 0 | 2775.8878 | 44.2725 | 166.6423 | 680.3742 | 54.2563 | 20.5379
|  | 92 | 3255.8213 | 97.3631 | 262.9157 | 0 | 0 | 0 | 2308.9357 | 36.8251 | 138.6102 | 680.3742 | 54.2563 | 20.5379
|  | 93 | 3251.9352 | 97.2469 | 262.6019 | 0 | 0 | 0 | 1841.9577 | 29.3773 | 110.5766 | 680.3742 | 54.2563 | 20.5379
|  | 94 | 3248.0749 | 97.1314 | 262.2902 | 0 | 0 | 0 | 1374.954 | 21.9291 | 82.5413 | 680.3742 | 54.2563 | 20.5379
|  | 95 | 3244.2404 | 97.0168 | 261.9805 | 0 | 0 | 0 | 907.9245 | 14.4805 | 54.5046 | 0 | 0 | 0
|  | 96 | 3240.4314 | 96.9029 | 261.6729 | 0 | 0 | 0 | 184.0344 | 2.9352 | 11.048 | 0 | 0 | 0
|  | 97 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 98 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 99 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 100 | 3082.0192 | 92.1656 | 248.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 101 | 3222.4692 | 96.3657 | 260.2224 | 0 | 0 | 0 | 170.8651 | 2.7251 | 10.2574 | 0 | 0 | 0
|  | 102 | 3217.922 | 96.2297 | 259.8552 | 0 | 0 | 0 | 393.3329 | 6.2733 | 23.6126 | 0 | 0 | 0
|  | 103 | 3213.4014 | 96.0945 | 259.4902 | 0 | 0 | 0 | 615.7741 | 9.821 | 36.9662 | 680.3742 | 54.2563 | 20.5379
|  | 104 | 3208.9074 | 95.9601 | 259.1273 | 0 | 0 | 0 | 838.1886 | 13.3682 | 50.3182 | 680.3742 | 54.2563 | 20.5379
|  | 105 | 3204.4398 | 95.8265 | 258.7665 | 0 | 0 | 0 | 1060.5767 | 16.9151 | 63.6686 | 680.3742 | 54.2563 | 20.5379
|  | 106 | 3199.9987 | 95.6937 | 258.4079 | 0 | 0 | 0 | 1282.9384 | 20.4615 | 77.0175 | 680.3742 | 54.2563 | 20.5379
|  | 107 | 3195.5838 | 95.5617 | 258.0514 | 0 | 0 | 0 | 1505.2738 | 24.0076 | 90.3647 | 680.3742 | 54.2563 | 20.5379
|  | 108 | 3191.7243 | 95.4463 | 257.7397 | 0 | 0 | 0 | 1727.0539 | 27.5447 | 103.6786 | 680.3742 | 54.2563 | 20.5379
|  | 109 | 3188.2422 | 95.3422 | 257.4585 | 0 | 0 | 0 | 1948.4565 | 31.0759 | 116.9699 | 680.3742 | 54.2563 | 20.5379
|  | 110 | 3184.7845 | 95.2388 | 257.1793 | 0 | 0 | 0 | 1854.0724 | 29.5705 | 111.3038 | 680.3742 | 54.2563 | 20.5379
|  | 111 | 3181.3511 | 95.1361 | 256.902 | 0 | 0 | 0 | 1759.6639 | 28.0648 | 105.6363 | 680.3742 | 54.2563 | 20.5379
|  | 112 | 3177.9418 | 95.0341 | 256.6267 | 0 | 0 | 0 | 1665.2313 | 26.5587 | 99.9673 | 680.3742 | 54.2563 | 20.5379
|  | 113 | 3174.5566 | 94.9329 | 256.3534 | 0 | 0 | 0 | 1570.7746 | 25.0522 | 94.2969 | 680.3742 | 54.2563 | 20.5379
|  | 114 | 3171.1954 | 94.8324 | 256.0819 | 0 | 0 | 0 | 1476.294 | 23.5454 | 88.625 | 680.3742 | 54.2563 | 20.5379
|  | 115 | 3167.8581 | 94.7326 | 255.8125 | 0 | 0 | 0 | 1381.7894 | 22.0381 | 82.9517 | 680.3742 | 54.2563 | 20.5379
|  | 116 | 3164.5446 | 94.6335 | 255.5449 | 0 | 0 | 0 | 1287.261 | 20.5305 | 77.277 | 680.3742 | 54.2563 | 20.5379
|  | 117 | 3161.2548 | 94.5351 | 255.2792 | 0 | 0 | 0 | 1632.9974 | 26.0446 | 98.0322 | 680.3742 | 54.2563 | 20.5379
|  | 118 | 3157.9887 | 94.4375 | 255.0155 | 0 | 0 | 0 | 1122.5936 | 17.9042 | 67.3916 | 680.3742 | 54.2563 | 20.5379
|  | 119 | 3154.3933 | 94.3299 | 254.7251 | 0 | 0 | 0 | 612.5191 | 9.769 | 36.7708 | 0 | 0 | 0
|  | 120 | 3150.2933 | 94.2073 | 254.3941 | 0 | 0 | 0 | 102.9492 | 1.6419 | 6.1803 | 0 | 0 | 0
|  | 121 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 122 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 123 | 2935.2564 | 87.7768 | 237.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 124 | 3130.9402 | 93.6286 | 252.8312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 125 | 3132.3349 | 93.6703 | 252.9439 | 0 | 0 | 0 | 194.2891 | 3.0987 | 11.6636 | 0 | 0 | 0
|  | 126 | 3128.3739 | 93.5518 | 252.624 | 0 | 0 | 0 | 393.9339 | 6.2828 | 23.6487 | 0 | 0 | 0
|  | 127 | 3124.4374 | 93.4341 | 252.3061 | 0 | 0 | 0 | 593.5541 | 9.4666 | 35.6323 | 680.3742 | 54.2563 | 20.5379
|  | 128 | 3120.5253 | 93.3171 | 251.9902 | 0 | 0 | 0 | 793.1499 | 12.6499 | 47.6144 | 680.3742 | 54.2563 | 20.5379
|  | 129 | 3116.6377 | 93.2009 | 251.6763 | 0 | 0 | 0 | 992.7213 | 15.8329 | 59.5951 | 0 | 0 | 0
|  | 130 | 3112.7743 | 93.0854 | 251.3643 | 0 | 0 | 0 | 1192.2685 | 19.0154 | 71.5744 | 0 | 0 | 0
|  | 131 | 3108.9351 | 92.9705 | 251.0543 | 0 | 0 | 0 | 1391.7914 | 22.1976 | 83.5521 | 0 | 0 | 0
|  | 132 | 3105.12 | 92.8565 | 250.7462 | 0 | 0 | 0 | 1591.2903 | 25.3794 | 95.5285 | 0 | 0 | 0
|  | 133 | 3101.3289 | 92.7431 | 250.4401 | 0 | 0 | 0 | 1692.9232 | 27.0004 | 101.6297 | 0 | 0 | 0
|  | 134 | 3097.5618 | 92.6304 | 250.1359 | 0 | 0 | 0 | 1696.6904 | 27.0605 | 101.8559 | 0 | 0 | 0
|  | 135 | 3093.8185 | 92.5185 | 249.8336 | 0 | 0 | 0 | 2189.6431 | 34.9225 | 131.4488 | 0 | 0 | 0
|  | 136 | 3090.099 | 92.4073 | 249.5332 | 0 | 0 | 0 | 2389.0463 | 38.1028 | 143.4194 | 680.3742 | 54.2563 | 20.5379
|  | 137 | 3086.4032 | 92.2967 | 249.2348 | 0 | 0 | 0 | 2118.7849 | 33.7924 | 127.1951 | 680.3742 | 54.2563 | 20.5379
|  | 138 | 3082.7309 | 92.1869 | 248.9382 | 0 | 0 | 0 | 1848.4999 | 29.4817 | 110.9693 | 680.3742 | 54.2563 | 20.5379
|  | 139 | 3079.435 | 92.0884 | 248.6721 | 0 | 0 | 0 | 1714.8172 | 27.3496 | 102.944 | 680.3742 | 54.2563 | 20.5379
|  | 140 | 3076.6905 | 92.0063 | 248.4504 | 0 | 0 | 0 | 1306.6258 | 20.8393 | 78.4395 | 680.3742 | 54.2563 | 20.5379
|  | 141 | 3073.9677 | 91.9249 | 248.2306 | 0 | 0 | 0 | 1035.3913 | 16.5134 | 62.1567 | 680.3742 | 54.2563 | 20.5379
|  | 142 | 3071.2665 | 91.8441 | 248.0124 | 0 | 0 | 0 | 764.1353 | 12.1872 | 45.8726 | 680.3742 | 54.2563 | 20.5379
|  | 143 | 3068.5868 | 91.764 | 247.796 | 0 | 0 | 0 | 13.4325 | 0.21423 | 0.80638 | 0 | 0 | 0
|  | 144 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 145 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 146 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 147 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 148 | 3057.5869 | 91.435 | 246.9078 | 0 | 0 | 0 | 24.4323 | 0.38967 | 1.4667 | 0 | 0 | 0
|  | 149 | 3055.025 | 91.3584 | 246.7009 | 0 | 0 | 0 | 198.2176 | 3.1614 | 11.8994 | 0 | 0 | 0
|  | 150 | 3052.484 | 91.2824 | 246.4957 | 0 | 0 | 0 | 371.9818 | 5.9327 | 22.3308 | 0 | 0 | 0
|  | 151 | 3049.9639 | 91.2071 | 246.2922 | 0 | 0 | 0 | 545.7252 | 8.7038 | 32.761 | 680.3742 | 54.2563 | 20.5379
|  | 152 | 3047.4646 | 91.1323 | 246.0904 | 0 | 0 | 0 | 719.4478 | 11.4744 | 43.19 | 680.3742 | 54.2563 | 20.5379
|  | 153 | 3044.9861 | 91.0582 | 245.8902 | 0 | 0 | 0 | 893.1496 | 14.2448 | 53.6176 | 0 | 0 | 0
|  | 154 | 3042.4399 | 90.9821 | 245.6846 | 0 | 0 | 0 | 1066.9191 | 17.0163 | 64.0494 | 0 | 0 | 0
|  | 155 | 3039.1213 | 90.8828 | 245.4166 | 0 | 0 | 0 | 1241.461 | 19.8 | 74.5275 | 0 | 0 | 0
|  | 156 | 3035.8248 | 90.7842 | 245.1504 | 0 | 0 | 0 | 1415.9808 | 22.5834 | 85.0043 | 0 | 0 | 0
|  | 157 | 3032.5503 | 90.6863 | 244.886 | 0 | 0 | 0 | 1590.4785 | 25.3665 | 95.4797 | 0 | 0 | 0
|  | 158 | 3029.2979 | 90.5891 | 244.6234 | 0 | 0 | 0 | 1764.9543 | 28.1492 | 105.9539 | 0 | 0 | 0
|  | 159 | 3026.0674 | 90.4924 | 244.3625 | 0 | 0 | 0 | 1596.9615 | 25.4699 | 95.8689 | 0 | 0 | 0
|  | 160 | 3022.8587 | 90.3965 | 244.1034 | 0 | 0 | 0 | 1771.3934 | 28.2519 | 106.3404 | 680.3742 | 54.2563 | 20.5379
|  | 161 | 3019.6718 | 90.3012 | 243.846 | 0 | 0 | 0 | 2459.4735 | 39.2261 | 147.6473 | 680.3742 | 54.2563 | 20.5379
|  | 162 | 3016.5066 | 90.2065 | 243.5904 | 0 | 0 | 0 | 2291.4154 | 36.5457 | 137.5584 | 680.3742 | 54.2563 | 20.5379
|  | 163 | 3013.363 | 90.1125 | 243.3366 | 0 | 0 | 0 | 2637.0056 | 42.0575 | 158.3049 | 680.3742 | 54.2563 | 20.5379
|  | 164 | 3010.2409 | 90.0192 | 243.0845 | 0 | 0 | 0 | 2263.4365 | 36.0995 | 135.8788 | 680.3742 | 54.2563 | 20.5379
|  | 165 | 3007.1403 | 89.9264 | 242.8341 | 0 | 0 | 0 | 1889.8459 | 30.1411 | 113.4514 | 680.3742 | 54.2563 | 20.5379
|  | 166 | 3004.3256 | 89.8423 | 242.6068 | 0 | 0 | 0 | 1515.9693 | 24.1781 | 91.0068 | 680.3742 | 54.2563 | 20.5379
|  | 167 | 3002.1486 | 89.7772 | 242.431 | 0 | 0 | 0 | 1141.4551 | 18.205 | 68.5239 | 0 | 0 | 0
|  | 168 | 2999.9911 | 89.7127 | 242.2568 | 0 | 0 | 0 | 766.9213 | 12.2316 | 46.0399 | 0 | 0 | 0
|  | 169 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 170 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 171 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 172 | 2992.3725 | 89.4848 | 241.6416 | 0 | 0 | 0 | 89.6468 | 1.4298 | 5.3817 | 0 | 0 | 0
|  | 173 | 2990.3078 | 89.4231 | 241.4748 | 0 | 0 | 0 | 519.7696 | 8.2898 | 31.2029 | 0 | 0 | 0
|  | 174 | 2988.2623 | 89.3619 | 241.3096 | 0 | 0 | 0 | 778.6501 | 12.4187 | 46.744 | 0 | 0 | 0
|  | 175 | 2986.2358 | 89.3013 | 241.146 | 0 | 0 | 0 | 1037.5116 | 16.5472 | 62.284 | 680.3742 | 54.2563 | 20.5379
|  | 176 | 2984.2282 | 89.2413 | 240.9839 | 0 | 0 | 0 | 1296.3541 | 20.6755 | 77.8228 | 680.3742 | 54.2563 | 20.5379
|  | 177 | 2982.2395 | 89.1818 | 240.8233 | 0 | 0 | 0 | 1555.1777 | 24.8035 | 93.3606 | 0 | 0 | 0
|  | 178 | 2980.2696 | 89.1229 | 240.6642 | 0 | 0 | 0 | 1813.9826 | 28.9311 | 108.8972 | 0 | 0 | 0
|  | 179 | 2978.3184 | 89.0645 | 240.5067 | 0 | 0 | 0 | 2072.7687 | 33.0585 | 124.4326 | 0 | 0 | 0
|  | 180 | 2976.3859 | 89.0068 | 240.3506 | 0 | 0 | 0 | 2331.5362 | 37.1856 | 139.967 | 0 | 0 | 0
|  | 181 | 2974.472 | 88.9495 | 240.196 | 0 | 0 | 0 | 2590.285 | 41.3124 | 155.5002 | 0 | 0 | 0
|  | 182 | 2972.5765 | 88.8928 | 240.043 | 0 | 0 | 0 | 2849.0154 | 45.4388 | 171.0323 | 0 | 0 | 0
|  | 183 | 2970.6995 | 88.8367 | 239.8914 | 0 | 0 | 0 | 2679.6691 | 42.7379 | 160.8661 | 0 | 0 | 0
|  | 184 | 2968.8409 | 88.7811 | 239.7413 | 0 | 0 | 0 | 2909.8254 | 46.4087 | 174.6829 | 680.3742 | 54.2563 | 20.5379
|  | 185 | 2967.0006 | 88.7261 | 239.5927 | 0 | 0 | 0 | 3710.7078 | 59.1819 | 222.7615 | 680.3742 | 54.2563 | 20.5379
|  | 186 | 2965.1784 | 88.6716 | 239.4456 | 0 | 0 | 0 | 3541.3066 | 56.4802 | 212.592 | 680.3742 | 54.2563 | 20.5379
|  | 187 | 2963.3745 | 88.6177 | 239.2999 | 0 | 0 | 0 | 3885.5572 | 61.9706 | 233.2581 | 680.3742 | 54.2563 | 20.5379
|  | 188 | 2961.5886 | 88.5643 | 239.1557 | 0 | 0 | 0 | 3544.8965 | 56.5374 | 212.8075 | 680.3742 | 54.2563 | 20.5379
|  | 189 | 2959.8207 | 88.5114 | 239.0129 | 0 | 0 | 0 | 4060.3343 | 64.7581 | 243.7503 | 680.3742 | 54.2563 | 20.5379
|  | 190 | 2958.0707 | 88.4591 | 238.8716 | 0 | 0 | 0 | 3205.9678 | 51.1319 | 192.4609 | 680.3742 | 54.2563 | 20.5379
|  | 191 | 2956.3386 | 88.4073 | 238.7317 | 0 | 0 | 0 | 2351.5835 | 37.5053 | 141.1705 | 0 | 0 | 0
|  | 192 | 2954.6243 | 88.356 | 238.5933 | 0 | 0 | 0 | 1497.1813 | 23.8785 | 89.8789 | 0 | 0 | 0
|  | 193 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 194 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 195 | 2945.0406 | 88.0694 | 237.8194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 196 | 2948.4698 | 88.1719 | 238.0963 | 0 | 0 | 0 | 133.5494 | 2.13 | 8.0173 | 0 | 0 | 0
|  | 197 | 2946.8409 | 88.1232 | 237.9648 | 0 | 0 | 0 | 453.1644 | 7.2275 | 27.2044 | 0 | 0 | 0
|  | 198 | 2945.2295 | 88.075 | 237.8346 | 0 | 0 | 0 | 674.9201 | 10.7643 | 40.5169 | 0 | 0 | 0
|  | 199 | 2943.6353 | 88.0274 | 237.7059 | 0 | 0 | 0 | 896.6585 | 14.3008 | 53.8283 | 680.3742 | 54.2563 | 20.5379
|  | 200 | 2942.0584 | 87.9802 | 237.5786 | 0 | 0 | 0 | 1118.3797 | 17.837 | 67.1387 | 680.3742 | 54.2563 | 20.5379
|  | 201 | 2940.4986 | 87.9336 | 237.4526 | 0 | 0 | 0 | 1340.0837 | 21.3729 | 80.448 | 0 | 0 | 0
|  | 202 | 2938.9559 | 87.8874 | 237.328 | 0 | 0 | 0 | 1561.7706 | 24.9086 | 93.7563 | 0 | 0 | 0
|  | 203 | 2937.4303 | 87.8418 | 237.2048 | 0 | 0 | 0 | 1783.4404 | 28.444 | 107.0636 | 0 | 0 | 0
|  | 204 | 2935.9216 | 87.7967 | 237.083 | 0 | 0 | 0 | 2005.0933 | 31.9792 | 120.3699 | 0 | 0 | 0
|  | 205 | 2934.4299 | 87.7521 | 236.9625 | 0 | 0 | 0 | 2226.7294 | 35.514 | 133.6752 | 0 | 0 | 0
|  | 206 | 2932.9549 | 87.708 | 236.8434 | 0 | 0 | 0 | 2448.3485 | 39.0486 | 146.9795 | 0 | 0 | 0
|  | 207 | 2931.4967 | 87.6644 | 236.7257 | 0 | 0 | 0 | 2669.951 | 42.5829 | 160.2827 | 0 | 0 | 0
|  | 208 | 2930.0552 | 87.6213 | 236.6093 | 0 | 0 | 0 | 2891.5367 | 46.117 | 173.585 | 680.3742 | 54.2563 | 20.5379
|  | 209 | 2928.6303 | 87.5787 | 236.4942 | 0 | 0 | 0 | 2721.7383 | 43.4089 | 163.3916 | 680.3742 | 54.2563 | 20.5379
|  | 210 | 2927.222 | 87.5365 | 236.3805 | 0 | 0 | 0 | 3065.5932 | 48.893 | 184.0339 | 680.3742 | 54.2563 | 20.5379
|  | 211 | 2925.8302 | 87.4949 | 236.2681 | 0 | 0 | 0 | 3409.4316 | 54.3769 | 204.6753 | 680.3742 | 54.2563 | 20.5379
|  | 212 | 2924.4548 | 87.4538 | 236.157 | 0 | 0 | 0 | 3582.0303 | 57.1297 | 215.0367 | 680.3742 | 54.2563 | 20.5379
|  | 213 | 2923.0957 | 87.4131 | 236.0473 | 0 | 0 | 0 | 4097.0593 | 65.3438 | 245.955 | 680.3742 | 54.2563 | 20.5379
|  | 214 | 2921.7529 | 87.373 | 235.9388 | 0 | 0 | 0 | 3242.2856 | 51.7111 | 194.6412 | 680.3742 | 54.2563 | 20.5379
|  | 215 | 2920.4264 | 87.3333 | 235.8317 | 0 | 0 | 0 | 2387.4957 | 38.0781 | 143.3263 | 0 | 0 | 0
|  | 216 | 2919.116 | 87.2941 | 235.7259 | 0 | 0 | 0 | 1532.6896 | 24.4448 | 92.0105 | 0 | 0 | 0
|  | 217 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 218 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 219 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 220 | 2914.4433 | 87.1544 | 235.3486 | 0 | 0 | 0 | 167.576 | 2.6727 | 10.0599 | 0 | 0 | 0
|  | 221 | 2913.2108 | 87.1175 | 235.249 | 0 | 0 | 0 | 537.5971 | 8.5741 | 32.2731 | 0 | 0 | 0
|  | 222 | 2911.9941 | 87.0812 | 235.1508 | 0 | 0 | 0 | 775.8922 | 12.3747 | 46.5784 | 0 | 0 | 0
|  | 223 | 2910.7931 | 87.0452 | 235.0538 | 0 | 0 | 0 | 1014.1716 | 16.175 | 60.8828 | 680.3742 | 54.2563 | 20.5379
|  | 224 | 2909.6078 | 87.0098 | 234.9581 | 0 | 0 | 0 | 1252.4353 | 19.975 | 75.1863 | 680.3742 | 54.2563 | 20.5379
|  | 225 | 2908.438 | 86.9748 | 234.8636 | 0 | 0 | 0 | 1490.6835 | 23.7749 | 89.4888 | 0 | 0 | 0
|  | 226 | 2907.2837 | 86.9403 | 234.7704 | 0 | 0 | 0 | 1728.9162 | 27.5744 | 103.7904 | 0 | 0 | 0
|  | 227 | 2906.1449 | 86.9062 | 234.6785 | 0 | 0 | 0 | 1967.1334 | 31.3737 | 118.0911 | 0 | 0 | 0
|  | 228 | 2905.0215 | 86.8727 | 234.5877 | 0 | 0 | 0 | 2205.3352 | 35.1728 | 132.3909 | 0 | 0 | 0
|  | 229 | 2903.9134 | 86.8395 | 234.4983 | 0 | 0 | 0 | 2443.5217 | 38.9716 | 146.6897 | 0 | 0 | 0
|  | 230 | 2902.8206 | 86.8068 | 234.41 | 0 | 0 | 0 | 2681.693 | 42.7702 | 160.9876 | 0 | 0 | 0
|  | 231 | 2901.7429 | 86.7746 | 234.323 | 0 | 0 | 0 | 2919.849 | 46.5686 | 175.2846 | 0 | 0 | 0
|  | 232 | 2900.6804 | 86.7428 | 234.2372 | 0 | 0 | 0 | 2749.6882 | 43.8547 | 165.0695 | 680.3742 | 54.2563 | 20.5379
|  | 233 | 2899.633 | 86.7115 | 234.1526 | 0 | 0 | 0 | 3058.9376 | 48.7869 | 183.6344 | 680.3742 | 54.2563 | 20.5379
|  | 234 | 2898.6005 | 86.6806 | 234.0692 | 0 | 0 | 0 | 3368.1719 | 53.7189 | 202.1984 | 680.3742 | 54.2563 | 20.5379
|  | 235 | 2897.5831 | 86.6502 | 233.9871 | 0 | 0 | 0 | 3951.3486 | 63.0199 | 237.2077 | 680.3742 | 54.2563 | 20.5379
|  | 236 | 2896.5805 | 86.6202 | 233.9061 | 0 | 0 | 0 | 3952.3512 | 63.0359 | 237.2679 | 680.3742 | 54.2563 | 20.5379
|  | 237 | 2895.5927 | 86.5907 | 233.8263 | 0 | 0 | 0 | 4295.7856 | 68.5133 | 257.885 | 680.3742 | 54.2563 | 20.5379
|  | 238 | 2894.6197 | 86.5616 | 233.7478 | 0 | 0 | 0 | 3406.3975 | 54.3285 | 204.4931 | 680.3742 | 54.2563 | 20.5379
|  | 239 | 2893.6613 | 86.5329 | 233.6704 | 0 | 0 | 0 | 2516.9947 | 40.1435 | 151.1004 | 0 | 0 | 0
|  | 240 | 2892.7177 | 86.5047 | 233.5942 | 0 | 0 | 0 | 1627.5772 | 25.9582 | 97.7069 | 0 | 0 | 0
|  | 241 | 2891.7886 | 86.4769 | 233.5192 | 0 | 0 | 0 | 19.0074 | 0.30315 | 1.1411 | 0 | 0 | 0
|  | 242 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 243 | 2888.5091 | 86.3789 | 233.2543 | 0 | 0 | 0 | 22.2869 | 0.35545 | 1.3379 | 0 | 0 | 0
|  | 244 | 2886.7438 | 86.3261 | 233.1118 | 0 | 0 | 0 | 195.2755 | 3.1144 | 11.7228 | 0 | 0 | 0
|  | 245 | 2884.9945 | 86.2738 | 232.9705 | 0 | 0 | 0 | 539.4713 | 8.604 | 32.3856 | 0 | 0 | 0
|  | 246 | 2883.2612 | 86.2219 | 232.8305 | 0 | 0 | 0 | 769.5024 | 12.2728 | 46.1948 | 0 | 0 | 0
|  | 247 | 2881.5437 | 86.1706 | 232.6919 | 0 | 0 | 0 | 999.5175 | 15.9413 | 60.0031 | 680.3742 | 54.2563 | 20.5379
|  | 248 | 2879.8421 | 86.1197 | 232.5544 | 0 | 0 | 0 | 1229.5169 | 19.6095 | 73.8105 | 680.3742 | 54.2563 | 20.5379
|  | 249 | 2878.1562 | 86.0693 | 232.4183 | 0 | 0 | 0 | 1459.5005 | 23.2775 | 87.6169 | 680.3742 | 54.2563 | 20.5379
|  | 250 | 2876.486 | 86.0193 | 232.2834 | 0 | 0 | 0 | 1689.4684 | 26.9453 | 101.4223 | 680.3742 | 54.2563 | 20.5379
|  | 251 | 2874.8315 | 85.9698 | 232.1498 | 0 | 0 | 0 | 1919.4207 | 30.6128 | 115.2268 | 680.3742 | 54.2563 | 20.5379
|  | 252 | 2873.1925 | 85.9208 | 232.0175 | 0 | 0 | 0 | 2149.3574 | 34.28 | 129.0304 | 680.3742 | 54.2563 | 20.5379
|  | 253 | 2871.569 | 85.8723 | 231.8864 | 0 | 0 | 0 | 2379.2786 | 37.947 | 142.833 | 680.3742 | 54.2563 | 20.5379
|  | 254 | 2869.961 | 85.8242 | 231.7565 | 0 | 0 | 0 | 2609.1843 | 41.6138 | 156.6348 | 680.3742 | 54.2563 | 20.5379
|  | 255 | 2868.3684 | 85.7766 | 231.6279 | 0 | 0 | 0 | 2439.5537 | 38.9084 | 146.4515 | 680.3742 | 54.2563 | 20.5379
|  | 256 | 2866.7911 | 85.7294 | 231.5005 | 0 | 0 | 0 | 2840.652 | 45.3055 | 170.5303 | 680.3742 | 54.2563 | 20.5379
|  | 257 | 2865.229 | 85.6827 | 231.3744 | 0 | 0 | 0 | 3241.735 | 51.7023 | 194.6081 | 680.3742 | 54.2563 | 20.5379
|  | 258 | 2863.6822 | 85.6364 | 231.2495 | 0 | 0 | 0 | 3642.8029 | 58.0989 | 218.685 | 680.3742 | 54.2563 | 20.5379
|  | 259 | 2862.1505 | 85.5906 | 231.1258 | 0 | 0 | 0 | 3173.4705 | 50.6136 | 190.51 | 680.3742 | 54.2563 | 20.5379
|  | 260 | 2860.6339 | 85.5453 | 231.0033 | 0 | 0 | 0 | 2704.123 | 43.128 | 162.3341 | 680.3742 | 54.2563 | 20.5379
|  | 261 | 2859.1324 | 85.5004 | 230.8821 | 0 | 0 | 0 | 2234.7606 | 35.6421 | 134.1573 | 680.3742 | 54.2563 | 20.5379
|  | 262 | 2857.6458 | 85.4559 | 230.762 | 0 | 0 | 0 | 1765.3831 | 28.156 | 105.9796 | 680.3742 | 54.2563 | 20.5379
|  | 263 | 2856.1741 | 85.4119 | 230.6432 | 0 | 0 | 0 | 1295.9907 | 20.6697 | 77.801 | 0 | 0 | 0
|  | 264 | 2854.7172 | 85.3683 | 230.5255 | 0 | 0 | 0 | 569.7486 | 9.0869 | 34.2032 | 0 | 0 | 0
|  | 265 | 2853.2752 | 85.3252 | 230.4091 | 0 | 0 | 0 | 57.5208 | 0.9174 | 3.4531 | 0 | 0 | 0
|  | 266 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 267 | 2850.6004 | 85.2452 | 230.1931 | 0 | 0 | 0 | 60.1955 | 0.96006 | 3.6137 | 0 | 0 | 0
|  | 268 | 2849.2017 | 85.2034 | 230.0802 | 0 | 0 | 0 | 232.8176 | 3.7132 | 13.9765 | 0 | 0 | 0
|  | 269 | 2847.8174 | 85.162 | 229.9684 | 0 | 0 | 0 | 545.5169 | 8.7004 | 32.7485 | 0 | 0 | 0
|  | 270 | 2846.4477 | 85.121 | 229.8578 | 0 | 0 | 0 | 764.8072 | 12.1979 | 45.913 | 0 | 0 | 0
|  | 271 | 2845.0924 | 85.0805 | 229.7483 | 0 | 0 | 0 | 984.083 | 15.6951 | 59.0766 | 680.3742 | 54.2563 | 20.5379
|  | 272 | 2843.7516 | 85.0404 | 229.64 | 0 | 0 | 0 | 1203.3444 | 19.1921 | 72.2393 | 680.3742 | 54.2563 | 20.5379
|  | 273 | 2842.425 | 85.0007 | 229.5329 | 0 | 0 | 0 | 1422.5915 | 22.6889 | 85.4011 | 680.3742 | 54.2563 | 20.5379
|  | 274 | 2841.1127 | 84.9615 | 229.4269 | 0 | 0 | 0 | 1641.8244 | 26.1854 | 98.5621 | 680.3742 | 54.2563 | 20.5379
|  | 275 | 2839.8146 | 84.9227 | 229.3221 | 0 | 0 | 0 | 1861.043 | 29.6817 | 111.7223 | 680.3742 | 54.2563 | 20.5379
|  | 276 | 2838.5307 | 84.8843 | 229.2184 | 0 | 0 | 0 | 2080.2475 | 33.1778 | 124.8816 | 680.3742 | 54.2563 | 20.5379
|  | 277 | 2837.2609 | 84.8463 | 229.1159 | 0 | 0 | 0 | 2299.4378 | 36.6736 | 138.04 | 680.3742 | 54.2563 | 20.5379
|  | 278 | 2836.0051 | 84.8088 | 229.0145 | 0 | 0 | 0 | 2202.8517 | 35.1332 | 132.2418 | 680.3742 | 54.2563 | 20.5379
|  | 279 | 2834.7634 | 84.7716 | 228.9142 | 0 | 0 | 0 | 2106.2516 | 33.5925 | 126.4427 | 680.3742 | 54.2563 | 20.5379
|  | 280 | 2833.5355 | 84.7349 | 228.8151 | 0 | 0 | 0 | 2009.6376 | 32.0516 | 120.6427 | 680.3742 | 54.2563 | 20.5379
|  | 281 | 2832.3215 | 84.6986 | 228.717 | 0 | 0 | 0 | 1913.0097 | 30.5105 | 114.842 | 680.3742 | 54.2563 | 20.5379
|  | 282 | 2831.1214 | 84.6627 | 228.6201 | 0 | 0 | 0 | 1816.368 | 28.9692 | 109.0404 | 680.3742 | 54.2563 | 20.5379
|  | 283 | 2829.935 | 84.6272 | 228.5243 | 0 | 0 | 0 | 1719.7125 | 27.4276 | 103.2379 | 680.3742 | 54.2563 | 20.5379
|  | 284 | 2828.7623 | 84.5922 | 228.4296 | 0 | 0 | 0 | 1623.0433 | 25.8859 | 97.4347 | 680.3742 | 54.2563 | 20.5379
|  | 285 | 2827.6033 | 84.5575 | 228.336 | 0 | 0 | 0 | 1966.6489 | 31.366 | 118.062 | 680.3742 | 54.2563 | 20.5379
|  | 286 | 2826.4579 | 84.5233 | 228.2435 | 0 | 0 | 0 | 1454.1244 | 23.1918 | 87.2941 | 680.3742 | 54.2563 | 20.5379
|  | 287 | 2825.326 | 84.4894 | 228.1521 | 0 | 0 | 0 | 941.5864 | 15.0173 | 56.5254 | 0 | 0 | 0
|  | 288 | 2824.2076 | 84.456 | 228.0618 | 0 | 0 | 0 | 429.035 | 6.8427 | 25.7559 | 0 | 0 | 0
|  | 289 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 290 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 291 | 2821.1725 | 84.3652 | 227.8167 | 0 | 0 | 0 | 114.084 | 1.8195 | 6.8487 | 0 | 0 | 0
|  | 292 | 2820.1064 | 84.3333 | 227.7306 | 0 | 0 | 0 | 310.8338 | 4.9575 | 18.66 | 0 | 0 | 0
|  | 293 | 2819.0535 | 84.3018 | 227.6456 | 0 | 0 | 0 | 507.5705 | 8.0952 | 30.4705 | 0 | 0 | 0
|  | 294 | 2818.0138 | 84.2707 | 227.5617 | 0 | 0 | 0 | 704.2939 | 11.2328 | 42.2802 | 0 | 0 | 0
|  | 295 | 2816.9872 | 84.24 | 227.4788 | 0 | 0 | 0 | 901.0043 | 14.3701 | 54.0892 | 680.3742 | 54.2563 | 20.5379
|  | 296 | 2816.4146 | 84.2229 | 227.4325 | 0 | 0 | 0 | 1097.2606 | 17.5002 | 65.8708 | 680.3742 | 54.2563 | 20.5379
|  | 297 | 2816.2947 | 84.2193 | 227.4228 | 0 | 0 | 0 | 1293.0643 | 20.623 | 77.6253 | 0 | 0 | 0
|  | 298 | 2816.1861 | 84.2161 | 227.4141 | 0 | 0 | 0 | 1488.8566 | 23.7457 | 89.3792 | 0 | 0 | 0
|  | 299 | 2816.0888 | 84.2132 | 227.4062 | 0 | 0 | 0 | 1684.6377 | 26.8682 | 101.1323 | 0 | 0 | 0
|  | 300 | 2816.0026 | 84.2106 | 227.3992 | 0 | 0 | 0 | 1880.4077 | 29.9906 | 112.8848 | 0 | 0 | 0
|  | 301 | 2815.9276 | 84.2084 | 227.3932 | 0 | 0 | 0 | 1978.3246 | 31.5522 | 118.7629 | 0 | 0 | 0
|  | 302 | 2815.8636 | 84.2064 | 227.388 | 0 | 0 | 0 | 1978.3886 | 31.5532 | 118.7668 | 0 | 0 | 0
|  | 303 | 2815.8107 | 84.2049 | 227.3837 | 0 | 0 | 0 | 2467.6509 | 39.3565 | 148.1382 | 0 | 0 | 0
|  | 304 | 2815.7687 | 84.2036 | 227.3804 | 0 | 0 | 0 | 2663.3766 | 42.4781 | 159.888 | 680.3742 | 54.2563 | 20.5379
|  | 305 | 2815.7377 | 84.2027 | 227.3779 | 0 | 0 | 0 | 2389.4504 | 38.1093 | 143.4437 | 680.3742 | 54.2563 | 20.5379
|  | 306 | 2815.7175 | 84.2021 | 227.3762 | 0 | 0 | 0 | 2115.5133 | 33.7402 | 126.9987 | 680.3742 | 54.2563 | 20.5379
|  | 307 | 2815.7082 | 84.2018 | 227.3755 | 0 | 0 | 0 | 1978.5439 | 31.5557 | 118.7761 | 680.3742 | 54.2563 | 20.5379
|  | 308 | 2815.7097 | 84.2018 | 227.3756 | 0 | 0 | 0 | 1567.6066 | 25.0017 | 94.1067 | 680.3742 | 54.2563 | 20.5379
|  | 309 | 2815.7219 | 84.2022 | 227.3766 | 0 | 0 | 0 | 1293.6371 | 20.6322 | 77.6597 | 680.3742 | 54.2563 | 20.5379
|  | 310 | 2815.7447 | 84.2029 | 227.3784 | 0 | 0 | 0 | 1019.657 | 16.2625 | 61.2121 | 680.3742 | 54.2563 | 20.5379
|  | 311 | 2815.7782 | 84.2039 | 227.3811 | 0 | 0 | 0 | 266.241 | 4.2463 | 15.983 | 0 | 0 | 0
|  | 312 | 2815.8223 | 84.2052 | 227.3847 | 0 | 0 | 0 | 94.9736 | 1.5147 | 5.7015 | 0 | 0 | 0
|  | 313 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 314 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 315 | 2816.2648 | 84.2184 | 227.4204 | 0 | 0 | 0 | 94.5311 | 1.5077 | 5.6749 | 0 | 0 | 0
|  | 316 | 2816.3496 | 84.221 | 227.4273 | 0 | 0 | 0 | 265.6696 | 4.2372 | 15.9487 | 0 | 0 | 0
|  | 317 | 2816.4447 | 84.2238 | 227.4349 | 0 | 0 | 0 | 436.7978 | 6.9665 | 26.2219 | 0 | 0 | 0
|  | 318 | 2816.5502 | 84.227 | 227.4435 | 0 | 0 | 0 | 607.9157 | 9.6956 | 36.4944 | 0 | 0 | 0
|  | 319 | 2816.6658 | 84.2304 | 227.4528 | 0 | 0 | 0 | 779.0233 | 12.4246 | 46.7664 | 680.3742 | 54.2563 | 20.5379
|  | 320 | 2816.7917 | 84.2342 | 227.463 | 0 | 0 | 0 | 950.1207 | 15.1534 | 57.0377 | 680.3742 | 54.2563 | 20.5379
|  | 321 | 2816.9278 | 84.2383 | 227.474 | 0 | 0 | 0 | 1121.208 | 17.8821 | 67.3084 | 0 | 0 | 0
|  | 322 | 2817.0739 | 84.2426 | 227.4858 | 0 | 0 | 0 | 1292.2851 | 20.6106 | 77.5786 | 0 | 0 | 0
|  | 323 | 2817.2301 | 84.2473 | 227.4984 | 0 | 0 | 0 | 1463.3522 | 23.339 | 87.8481 | 0 | 0 | 0
|  | 324 | 2817.3963 | 84.2523 | 227.5118 | 0 | 0 | 0 | 1634.4093 | 26.0671 | 98.117 | 0 | 0 | 0
|  | 325 | 2817.5725 | 84.2575 | 227.526 | 0 | 0 | 0 | 1805.4564 | 28.7952 | 108.3853 | 0 | 0 | 0
|  | 326 | 2817.7585 | 84.2631 | 227.541 | 0 | 0 | 0 | 1976.4936 | 31.523 | 118.653 | 0 | 0 | 0
|  | 327 | 2817.9545 | 84.269 | 227.5569 | 0 | 0 | 0 | 1805.0744 | 28.7891 | 108.3624 | 0 | 0 | 0
|  | 328 | 2818.1603 | 84.2751 | 227.5735 | 0 | 0 | 0 | 1976.0919 | 31.5166 | 118.6289 | 680.3742 | 54.2563 | 20.5379
|  | 329 | 2818.3758 | 84.2816 | 227.5909 | 0 | 0 | 0 | 2660.7695 | 42.4365 | 159.7315 | 680.3742 | 54.2563 | 20.5379
|  | 330 | 2818.6011 | 84.2883 | 227.6091 | 0 | 0 | 0 | 2489.3209 | 39.7021 | 149.4391 | 680.3742 | 54.2563 | 20.5379
|  | 331 | 2818.8361 | 84.2953 | 227.6281 | 0 | 0 | 0 | 2831.5325 | 45.16 | 169.9828 | 680.3742 | 54.2563 | 20.5379
|  | 332 | 2819.0807 | 84.3027 | 227.6478 | 0 | 0 | 0 | 2454.5967 | 39.1483 | 147.3546 | 680.3742 | 54.2563 | 20.5379
|  | 333 | 2819.3349 | 84.3103 | 227.6683 | 0 | 0 | 0 | 2077.6512 | 33.1364 | 124.7257 | 680.3742 | 54.2563 | 20.5379
|  | 334 | 2819.5987 | 84.3181 | 227.6896 | 0 | 0 | 0 | 1700.6962 | 27.1243 | 102.0963 | 680.3742 | 54.2563 | 20.5379
|  | 335 | 2819.8719 | 84.3263 | 227.7117 | 0 | 0 | 0 | 1323.7317 | 21.1121 | 79.4664 | 0 | 0 | 0
|  | 336 | 2820.1547 | 84.3348 | 227.7345 | 0 | 0 | 0 | 946.7578 | 15.0998 | 56.8358 | 0 | 0 | 0
|  | 337 | 2820.4468 | 84.3435 | 227.7581 | 0 | 0 | 0 | 90.3492 | 1.441 | 5.4238 | 0 | 0 | 0
|  | 338 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 339 | 2821.1453 | 84.3644 | 227.8145 | 0 | 0 | 0 | 89.6507 | 1.4298 | 5.3819 | 0 | 0 | 0
|  | 340 | 2821.465 | 84.374 | 227.8403 | 0 | 0 | 0 | 260.5543 | 4.1556 | 15.6416 | 0 | 0 | 0
|  | 341 | 2821.7939 | 84.3838 | 227.8669 | 0 | 0 | 0 | 688.2836 | 10.9774 | 41.3191 | 0 | 0 | 0
|  | 342 | 2822.1321 | 84.3939 | 227.8942 | 0 | 0 | 0 | 944.7804 | 15.0683 | 56.7171 | 0 | 0 | 0
|  | 343 | 2822.4793 | 84.4043 | 227.9223 | 0 | 0 | 0 | 1201.268 | 19.159 | 72.1146 | 680.3742 | 54.2563 | 20.5379
|  | 344 | 2822.8357 | 84.4149 | 227.951 | 0 | 0 | 0 | 1457.7466 | 23.2495 | 87.5116 | 680.3742 | 54.2563 | 20.5379
|  | 345 | 2823.2011 | 84.4259 | 227.9805 | 0 | 0 | 0 | 1714.2161 | 27.34 | 102.908 | 0 | 0 | 0
|  | 346 | 2823.5756 | 84.4371 | 228.0108 | 0 | 0 | 0 | 1970.6766 | 31.4302 | 118.3038 | 0 | 0 | 0
|  | 347 | 2823.959 | 84.4485 | 228.0417 | 0 | 0 | 0 | 2227.1281 | 35.5204 | 133.6991 | 0 | 0 | 0
|  | 348 | 2824.3513 | 84.4603 | 228.0734 | 0 | 0 | 0 | 2483.5707 | 39.6104 | 149.0939 | 0 | 0 | 0
|  | 349 | 2824.7525 | 84.4723 | 228.1058 | 0 | 0 | 0 | 2740.0044 | 43.7002 | 164.4882 | 0 | 0 | 0
|  | 350 | 2825.1626 | 84.4845 | 228.1389 | 0 | 0 | 0 | 2996.4293 | 47.7899 | 179.8819 | 0 | 0 | 0
|  | 351 | 2825.5815 | 84.4971 | 228.1728 | 0 | 0 | 0 | 2824.7872 | 45.0524 | 169.5779 | 0 | 0 | 0
|  | 352 | 2826.0091 | 84.5098 | 228.2073 | 0 | 0 | 0 | 3052.6573 | 48.6867 | 183.2574 | 680.3742 | 54.2563 | 20.5379
|  | 353 | 2826.4454 | 84.5229 | 228.2425 | 0 | 0 | 0 | 3851.263 | 61.4237 | 231.1993 | 680.3742 | 54.2563 | 20.5379
|  | 354 | 2826.8904 | 84.5362 | 228.2785 | 0 | 0 | 0 | 3679.5947 | 58.6857 | 220.8937 | 680.3742 | 54.2563 | 20.5379
|  | 355 | 2827.344 | 84.5498 | 228.3151 | 0 | 0 | 0 | 4021.5877 | 64.1402 | 241.4243 | 680.3742 | 54.2563 | 20.5379
|  | 356 | 2827.8062 | 84.5636 | 228.3524 | 0 | 0 | 0 | 3678.6789 | 58.6711 | 220.8388 | 680.3742 | 54.2563 | 20.5379
|  | 357 | 2828.2769 | 84.5777 | 228.3904 | 0 | 0 | 0 | 4191.878 | 66.8561 | 251.6472 | 680.3742 | 54.2563 | 20.5379
|  | 358 | 2828.7562 | 84.592 | 228.4291 | 0 | 0 | 0 | 3335.2823 | 53.1943 | 200.2239 | 680.3742 | 54.2563 | 20.5379
|  | 359 | 2829.2439 | 84.6066 | 228.4685 | 0 | 0 | 0 | 2478.6782 | 39.5323 | 148.8002 | 0 | 0 | 0
|  | 360 | 2829.74 | 84.6214 | 228.5086 | 0 | 0 | 0 | 1622.0656 | 25.8703 | 97.376 | 0 | 0 | 0
|  | 361 | 2830.2445 | 84.6365 | 228.5493 | 0 | 0 | 0 | 80.5515 | 1.2847 | 4.8357 | 0 | 0 | 0
|  | 362 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 363 | 2831.3782 | 84.6704 | 228.6409 | 0 | 0 | 0 | 113.6624 | 1.8128 | 6.8234 | 0 | 0 | 0
|  | 364 | 2831.9071 | 84.6862 | 228.6836 | 0 | 0 | 0 | 250.1122 | 3.989 | 15.0148 | 0 | 0 | 0
|  | 365 | 2832.4442 | 84.7023 | 228.7269 | 0 | 0 | 0 | 567.5612 | 9.052 | 34.0719 | 0 | 0 | 0
|  | 366 | 2832.9895 | 84.7186 | 228.771 | 0 | 0 | 0 | 787.1601 | 12.5544 | 47.2549 | 0 | 0 | 0
|  | 367 | 2833.5429 | 84.7351 | 228.8157 | 0 | 0 | 0 | 1006.751 | 16.0566 | 60.4374 | 680.3742 | 54.2563 | 20.5379
|  | 368 | 2834.1044 | 84.7519 | 228.861 | 0 | 0 | 0 | 1226.3337 | 19.5588 | 73.6194 | 680.3742 | 54.2563 | 20.5379
|  | 369 | 2834.6739 | 84.769 | 228.907 | 0 | 0 | 0 | 1445.9084 | 23.0607 | 86.8009 | 0 | 0 | 0
|  | 370 | 2835.2514 | 84.7862 | 228.9536 | 0 | 0 | 0 | 1665.4751 | 26.5626 | 99.9819 | 0 | 0 | 0
|  | 371 | 2835.8369 | 84.8037 | 229.0009 | 0 | 0 | 0 | 1885.0338 | 30.0643 | 113.1625 | 0 | 0 | 0
|  | 372 | 2836.4304 | 84.8215 | 229.0488 | 0 | 0 | 0 | 2104.5846 | 33.5659 | 126.3426 | 0 | 0 | 0
|  | 373 | 2837.0317 | 84.8395 | 229.0974 | 0 | 0 | 0 | 2324.1275 | 37.0674 | 139.5222 | 0 | 0 | 0
|  | 374 | 2837.6408 | 84.8577 | 229.1466 | 0 | 0 | 0 | 2543.6626 | 40.5688 | 152.7014 | 0 | 0 | 0
|  | 375 | 2838.2578 | 84.8761 | 229.1964 | 0 | 0 | 0 | 2763.1899 | 44.07 | 165.88 | 0 | 0 | 0
|  | 376 | 2838.8825 | 84.8948 | 229.2469 | 0 | 0 | 0 | 2982.7094 | 47.5711 | 179.0583 | 680.3742 | 54.2563 | 20.5379
|  | 377 | 2839.515 | 84.9137 | 229.2979 | 0 | 0 | 0 | 2810.8536 | 44.8302 | 168.7414 | 680.3742 | 54.2563 | 20.5379
|  | 378 | 2840.1551 | 84.9329 | 229.3496 | 0 | 0 | 0 | 3152.6601 | 50.2817 | 189.2607 | 680.3742 | 54.2563 | 20.5379
|  | 379 | 2840.8029 | 84.9522 | 229.4019 | 0 | 0 | 0 | 3494.4589 | 55.733 | 209.7796 | 680.3742 | 54.2563 | 20.5379
|  | 380 | 2841.4583 | 84.9718 | 229.4549 | 0 | 0 | 0 | 3665.0267 | 58.4534 | 220.0192 | 680.3742 | 54.2563 | 20.5379
|  | 381 | 2842.1213 | 84.9917 | 229.5084 | 0 | 0 | 0 | 4178.0337 | 66.6353 | 250.8161 | 680.3742 | 54.2563 | 20.5379
|  | 382 | 2842.7918 | 85.0117 | 229.5625 | 0 | 0 | 0 | 3321.2467 | 52.9704 | 199.3814 | 680.3742 | 54.2563 | 20.5379
|  | 383 | 2843.4698 | 85.032 | 229.6173 | 0 | 0 | 0 | 2464.4523 | 39.3055 | 147.9462 | 0 | 0 | 0
|  | 384 | 2844.1552 | 85.0525 | 229.6726 | 0 | 0 | 0 | 1607.6504 | 25.6404 | 96.5106 | 0 | 0 | 0
|  | 385 | 2844.8481 | 85.0732 | 229.7286 | 0 | 0 | 0 | 65.9479 | 1.0518 | 3.959 | 0 | 0 | 0
|  | 386 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 387 | 2846.4029 | 85.1197 | 229.8541 | 0 | 0 | 0 | 64.393 | 1.027 | 3.8656 | 0 | 0 | 0
|  | 388 | 2847.1171 | 85.1411 | 229.9118 | 0 | 0 | 0 | 234.9021 | 3.7464 | 14.1017 | 0 | 0 | 0
|  | 389 | 2847.8386 | 85.1626 | 229.9701 | 0 | 0 | 0 | 602.9693 | 9.6167 | 36.1975 | 0 | 0 | 0
|  | 390 | 2848.5673 | 85.1844 | 230.0289 | 0 | 0 | 0 | 839.319 | 13.3863 | 50.3861 | 0 | 0 | 0
|  | 391 | 2849.3031 | 85.2064 | 230.0883 | 0 | 0 | 0 | 1075.6615 | 17.1557 | 64.5742 | 680.3742 | 54.2563 | 20.5379
|  | 392 | 2850.0462 | 85.2287 | 230.1483 | 0 | 0 | 0 | 1311.9969 | 20.925 | 78.7619 | 680.3742 | 54.2563 | 20.5379
|  | 393 | 2850.7963 | 85.2511 | 230.2089 | 0 | 0 | 0 | 1548.3252 | 24.6942 | 92.9492 | 0 | 0 | 0
|  | 394 | 2851.5535 | 85.2737 | 230.2701 | 0 | 0 | 0 | 1784.6464 | 28.4633 | 107.136 | 0 | 0 | 0
|  | 395 | 2852.3178 | 85.2966 | 230.3318 | 0 | 0 | 0 | 2020.9605 | 32.2322 | 121.3225 | 0 | 0 | 0
|  | 396 | 2853.089 | 85.3196 | 230.3941 | 0 | 0 | 0 | 2257.2677 | 36.0011 | 135.5085 | 0 | 0 | 0
|  | 397 | 2853.8672 | 85.3429 | 230.4569 | 0 | 0 | 0 | 2493.5679 | 39.7698 | 149.6941 | 0 | 0 | 0
|  | 398 | 2854.0351 | 85.3479 | 230.4705 | 0 | 0 | 0 | 2730.4784 | 43.5483 | 163.9163 | 0 | 0 | 0
|  | 399 | 2853.9468 | 85.3453 | 230.4633 | 0 | 0 | 0 | 2967.6451 | 47.3309 | 178.1539 | 0 | 0 | 0
|  | 400 | 2853.867 | 85.3429 | 230.4569 | 0 | 0 | 0 | 2796.5016 | 44.6013 | 167.8798 | 680.3742 | 54.2563 | 20.5379
|  | 401 | 2853.7957 | 85.3408 | 230.4511 | 0 | 0 | 0 | 3104.7748 | 49.5179 | 186.3861 | 680.3742 | 54.2563 | 20.5379
|  | 402 | 2853.7329 | 85.3389 | 230.4461 | 0 | 0 | 0 | 3413.0396 | 54.4344 | 204.8919 | 680.3742 | 54.2563 | 20.5379
|  | 403 | 2853.6784 | 85.3373 | 230.4417 | 0 | 0 | 0 | 3995.2533 | 63.7201 | 239.8434 | 680.3742 | 54.2563 | 20.5379
|  | 404 | 2853.6323 | 85.3359 | 230.4379 | 0 | 0 | 0 | 3995.2993 | 63.7209 | 239.8461 | 680.3742 | 54.2563 | 20.5379
|  | 405 | 2853.5946 | 85.3348 | 230.4349 | 0 | 0 | 0 | 4337.7837 | 69.1832 | 260.4062 | 680.3742 | 54.2563 | 20.5379
|  | 406 | 2853.5651 | 85.3339 | 230.4325 | 0 | 0 | 0 | 3447.452 | 54.9833 | 206.9577 | 680.3742 | 54.2563 | 20.5379
|  | 407 | 2853.5439 | 85.3333 | 230.4308 | 0 | 0 | 0 | 2557.1121 | 40.7833 | 153.5088 | 0 | 0 | 0
|  | 408 | 2853.5309 | 85.3329 | 230.4298 | 0 | 0 | 0 | 1666.764 | 26.5832 | 100.0593 | 0 | 0 | 0
|  | 409 | 2853.5261 | 85.3327 | 230.4294 | 0 | 0 | 0 | 57.2698 | 0.91339 | 3.438 | 0 | 0 | 0
|  | 410 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 411 | 2853.711 | 85.3382 | 230.4443 | 0 | 0 | 0 | 57.085 | 0.91045 | 3.4269 | 0 | 0 | 0
|  | 412 | 2853.7297 | 85.3388 | 230.4458 | 0 | 0 | 0 | 228.2895 | 3.641 | 13.7047 | 0 | 0 | 0
|  | 413 | 2853.7565 | 85.3396 | 230.448 | 0 | 0 | 0 | 570.7094 | 9.1022 | 34.2609 | 0 | 0 | 0
|  | 414 | 2853.7912 | 85.3406 | 230.4508 | 0 | 0 | 0 | 798.9723 | 12.7428 | 47.964 | 0 | 0 | 0
|  | 415 | 2853.8339 | 85.3419 | 230.4542 | 0 | 0 | 0 | 1027.2274 | 16.3832 | 61.6666 | 680.3742 | 54.2563 | 20.5379
|  | 416 | 2853.8846 | 85.3434 | 230.4583 | 0 | 0 | 0 | 1255.4744 | 20.0235 | 75.3687 | 680.3742 | 54.2563 | 20.5379
|  | 417 | 2853.9431 | 85.3452 | 230.463 | 0 | 0 | 0 | 1483.7137 | 23.6637 | 89.0704 | 680.3742 | 54.2563 | 20.5379
|  | 418 | 2854.0094 | 85.3472 | 230.4684 | 0 | 0 | 0 | 1711.945 | 27.3037 | 102.7716 | 680.3742 | 54.2563 | 20.5379
|  | 419 | 2854.0836 | 85.3494 | 230.4744 | 0 | 0 | 0 | 1940.1686 | 30.9437 | 116.4724 | 680.3742 | 54.2563 | 20.5379
|  | 420 | 2854.1656 | 85.3518 | 230.481 | 0 | 0 | 0 | 2168.3843 | 34.5835 | 130.1726 | 680.3742 | 54.2563 | 20.5379
|  | 421 | 2854.2553 | 85.3545 | 230.4882 | 0 | 0 | 0 | 2396.5924 | 38.2232 | 143.8724 | 680.3742 | 54.2563 | 20.5379
|  | 422 | 2854.3527 | 85.3574 | 230.4961 | 0 | 0 | 0 | 2624.7927 | 41.8627 | 157.5718 | 680.3742 | 54.2563 | 20.5379
|  | 423 | 2854.4577 | 85.3606 | 230.5046 | 0 | 0 | 0 | 2453.4643 | 39.1302 | 147.2866 | 680.3742 | 54.2563 | 20.5379
|  | 424 | 2854.5704 | 85.3639 | 230.5137 | 0 | 0 | 0 | 2852.8726 | 45.5004 | 171.2639 | 680.3742 | 54.2563 | 20.5379
|  | 425 | 2854.6907 | 85.3675 | 230.5234 | 0 | 0 | 0 | 3252.2734 | 51.8704 | 195.2407 | 680.3742 | 54.2563 | 20.5379
|  | 426 | 2854.8186 | 85.3714 | 230.5337 | 0 | 0 | 0 | 3651.6665 | 58.2403 | 219.2171 | 680.3742 | 54.2563 | 20.5379
|  | 427 | 2854.954 | 85.3754 | 230.5447 | 0 | 0 | 0 | 3180.6671 | 50.7283 | 190.9421 | 680.3742 | 54.2563 | 20.5379
|  | 428 | 2855.0968 | 85.3797 | 230.5562 | 0 | 0 | 0 | 2709.6602 | 43.2163 | 162.6665 | 680.3742 | 54.2563 | 20.5379
|  | 429 | 2855.2472 | 85.3842 | 230.5683 | 0 | 0 | 0 | 2238.6458 | 35.7041 | 134.3906 | 680.3742 | 54.2563 | 20.5379
|  | 430 | 2855.4049 | 85.3889 | 230.5811 | 0 | 0 | 0 | 1767.624 | 28.1918 | 106.1141 | 680.3742 | 54.2563 | 20.5379
|  | 431 | 2855.57 | 85.3938 | 230.5944 | 0 | 0 | 0 | 1296.5948 | 20.6793 | 77.8373 | 0 | 0 | 0
|  | 432 | 2855.7425 | 85.399 | 230.6083 | 0 | 0 | 0 | 568.7233 | 9.0705 | 34.1416 | 0 | 0 | 0
|  | 433 | 2855.9223 | 85.4044 | 230.6229 | 0 | 0 | 0 | 54.8737 | 0.87518 | 3.2942 | 0 | 0 | 0
|  | 434 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 435 | 2856.4816 | 85.4211 | 230.668 | 0 | 0 | 0 | 54.3144 | 0.86626 | 3.2606 | 0 | 0 | 0
|  | 436 | 2856.6823 | 85.4271 | 230.6842 | 0 | 0 | 0 | 225.337 | 3.5939 | 13.5274 | 0 | 0 | 0
|  | 437 | 2856.8902 | 85.4333 | 230.701 | 0 | 0 | 0 | 536.4442 | 8.5557 | 32.2039 | 0 | 0 | 0
|  | 438 | 2857.1052 | 85.4397 | 230.7184 | 0 | 0 | 0 | 754.1497 | 12.0279 | 45.2732 | 0 | 0 | 0
|  | 439 | 2857.3274 | 85.4464 | 230.7363 | 0 | 0 | 0 | 971.8481 | 15.5 | 58.3421 | 680.3742 | 54.2563 | 20.5379
|  | 440 | 2857.5566 | 85.4532 | 230.7548 | 0 | 0 | 0 | 1189.5394 | 18.9719 | 71.4105 | 680.3742 | 54.2563 | 20.5379
|  | 441 | 2857.7929 | 85.4603 | 230.7739 | 0 | 0 | 0 | 1407.2237 | 22.4438 | 84.4786 | 680.3742 | 54.2563 | 20.5379
|  | 442 | 2858.0361 | 85.4676 | 230.7936 | 0 | 0 | 0 | 1624.901 | 25.9155 | 97.5462 | 680.3742 | 54.2563 | 20.5379
|  | 443 | 2858.2864 | 85.4751 | 230.8138 | 0 | 0 | 0 | 1842.5712 | 29.3871 | 110.6134 | 680.3742 | 54.2563 | 20.5379
|  | 444 | 2858.5436 | 85.4828 | 230.8345 | 0 | 0 | 0 | 2060.2346 | 32.8586 | 123.6802 | 680.3742 | 54.2563 | 20.5379
|  | 445 | 2858.8077 | 85.4907 | 230.8559 | 0 | 0 | 0 | 2277.891 | 36.33 | 136.7465 | 680.3742 | 54.2563 | 20.5379
|  | 446 | 2859.0787 | 85.4988 | 230.8777 | 0 | 0 | 0 | 2179.7782 | 34.7652 | 130.8566 | 680.3742 | 54.2563 | 20.5379
|  | 447 | 2859.3565 | 85.5071 | 230.9002 | 0 | 0 | 0 | 2081.6585 | 33.2003 | 124.9663 | 680.3742 | 54.2563 | 20.5379
|  | 448 | 2859.6412 | 85.5156 | 230.9232 | 0 | 0 | 0 | 1983.532 | 31.6353 | 119.0756 | 680.3742 | 54.2563 | 20.5379
|  | 449 | 2859.9326 | 85.5243 | 230.9467 | 0 | 0 | 0 | 1885.3987 | 30.0702 | 113.1844 | 680.3742 | 54.2563 | 20.5379
|  | 450 | 2860.2307 | 85.5332 | 230.9708 | 0 | 0 | 0 | 1787.2586 | 28.5049 | 107.2929 | 680.3742 | 54.2563 | 20.5379
|  | 451 | 2860.5356 | 85.5423 | 230.9954 | 0 | 0 | 0 | 1689.1119 | 26.9396 | 101.4009 | 680.3742 | 54.2563 | 20.5379
|  | 452 | 2860.8471 | 85.5516 | 231.0206 | 0 | 0 | 0 | 1590.9585 | 25.3741 | 95.5085 | 680.3742 | 54.2563 | 20.5379
|  | 453 | 2861.1653 | 85.5612 | 231.0462 | 0 | 0 | 0 | 1933.0869 | 30.8307 | 116.0472 | 680.3742 | 54.2563 | 20.5379
|  | 454 | 2861.4901 | 85.5709 | 231.0725 | 0 | 0 | 0 | 1419.0922 | 22.633 | 85.1911 | 680.3742 | 54.2563 | 20.5379
|  | 455 | 2861.8215 | 85.5808 | 231.0992 | 0 | 0 | 0 | 905.0909 | 14.4353 | 54.3345 | 0 | 0 | 0
|  | 456 | 2862.1594 | 85.5909 | 231.1265 | 0 | 0 | 0 | 391.0831 | 6.2374 | 23.4775 | 0 | 0 | 0
|  | 457 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 458 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 459 | 2863.6082 | 85.6342 | 231.2435 | 0 | 0 | 0 | 71.6482 | 1.1427 | 4.3012 | 0 | 0 | 0
|  | 460 | 2863.9702 | 85.645 | 231.2727 | 0 | 0 | 0 | 266.97 | 4.2579 | 16.0268 | 0 | 0 | 0
|  | 461 | 2864.3386 | 85.6561 | 231.3025 | 0 | 0 | 0 | 462.2854 | 7.373 | 27.752 | 0 | 0 | 0
|  | 462 | 2864.7133 | 85.6673 | 231.3328 | 0 | 0 | 0 | 657.5944 | 10.4879 | 39.4768 | 0 | 0 | 0
|  | 463 | 2865.0944 | 85.6787 | 231.3635 | 0 | 0 | 0 | 852.8971 | 13.6028 | 51.2012 | 680.3742 | 54.2563 | 20.5379
|  | 464 | 2865.4817 | 85.6902 | 231.3948 | 0 | 0 | 0 | 1048.1935 | 16.7176 | 62.9252 | 680.3742 | 54.2563 | 20.5379
|  | 465 | 2865.8754 | 85.702 | 231.4266 | 0 | 0 | 0 | 1243.4836 | 19.8323 | 74.6489 | 0 | 0 | 0
|  | 466 | 2866.2752 | 85.714 | 231.4589 | 0 | 0 | 0 | 1438.7675 | 22.9469 | 86.3722 | 0 | 0 | 0
|  | 467 | 2866.6813 | 85.7261 | 231.4917 | 0 | 0 | 0 | 1634.0452 | 26.0613 | 98.0951 | 0 | 0 | 0
|  | 468 | 2867.0936 | 85.7384 | 231.525 | 0 | 0 | 0 | 1829.3167 | 29.1757 | 109.8177 | 0 | 0 | 0
|  | 469 | 2867.512 | 85.751 | 231.5588 | 0 | 0 | 0 | 1926.7402 | 30.7295 | 115.6662 | 0 | 0 | 0
|  | 470 | 2867.9365 | 85.7637 | 231.593 | 0 | 0 | 0 | 1926.3157 | 30.7227 | 115.6407 | 0 | 0 | 0
|  | 471 | 2868.3671 | 85.7765 | 231.6278 | 0 | 0 | 0 | 2415.0945 | 38.5183 | 144.9832 | 0 | 0 | 0
|  | 472 | 2868.8037 | 85.7896 | 231.6631 | 0 | 0 | 0 | 2610.3416 | 41.6322 | 156.7042 | 680.3742 | 54.2563 | 20.5379
|  | 473 | 2869.2464 | 85.8028 | 231.6988 | 0 | 0 | 0 | 2335.9417 | 37.2558 | 140.2314 | 680.3742 | 54.2563 | 20.5379
|  | 474 | 2869.695 | 85.8162 | 231.735 | 0 | 0 | 0 | 2061.5358 | 32.8794 | 123.7583 | 680.3742 | 54.2563 | 20.5379
|  | 475 | 2870.1496 | 85.8298 | 231.7718 | 0 | 0 | 0 | 1924.1025 | 30.6874 | 115.5079 | 680.3742 | 54.2563 | 20.5379
|  | 476 | 2870.6102 | 85.8436 | 231.8089 | 0 | 0 | 0 | 1512.7061 | 24.1261 | 90.8109 | 680.3742 | 54.2563 | 20.5379
|  | 477 | 2871.0766 | 85.8576 | 231.8466 | 0 | 0 | 0 | 1238.2824 | 19.7493 | 74.3367 | 680.3742 | 54.2563 | 20.5379
|  | 478 | 2871.549 | 85.8717 | 231.8848 | 0 | 0 | 0 | 963.8528 | 15.3725 | 57.8621 | 680.3742 | 54.2563 | 20.5379
|  | 479 | 2872.0271 | 85.886 | 231.9234 | 0 | 0 | 0 | 209.9921 | 3.3492 | 12.6063 | 0 | 0 | 0
|  | 480 | 2872.5111 | 85.9005 | 231.9624 | 0 | 0 | 0 | 38.2849 | 0.6106 | 2.2983 | 0 | 0 | 0
|  | 481 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 482 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 483 | 2874.531 | 85.9609 | 232.1256 | 0 | 0 | 0 | 36.2649 | 0.57839 | 2.1771 | 0 | 0 | 0
|  | 484 | 2875.0355 | 85.9759 | 232.1663 | 0 | 0 | 0 | 206.9838 | 3.3012 | 12.4257 | 0 | 0 | 0
|  | 485 | 2875.5456 | 85.9912 | 232.2075 | 0 | 0 | 0 | 377.6969 | 6.0239 | 22.6739 | 0 | 0 | 0
|  | 486 | 2876.0614 | 86.0066 | 232.2491 | 0 | 0 | 0 | 548.4045 | 8.7465 | 32.9219 | 0 | 0 | 0
|  | 487 | 2876.5828 | 86.0222 | 232.2912 | 0 | 0 | 0 | 719.1064 | 11.469 | 43.1695 | 680.3742 | 54.2563 | 20.5379
|  | 488 | 2877.1097 | 86.038 | 232.3338 | 0 | 0 | 0 | 889.8027 | 14.1914 | 53.4167 | 680.3742 | 54.2563 | 20.5379
|  | 489 | 2877.6423 | 86.0539 | 232.3768 | 0 | 0 | 0 | 1060.4934 | 16.9138 | 63.6636 | 0 | 0 | 0
|  | 490 | 2878.1803 | 86.07 | 232.4203 | 0 | 0 | 0 | 1231.1787 | 19.636 | 73.9102 | 0 | 0 | 0
|  | 491 | 2878.7239 | 86.0862 | 232.4641 | 0 | 0 | 0 | 1401.8584 | 22.3582 | 84.1565 | 0 | 0 | 0
|  | 492 | 2879.2729 | 86.1027 | 232.5085 | 0 | 0 | 0 | 1572.5327 | 25.0803 | 94.4024 | 0 | 0 | 0
|  | 493 | 2879.8273 | 86.1192 | 232.5533 | 0 | 0 | 0 | 1743.2015 | 27.8023 | 104.648 | 0 | 0 | 0
|  | 494 | 2880.3872 | 86.136 | 232.5985 | 0 | 0 | 0 | 1913.865 | 30.5242 | 114.8933 | 0 | 0 | 0
|  | 495 | 2880.9525 | 86.1529 | 232.6441 | 0 | 0 | 0 | 1742.0764 | 27.7843 | 104.5805 | 0 | 0 | 0
|  | 496 | 2881.5231 | 86.1699 | 232.6902 | 0 | 0 | 0 | 1912.7291 | 30.506 | 114.8251 | 680.3742 | 54.2563 | 20.5379
|  | 497 | 2882.099 | 86.1872 | 232.7367 | 0 | 0 | 0 | 2597.0463 | 41.4202 | 155.9061 | 680.3742 | 54.2563 | 20.5379
|  | 498 | 2882.6802 | 86.2046 | 232.7836 | 0 | 0 | 0 | 2425.2418 | 38.6801 | 145.5923 | 680.3742 | 54.2563 | 20.5379
|  | 499 | 2883.2667 | 86.2221 | 232.831 | 0 | 0 | 0 | 2767.1019 | 44.1324 | 166.1149 | 680.3742 | 54.2563 | 20.5379
|  | 500 | 2883.8585 | 86.2398 | 232.8788 | 0 | 0 | 0 | 2389.8189 | 38.1151 | 143.4658 | 680.3742 | 54.2563 | 20.5379
|  | 501 | 2884.4554 | 86.2576 | 232.927 | 0 | 0 | 0 | 2012.5307 | 32.0978 | 120.8164 | 680.3742 | 54.2563 | 20.5379
|  | 502 | 2885.0576 | 86.2756 | 232.9756 | 0 | 0 | 0 | 1635.2373 | 26.0803 | 98.1667 | 680.3742 | 54.2563 | 20.5379
|  | 503 | 2885.6649 | 86.2938 | 233.0246 | 0 | 0 | 0 | 1257.9388 | 20.0628 | 75.5167 | 0 | 0 | 0
|  | 504 | 2886.2773 | 86.3121 | 233.0741 | 0 | 0 | 0 | 880.6351 | 14.0452 | 52.8664 | 0 | 0 | 0
|  | 505 | 2886.8949 | 86.3306 | 233.124 | 0 | 0 | 0 | 23.9011 | 0.3812 | 1.4348 | 0 | 0 | 0
|  | 506 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 507 | 2888.432 | 86.3766 | 233.2481 | 0 | 0 | 0 | 22.3639 | 0.35668 | 1.3426 | 0 | 0 | 0
|  | 508 | 2889.0634 | 86.3954 | 233.2991 | 0 | 0 | 0 | 192.9558 | 3.0774 | 11.5835 | 0 | 0 | 0
|  | 509 | 2889.6998 | 86.4145 | 233.3505 | 0 | 0 | 0 | 620.3777 | 9.8944 | 37.2426 | 0 | 0 | 0
|  | 510 | 2890.3411 | 86.4336 | 233.4023 | 0 | 0 | 0 | 876.5713 | 13.9804 | 52.6224 | 0 | 0 | 0
|  | 511 | 2890.9874 | 86.453 | 233.4545 | 0 | 0 | 0 | 1132.7599 | 18.0663 | 68.0019 | 680.3742 | 54.2563 | 20.5379
|  | 512 | 2891.6386 | 86.4724 | 233.507 | 0 | 0 | 0 | 1388.9436 | 22.1522 | 83.3812 | 680.3742 | 54.2563 | 20.5379
|  | 513 | 2892.2948 | 86.4921 | 233.56 | 0 | 0 | 0 | 1645.1225 | 26.238 | 98.7601 | 0 | 0 | 0
|  | 514 | 2892.9557 | 86.5118 | 233.6134 | 0 | 0 | 0 | 1901.2964 | 30.3237 | 114.1388 | 0 | 0 | 0
|  | 515 | 2893.6216 | 86.5317 | 233.6672 | 0 | 0 | 0 | 2157.4656 | 34.4093 | 129.5172 | 0 | 0 | 0
|  | 516 | 2894.2922 | 86.5518 | 233.7213 | 0 | 0 | 0 | 2413.6299 | 38.4949 | 144.8952 | 0 | 0 | 0
|  | 517 | 2894.9676 | 86.572 | 233.7759 | 0 | 0 | 0 | 2669.7894 | 42.5804 | 160.273 | 0 | 0 | 0
|  | 518 | 2895.6478 | 86.5923 | 233.8308 | 0 | 0 | 0 | 2925.9441 | 46.6658 | 175.6505 | 0 | 0 | 0
|  | 519 | 2896.3327 | 86.6128 | 233.8861 | 0 | 0 | 0 | 2754.0359 | 43.924 | 165.3305 | 0 | 0 | 0
|  | 520 | 2897.0223 | 86.6334 | 233.9418 | 0 | 0 | 0 | 2981.644 | 47.5541 | 178.9943 | 680.3742 | 54.2563 | 20.5379
|  | 521 | 2897.7166 | 86.6542 | 233.9979 | 0 | 0 | 0 | 3779.9918 | 60.2869 | 226.9208 | 680.3742 | 54.2563 | 20.5379
|  | 522 | 2898.4156 | 86.6751 | 234.0543 | 0 | 0 | 0 | 3608.0695 | 57.545 | 216.5999 | 680.3742 | 54.2563 | 20.5379
|  | 523 | 2899.1192 | 86.6961 | 234.1111 | 0 | 0 | 0 | 3949.8125 | 62.9954 | 237.1155 | 680.3742 | 54.2563 | 20.5379
|  | 524 | 2899.8274 | 86.7173 | 234.1683 | 0 | 0 | 0 | 3606.6577 | 57.5225 | 216.5152 | 680.3742 | 54.2563 | 20.5379
|  | 525 | 2900.5402 | 86.7386 | 234.2259 | 0 | 0 | 0 | 4119.6148 | 65.7036 | 247.3091 | 680.3742 | 54.2563 | 20.5379
|  | 526 | 2901.2575 | 86.7601 | 234.2838 | 0 | 0 | 0 | 3262.781 | 52.038 | 195.8715 | 680.3742 | 54.2563 | 20.5379
|  | 527 | 2901.9794 | 86.7817 | 234.3421 | 0 | 0 | 0 | 2405.9427 | 38.3723 | 144.4338 | 0 | 0 | 0
|  | 528 | 2902.7057 | 86.8034 | 234.4007 | 0 | 0 | 0 | 1549.0999 | 24.7065 | 92.9957 | 0 | 0 | 0
|  | 529 | 2903.4366 | 86.8253 | 234.4598 | 0 | 0 | 0 | 7.3594 | 0.11737 | 0.4418 | 0 | 0 | 0
|  | 530 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 531 | 2905.2368 | 86.8791 | 234.6051 | 0 | 0 | 0 | 39.8038 | 0.63483 | 2.3895 | 0 | 0 | 0
|  | 532 | 2905.9795 | 86.9013 | 234.6651 | 0 | 0 | 0 | 176.0398 | 2.8077 | 10.568 | 0 | 0 | 0
|  | 533 | 2906.7265 | 86.9236 | 234.7254 | 0 | 0 | 0 | 493.2789 | 7.8673 | 29.6126 | 0 | 0 | 0
|  | 534 | 2907.4779 | 86.9461 | 234.7861 | 0 | 0 | 0 | 712.6717 | 11.3664 | 42.7832 | 0 | 0 | 0
|  | 535 | 2908.2336 | 86.9687 | 234.8471 | 0 | 0 | 0 | 932.0603 | 14.8654 | 55.9535 | 680.3742 | 54.2563 | 20.5379
|  | 536 | 2908.9936 | 86.9914 | 234.9085 | 0 | 0 | 0 | 1151.4445 | 18.3643 | 69.1236 | 680.3742 | 54.2563 | 20.5379
|  | 537 | 2909.7579 | 87.0143 | 234.9702 | 0 | 0 | 0 | 1370.8244 | 21.8632 | 82.2934 | 0 | 0 | 0
|  | 538 | 2910.5265 | 87.0373 | 235.0323 | 0 | 0 | 0 | 1590.2001 | 25.362 | 95.463 | 0 | 0 | 0
|  | 539 | 2911.2993 | 87.0604 | 235.0947 | 0 | 0 | 0 | 1809.5715 | 28.8608 | 108.6323 | 0 | 0 | 0
|  | 540 | 2912.0763 | 87.0836 | 235.1574 | 0 | 0 | 0 | 2028.9387 | 32.3595 | 121.8014 | 0 | 0 | 0
|  | 541 | 2912.8575 | 87.107 | 235.2205 | 0 | 0 | 0 | 2248.3017 | 35.8581 | 134.9702 | 0 | 0 | 0
|  | 542 | 2913.6429 | 87.1305 | 235.2839 | 0 | 0 | 0 | 2467.6606 | 39.3566 | 148.1388 | 0 | 0 | 0
|  | 543 | 2914.4324 | 87.1541 | 235.3477 | 0 | 0 | 0 | 2687.0153 | 42.8551 | 161.3071 | 0 | 0 | 0
|  | 544 | 2915.226 | 87.1778 | 235.4118 | 0 | 0 | 0 | 2906.3659 | 46.3535 | 174.4752 | 680.3742 | 54.2563 | 20.5379
|  | 545 | 2916.0237 | 87.2017 | 235.4762 | 0 | 0 | 0 | 2734.3449 | 43.61 | 164.1484 | 680.3742 | 54.2563 | 20.5379
|  | 546 | 2916.8255 | 87.2256 | 235.5409 | 0 | 0 | 0 | 3075.9897 | 49.0588 | 184.6581 | 680.3742 | 54.2563 | 20.5379
|  | 547 | 2917.6313 | 87.2497 | 235.606 | 0 | 0 | 0 | 3417.6305 | 54.5077 | 205.1675 | 680.3742 | 54.2563 | 20.5379
|  | 548 | 2918.4411 | 87.274 | 235.6714 | 0 | 0 | 0 | 3588.044 | 57.2256 | 215.3978 | 680.3742 | 54.2563 | 20.5379
|  | 549 | 2919.255 | 87.2983 | 235.7371 | 0 | 0 | 0 | 4100.9 | 65.4051 | 246.1856 | 680.3742 | 54.2563 | 20.5379
|  | 550 | 2920.0728 | 87.3228 | 235.8032 | 0 | 0 | 0 | 3243.9657 | 51.7379 | 194.742 | 680.3742 | 54.2563 | 20.5379
|  | 551 | 2920.8945 | 87.3473 | 235.8695 | 0 | 0 | 0 | 2387.0275 | 38.0706 | 143.2982 | 0 | 0 | 0
|  | 552 | 2921.7202 | 87.372 | 235.9362 | 0 | 0 | 0 | 1530.0854 | 24.4033 | 91.8542 | 0 | 0 | 0
|  | 553 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 554 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 555 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 556 | 2925.5021 | 87.4851 | 236.2416 | 0 | 0 | 0 | 156.5171 | 2.4963 | 9.396 | 0 | 0 | 0
|  | 557 | 2926.3451 | 87.5103 | 236.3097 | 0 | 0 | 0 | 524.4628 | 8.3646 | 31.4846 | 0 | 0 | 0
|  | 558 | 2927.1918 | 87.5356 | 236.3781 | 0 | 0 | 0 | 760.6945 | 12.1323 | 45.6661 | 0 | 0 | 0
|  | 559 | 2928.0423 | 87.5611 | 236.4467 | 0 | 0 | 0 | 996.9223 | 15.8999 | 59.8473 | 680.3742 | 54.2563 | 20.5379
|  | 560 | 2928.8966 | 87.5866 | 236.5157 | 0 | 0 | 0 | 1233.1465 | 19.6674 | 74.0284 | 680.3742 | 54.2563 | 20.5379
|  | 561 | 2929.7546 | 87.6123 | 236.585 | 0 | 0 | 0 | 1469.3669 | 23.4349 | 88.2092 | 0 | 0 | 0
|  | 562 | 2930.6163 | 87.638 | 236.6546 | 0 | 0 | 0 | 1705.5836 | 27.2023 | 102.3897 | 0 | 0 | 0
|  | 563 | 2931.4817 | 87.6639 | 236.7245 | 0 | 0 | 0 | 1941.7966 | 30.9696 | 116.5701 | 0 | 0 | 0
|  | 564 | 2932.3507 | 87.6899 | 236.7946 | 0 | 0 | 0 | 2178.006 | 34.7369 | 130.7502 | 0 | 0 | 0
|  | 565 | 2933.2234 | 87.716 | 236.8651 | 0 | 0 | 0 | 2414.2117 | 38.5042 | 144.9302 | 0 | 0 | 0
|  | 566 | 2934.0996 | 87.7422 | 236.9359 | 0 | 0 | 0 | 2650.4139 | 42.2714 | 159.1099 | 0 | 0 | 0
|  | 567 | 2934.9795 | 87.7685 | 237.0069 | 0 | 0 | 0 | 2886.6124 | 46.0385 | 173.2894 | 0 | 0 | 0
|  | 568 | 2935.863 | 87.7949 | 237.0783 | 0 | 0 | 0 | 2714.5056 | 43.2936 | 162.9574 | 680.3742 | 54.2563 | 20.5379
|  | 569 | 2936.75 | 87.8215 | 237.1499 | 0 | 0 | 0 | 3021.8206 | 48.1949 | 181.4062 | 680.3742 | 54.2563 | 20.5379
|  | 570 | 2937.6405 | 87.8481 | 237.2218 | 0 | 0 | 0 | 3329.132 | 53.0962 | 199.8547 | 680.3742 | 54.2563 | 20.5379
|  | 571 | 2938.5345 | 87.8748 | 237.294 | 0 | 0 | 0 | 3910.3971 | 62.3668 | 234.7493 | 680.3742 | 54.2563 | 20.5379
|  | 572 | 2939.432 | 87.9017 | 237.3665 | 0 | 0 | 0 | 3909.4996 | 62.3525 | 234.6954 | 680.3742 | 54.2563 | 20.5379
|  | 573 | 2940.333 | 87.9286 | 237.4392 | 0 | 0 | 0 | 4251.0452 | 67.7998 | 255.1991 | 680.3742 | 54.2563 | 20.5379
|  | 574 | 2941.2374 | 87.9557 | 237.5123 | 0 | 0 | 0 | 3359.7797 | 53.585 | 201.6946 | 680.3742 | 54.2563 | 20.5379
|  | 575 | 2942.1453 | 87.9828 | 237.5856 | 0 | 0 | 0 | 2468.5107 | 39.3702 | 148.1898 | 0 | 0 | 0
|  | 576 | 2943.0565 | 88.0101 | 237.6592 | 0 | 0 | 0 | 1577.2384 | 25.1553 | 94.6849 | 0 | 0 | 0
|  | 577 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 578 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 579 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 580 | 2947.2783 | 88.1363 | 238.0001 | 0 | 0 | 0 | 134.741 | 2.149 | 8.0888 | 0 | 0 | 0
|  | 581 | 2948.2037 | 88.164 | 238.0748 | 0 | 0 | 0 | 476.2622 | 7.5959 | 28.591 | 0 | 0 | 0
|  | 582 | 2949.1323 | 88.1918 | 238.1498 | 0 | 0 | 0 | 703.6312 | 11.2222 | 42.2404 | 0 | 0 | 0
|  | 583 | 2950.0643 | 88.2196 | 238.2251 | 0 | 0 | 0 | 930.997 | 14.8484 | 55.8897 | 680.3742 | 54.2563 | 20.5379
|  | 584 | 2950.9995 | 88.2476 | 238.3006 | 0 | 0 | 0 | 1158.3595 | 18.4746 | 69.5387 | 680.3742 | 54.2563 | 20.5379
|  | 585 | 2951.9378 | 88.2757 | 238.3764 | 0 | 0 | 0 | 1385.7189 | 22.1008 | 83.1876 | 680.3742 | 54.2563 | 20.5379
|  | 586 | 2952.8794 | 88.3038 | 238.4524 | 0 | 0 | 0 | 1613.075 | 25.7269 | 96.8363 | 680.3742 | 54.2563 | 20.5379
|  | 587 | 2953.8242 | 88.3321 | 238.5287 | 0 | 0 | 0 | 1840.428 | 29.3529 | 110.4847 | 680.3742 | 54.2563 | 20.5379
|  | 588 | 2954.7721 | 88.3604 | 238.6052 | 0 | 0 | 0 | 2067.7778 | 32.9789 | 124.133 | 680.3742 | 54.2563 | 20.5379
|  | 589 | 2955.7232 | 88.3889 | 238.682 | 0 | 0 | 0 | 2295.1245 | 36.6049 | 137.7811 | 680.3742 | 54.2563 | 20.5379
|  | 590 | 2956.6773 | 88.4174 | 238.7591 | 0 | 0 | 0 | 2522.468 | 40.2307 | 151.429 | 680.3742 | 54.2563 | 20.5379
|  | 591 | 2957.6346 | 88.446 | 238.8364 | 0 | 0 | 0 | 2350.2875 | 37.4846 | 141.0927 | 680.3742 | 54.2563 | 20.5379
|  | 592 | 2958.5949 | 88.4747 | 238.9139 | 0 | 0 | 0 | 2748.8482 | 43.8413 | 165.0191 | 680.3742 | 54.2563 | 20.5379
|  | 593 | 2959.5583 | 88.5035 | 238.9917 | 0 | 0 | 0 | 3147.4058 | 50.1979 | 188.9453 | 680.3742 | 54.2563 | 20.5379
|  | 594 | 2960.5247 | 88.5324 | 239.0698 | 0 | 0 | 0 | 3545.9604 | 56.5544 | 212.8714 | 680.3742 | 54.2563 | 20.5379
|  | 595 | 2961.4941 | 88.5614 | 239.148 | 0 | 0 | 0 | 3074.1269 | 49.0291 | 184.5462 | 680.3742 | 54.2563 | 20.5379
|  | 596 | 2962.4665 | 88.5905 | 239.2266 | 0 | 0 | 0 | 2602.2904 | 41.5038 | 156.2209 | 680.3742 | 54.2563 | 20.5379
|  | 597 | 2963.4419 | 88.6197 | 239.3053 | 0 | 0 | 0 | 2130.451 | 33.9785 | 127.8954 | 680.3742 | 54.2563 | 20.5379
|  | 598 | 2964.4203 | 88.6489 | 239.3843 | 0 | 0 | 0 | 1658.6086 | 26.4531 | 99.5697 | 680.3742 | 54.2563 | 20.5379
|  | 599 | 2965.4015 | 88.6783 | 239.4636 | 0 | 0 | 0 | 1186.7633 | 18.9276 | 71.2439 | 0 | 0 | 0
|  | 600 | 2966.3857 | 88.7077 | 239.5431 | 0 | 0 | 0 | 458.0801 | 7.3059 | 27.4995 | 0 | 0 | 0
|  | 601 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 602 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 603 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 604 | 2971.0212 | 88.8463 | 239.9174 | 0 | 0 | 0 | 110.998 | 1.7703 | 6.6634 | 0 | 0 | 0
|  | 605 | 2972.0166 | 88.8761 | 239.9978 | 0 | 0 | 0 | 421.3177 | 6.7196 | 25.2926 | 0 | 0 | 0
|  | 606 | 2973.0148 | 88.9059 | 240.0784 | 0 | 0 | 0 | 638.2401 | 10.1793 | 38.3149 | 0 | 0 | 0
|  | 607 | 2974.0158 | 88.9359 | 240.1592 | 0 | 0 | 0 | 855.1596 | 13.6389 | 51.337 | 680.3742 | 54.2563 | 20.5379
|  | 608 | 2975.0195 | 88.9659 | 240.2403 | 0 | 0 | 0 | 1072.0764 | 17.0985 | 64.359 | 680.3742 | 54.2563 | 20.5379
|  | 609 | 2976.026 | 88.996 | 240.3215 | 0 | 0 | 0 | 1288.9905 | 20.5581 | 77.3808 | 680.3742 | 54.2563 | 20.5379
|  | 610 | 2977.0353 | 89.0262 | 240.403 | 0 | 0 | 0 | 1505.9018 | 24.0176 | 90.4024 | 680.3742 | 54.2563 | 20.5379
|  | 611 | 2978.0472 | 89.0564 | 240.4848 | 0 | 0 | 0 | 1722.8104 | 27.477 | 103.4239 | 680.3742 | 54.2563 | 20.5379
|  | 612 | 2979.0618 | 89.0868 | 240.5667 | 0 | 0 | 0 | 1939.7163 | 30.9365 | 116.4452 | 680.3742 | 54.2563 | 20.5379
|  | 613 | 2980.0792 | 89.1172 | 240.6488 | 0 | 0 | 0 | 2156.6196 | 34.3958 | 129.4664 | 680.3742 | 54.2563 | 20.5379
|  | 614 | 2981.0991 | 89.1477 | 240.7312 | 0 | 0 | 0 | 2057.7577 | 32.8191 | 123.5315 | 680.3742 | 54.2563 | 20.5379
|  | 615 | 2982.1217 | 89.1783 | 240.8138 | 0 | 0 | 0 | 1958.8933 | 31.2423 | 117.5964 | 680.3742 | 54.2563 | 20.5379
|  | 616 | 2983.1469 | 89.2089 | 240.8966 | 0 | 0 | 0 | 1860.0262 | 29.6655 | 111.6612 | 680.3742 | 54.2563 | 20.5379
|  | 617 | 2984.1748 | 89.2397 | 240.9796 | 0 | 0 | 0 | 1761.1565 | 28.0886 | 105.7259 | 680.3742 | 54.2563 | 20.5379
|  | 618 | 2985.2052 | 89.2705 | 241.0628 | 0 | 0 | 0 | 1662.2842 | 26.5117 | 99.7904 | 680.3742 | 54.2563 | 20.5379
|  | 619 | 2986.2381 | 89.3014 | 241.1462 | 0 | 0 | 0 | 1563.4093 | 24.9348 | 93.8547 | 680.3742 | 54.2563 | 20.5379
|  | 620 | 2987.2736 | 89.3323 | 241.2298 | 0 | 0 | 0 | 1464.5319 | 23.3578 | 87.9189 | 680.3742 | 54.2563 | 20.5379
|  | 621 | 2988.3117 | 89.3634 | 241.3136 | 0 | 0 | 0 | 1805.9405 | 28.8029 | 108.4144 | 680.3742 | 54.2563 | 20.5379
|  | 622 | 2989.3522 | 89.3945 | 241.3977 | 0 | 0 | 0 | 1291.2301 | 20.5938 | 77.5152 | 680.3742 | 54.2563 | 20.5379
|  | 623 | 2990.3953 | 89.4257 | 241.4819 | 0 | 0 | 0 | 776.5172 | 12.3846 | 46.6159 | 0 | 0 | 0
|  | 624 | 2991.4408 | 89.457 | 241.5663 | 0 | 0 | 0 | 261.8018 | 4.1755 | 15.7165 | 0 | 0 | 0
|  | 625 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 626 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 627 | 2935.2564 | 87.7768 | 237.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 628 | 2996.7227 | 89.6149 | 241.9928 | 0 | 0 | 0 | 134.2175 | 2.1406 | 8.0574 | 0 | 0 | 0
|  | 629 | 2997.7753 | 89.6464 | 242.0778 | 0 | 0 | 0 | 328.8486 | 5.2448 | 19.7415 | 0 | 0 | 0
|  | 630 | 2998.8304 | 89.6779 | 242.163 | 0 | 0 | 0 | 523.4774 | 8.3489 | 31.4254 | 0 | 0 | 0
|  | 631 | 2999.8878 | 89.7096 | 242.2484 | 0 | 0 | 0 | 718.1037 | 11.453 | 43.1093 | 680.3742 | 54.2563 | 20.5379
|  | 632 | 3000.9475 | 89.7413 | 242.334 | 0 | 0 | 0 | 912.7277 | 14.5571 | 54.7929 | 680.3742 | 54.2563 | 20.5379
|  | 633 | 3002.0096 | 89.773 | 242.4198 | 0 | 0 | 0 | 1107.3494 | 17.6611 | 66.4765 | 0 | 0 | 0
|  | 634 | 3003.074 | 89.8048 | 242.5057 | 0 | 0 | 0 | 1301.9688 | 20.7651 | 78.1599 | 0 | 0 | 0
|  | 635 | 3004.1406 | 89.8367 | 242.5919 | 0 | 0 | 0 | 1496.5859 | 23.869 | 89.8432 | 0 | 0 | 0
|  | 636 | 3005.2096 | 89.8687 | 242.6782 | 0 | 0 | 0 | 1691.2007 | 26.9729 | 101.5263 | 0 | 0 | 0
|  | 637 | 3006.2808 | 89.9007 | 242.7647 | 0 | 0 | 0 | 1787.9713 | 28.5163 | 107.3356 | 0 | 0 | 0
|  | 638 | 3007.3543 | 89.9328 | 242.8514 | 0 | 0 | 0 | 1786.8979 | 28.4992 | 107.2712 | 0 | 0 | 0
|  | 639 | 3008.43 | 89.965 | 242.9382 | 0 | 0 | 0 | 2275.0316 | 36.2844 | 136.5749 | 0 | 0 | 0
|  | 640 | 3009.5079 | 89.9972 | 243.0253 | 0 | 0 | 0 | 2469.6375 | 39.3882 | 148.2575 | 680.3742 | 54.2563 | 20.5379
|  | 641 | 3010.588 | 90.0295 | 243.1125 | 0 | 0 | 0 | 2194.6001 | 35.0016 | 131.7464 | 680.3742 | 54.2563 | 20.5379
|  | 642 | 3011.6702 | 90.0619 | 243.1999 | 0 | 0 | 0 | 1919.5606 | 30.615 | 115.2352 | 680.3742 | 54.2563 | 20.5379
|  | 643 | 3012.7546 | 90.0943 | 243.2875 | 0 | 0 | 0 | 1781.4975 | 28.413 | 106.947 | 680.3742 | 54.2563 | 20.5379
|  | 644 | 3013.8412 | 90.1268 | 243.3752 | 0 | 0 | 0 | 1369.4751 | 21.8417 | 82.2124 | 680.3742 | 54.2563 | 20.5379
|  | 645 | 3014.9299 | 90.1594 | 243.4631 | 0 | 0 | 0 | 1094.4291 | 17.455 | 65.7009 | 680.3742 | 54.2563 | 20.5379
|  | 646 | 3016.0207 | 90.192 | 243.5512 | 0 | 0 | 0 | 819.3811 | 13.0683 | 49.1892 | 680.3742 | 54.2563 | 20.5379
|  | 647 | 3017.1136 | 90.2247 | 243.6395 | 0 | 0 | 0 | 64.9057 | 1.0352 | 3.8964 | 0 | 0 | 0
|  | 648 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 649 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 650 | 2739.5727 | 81.925 | 221.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 651 | 2910.796 | 87.0453 | 235.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 652 | 3024.2608 | 90.4384 | 244.2166 | 0 | 0 | 0 | 57.7584 | 0.92119 | 3.4674 | 0 | 0 | 0
|  | 653 | 3025.3583 | 90.4712 | 244.3052 | 0 | 0 | 0 | 227.8842 | 3.6345 | 13.6804 | 0 | 0 | 0
|  | 654 | 3026.4578 | 90.5041 | 244.394 | 0 | 0 | 0 | 398.008 | 6.3478 | 23.8933 | 0 | 0 | 0
|  | 655 | 3027.5593 | 90.5371 | 244.483 | 0 | 0 | 0 | 568.1299 | 9.0611 | 34.106 | 680.3742 | 54.2563 | 20.5379
|  | 656 | 3028.6627 | 90.5701 | 244.5721 | 0 | 0 | 0 | 738.2497 | 11.7743 | 44.3187 | 680.3742 | 54.2563 | 20.5379
|  | 657 | 3029.7681 | 90.6031 | 244.6613 | 0 | 0 | 0 | 908.3676 | 14.4875 | 54.5312 | 0 | 0 | 0
|  | 658 | 3030.8754 | 90.6362 | 244.7508 | 0 | 0 | 0 | 1078.4836 | 17.2007 | 64.7436 | 0 | 0 | 0
|  | 659 | 3031.9847 | 90.6694 | 244.8403 | 0 | 0 | 0 | 1248.5976 | 19.9138 | 74.9559 | 0 | 0 | 0
|  | 660 | 3033.0959 | 90.7026 | 244.9301 | 0 | 0 | 0 | 1418.7097 | 22.6269 | 85.1681 | 0 | 0 | 0
|  | 661 | 3034.2089 | 90.7359 | 245.02 | 0 | 0 | 0 | 1588.82 | 25.34 | 95.3802 | 0 | 0 | 0
|  | 662 | 3035.3238 | 90.7693 | 245.11 | 0 | 0 | 0 | 1758.9283 | 28.0531 | 105.5921 | 0 | 0 | 0
|  | 663 | 3036.4406 | 90.8027 | 245.2002 | 0 | 0 | 0 | 1586.5882 | 25.3044 | 95.2462 | 0 | 0 | 0
|  | 664 | 3037.5593 | 90.8361 | 245.2905 | 0 | 0 | 0 | 1756.6929 | 28.0174 | 105.4579 | 680.3742 | 54.2563 | 20.5379
|  | 665 | 3038.6797 | 90.8696 | 245.381 | 0 | 0 | 0 | 2440.4656 | 38.9229 | 146.5062 | 680.3742 | 54.2563 | 20.5379
|  | 666 | 3039.802 | 90.9032 | 245.4716 | 0 | 0 | 0 | 2268.12 | 36.1742 | 136.16 | 680.3742 | 54.2563 | 20.5379
|  | 667 | 3040.9261 | 90.9368 | 245.5624 | 0 | 0 | 0 | 2609.4426 | 41.6179 | 156.6503 | 680.3742 | 54.2563 | 20.5379
|  | 668 | 3042.0519 | 90.9705 | 245.6533 | 0 | 0 | 0 | 2231.6255 | 35.5921 | 133.9691 | 680.3742 | 54.2563 | 20.5379
|  | 669 | 3043.7086 | 91.02 | 245.7871 | 0 | 0 | 0 | 1853.2775 | 29.5579 | 111.2561 | 680.3742 | 54.2563 | 20.5379
|  | 670 | 3045.7185 | 91.0801 | 245.9494 | 0 | 0 | 0 | 1474.5764 | 23.518 | 88.5219 | 680.3742 | 54.2563 | 20.5379
|  | 671 | 3047.7284 | 91.1402 | 246.1117 | 0 | 0 | 0 | 1095.8752 | 17.4781 | 65.7877 | 0 | 0 | 0
|  | 672 | 3049.7384 | 91.2003 | 246.274 | 0 | 0 | 0 | 717.174 | 11.4382 | 43.0534 | 0 | 0 | 0
|  | Total | 1999013.7215 |  | 161425.3519 | 0 |  | 0 | 1028260.9548 |  | 61728.6467 | 209555.2669 |  | 6325.6778
Note on C8: Peter North: (Sat-Toutlet = 2 to 5K) Condenser refrig sat temp (30ºC) minus 2ºC approach temp. Needs to be written-up and justified. Sat temp - outlet temp btw 2 to 5K. 2K taken to max deltaT and min mass flowrate.
Note on C9: Peter North: (Toutlet - sat = 5K) Evaporator refrig sat temp (5ºC) plus 5K or 2K approach temp. Needs to be written-up and justified.