## Dashboard
| Hot Sink |  | Cold Sink
| Qcond, hot | Edes cond, hot | Qcond, cold | Edes cond, cold
| kWh | kWh | kWh | kWh
Winter | 2286226.9586 | 184618.5382 | 339293.6997 | 21976.8216
Spring/autumn | 2182261.1703 | 176223.0411 | 640290.5163 | 41473.0674
Summer | 1999013.7215 | 161425.3519 | 1028260.9548 | 66602.7916
<1946 | 1946 to 1980 | 1980 to 2000 | Post 2000
37.8 | 39.7 | 15.6 | 6.9 | 100
| 77.5 | 93.1 | 100

## Winter
[13 empty] | ºC | K
T0 | K | 273 | [9 empty] | T2/T1 | 1.4 | 0.97342
cp water | kJ/kg.K | 4.18 | [9 empty] | LN | 0.33647 | -0.026938
Tcond.sat | ºC | 30 | [9 empty] | T0 | 91.8569 | -7.354
T evap.sat | ºC | 5 | [9 empty] | T2-T1 | 8 | -8
Thot sink | ºC | 20 | 293 | K | [9 empty] | -0.64602
Tcold sink | ºC | 10 | 283 | K | Approach Temp | [7 empty] | 0 | 0
Tcond.hot, out | ºC | 28 | 301 | K | 2 | K
Thp.hot, out | ºC | 10 | 283 | K | 5 | K
Tcond.cold, out | ºC | 28 | 301 | K | 5 | K
Thp.cold, out | ºC | 7 | 280 | K | 2 | K
Winter
|  |  | Hot Sink | [5 empty] | Cold Sink
|  |  | Condenser |  |  | HP Evaporator |  |  | Condenser |  |  | HP Evaporator |  |  | total Ex dest
|  |  | Qcond, hot | ṁcond, hot | Edest cond, hot | Qhp, hot | ṁhp, hot | Edest hp, hot | Qcond, cold | ṁcond, cold | Edest cond, cold | Qhp, cold | ṁhp, cold | Edest hp, hot
|  |  | kW | kg/s | kW | kW | kg/s | kW | kW | kg/s | kW | kW | kg/s | kW
|  | Total | 2286226.9586 |  | 184618.5382 |  |  |  | 339293.6997 |  | 21976.8216 | 0 |  | 0 | 206595.3599
|  | Hours |  |  |  | 8.075% | [5 empty] | 6.477%
| 31.5563 | 1 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 2 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 3 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 4 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 5 | 3044.25 |  | 245.8308 |  |  |  | 0 |  | 0
|  | 6 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 7 | 3489.75 |  | 281.806 |  |  |  | 0 |  | 0
|  | 8 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 9 | 3732.6611 |  | 301.4217 |  |  |  | 202.5889 |  | 13.1221
|  | 10 | 3726.13 |  | 300.8943 |  |  |  | 431.87 |  | 27.9732
|  | 11 | 3719.6339 |  | 300.3697 |  |  |  | 661.1161 |  | 42.822
|  | 12 | 3713.1725 |  | 299.848 |  |  |  | 890.3275 |  | 57.6685
|  | 13 | 3706.7458 |  | 299.329 |  |  |  | 1119.5042 |  | 72.5128
|  | 14 | 3700.3537 |  | 298.8128 |  |  |  | 1348.6463 |  | 87.3549
|  | 15 | 3693.9961 |  | 298.2994 |  |  |  | 1206.5039 |  | 78.148
|  | 16 | 3693.5554 |  | 298.2638 |  |  |  | 1404.9446 |  | 91.0014
|  | 17 | 3701.1356 |  | 298.8759 |  |  |  | 2090.3644 |  | 135.3976
|  | 18 | 3708.6838 |  | 299.4855 |  |  |  | 1934.3162 |  | 125.29
|  | 19 | 3716.1999 |  | 300.0924 |  |  |  | 2223.8001 |  | 144.0406
|  | 20 | 3723.6835 |  | 300.6967 |  |  |  | 1919.3165 |  | 124.3185
|  | 21 | 3731.135 |  | 301.2985 |  |  |  | 2357.365 |  | 152.6919
|  | 22 | 3738.5542 |  | 301.8976 |  |  |  | 1607.4458 |  | 104.1179
|  | 23 | 3737.9181 |  | 301.8462 |  |  |  | 865.5819 |  | 56.0657
|  | 24 | 3731.4337 |  | 301.3226 |  |  |  | 129.5663 |  | 8.3923
|  | 25 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 26 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 27 | 2554.2 |  | 206.258 |  |  |  | 0 |  | 0
|  | 28 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 29 | 2948.7857 |  | 238.1218 |  |  |  | 0 |  | 0
|  | 30 | 3139.7143 |  | 253.5398 |  |  |  | 0 |  | 0
|  | 31 | 3330.6429 |  | 268.9577 |  |  |  | 0 |  | 0
|  | 32 | 3521.5714 |  | 284.3757 |  |  |  | 0 |  | 0
|  | 33 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 34 | 3708.2572 |  | 299.451 |  |  |  | 195.1714 |  | 12.6417
|  | 35 | 3701.9642 |  | 298.9429 |  |  |  | 392.3929 |  | 25.4162
|  | 36 | 3695.7053 |  | 298.4374 |  |  |  | 589.5804 |  | 38.1885
|  | 37 | 3689.4802 |  | 297.9347 |  |  |  | 786.7341 |  | 50.9586
|  | 38 | 3682.936 |  | 297.4063 |  |  |  | 984.2068 |  | 63.7493
|  | 39 | 3675.8975 |  | 296.8379 |  |  |  | 1182.1739 |  | 76.5721
|  | 40 | 3674.7605 |  | 296.7461 |  |  |  | 1374.2395 |  | 89.0126
|  | 41 | 3681.6431 |  | 297.3019 |  |  |  | 1218.8569 |  | 78.9481
|  | 42 | 3688.4966 |  | 297.8553 |  |  |  | 1509.0034 |  | 97.7416
|  | 43 | 3695.3205 |  | 298.4064 |  |  |  | 1799.1795 |  | 116.5369
|  | 44 | 3702.114 |  | 298.955 |  |  |  | 1940.886 |  | 125.7156
|  | 45 | 3708.8766 |  | 299.5011 |  |  |  | 2379.6234 |  | 154.1336
|  | 46 | 3715.6078 |  | 300.0446 |  |  |  | 1630.3922 |  | 105.6042
|  | 47 | 3714.2866 |  | 299.9379 |  |  |  | 889.2134 |  | 57.5964
|  | 48 | 3707.1295 |  | 299.36 |  |  |  | 153.8705 |  | 9.9665
|  | 49 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 50 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 51 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 52 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 53 | 2992.8462 |  | 241.6798 |  |  |  | 0 |  | 0
|  | 54 | 3198.4615 |  | 258.2838 |  |  |  | 0 |  | 0
|  | 55 | 3404.0769 |  | 274.8877 |  |  |  | 0 |  | 0
|  | 56 | 3609.6923 |  | 291.4917 |  |  |  | 0 |  | 0
|  | 57 | 3683.1396 |  | 297.4227 |  |  |  | 132.1681 |  | 8.5608
|  | 58 | 3676.1537 |  | 296.8586 |  |  |  | 344.7693 |  | 22.3315
|  | 59 | 3669.2028 |  | 296.2973 |  |  |  | 557.3357 |  | 36.0999
|  | 60 | 3662.2867 |  | 295.7388 |  |  |  | 769.8672 |  | 49.866
|  | 61 | 3655.4053 |  | 295.1831 |  |  |  | 982.3639 |  | 63.6299
|  | 62 | 3648.5585 |  | 294.6302 |  |  |  | 1194.8261 |  | 77.3916
|  | 63 | 3641.7462 |  | 294.0801 |  |  |  | 1407.2538 |  | 91.151
|  | 64 | 3640.8211 |  | 294.0054 |  |  |  | 1259.6789 |  | 81.5923
|  | 65 | 3647.9123 |  | 294.578 |  |  |  | 1519.8877 |  | 98.4466
|  | 66 | 3654.9732 |  | 295.1482 |  |  |  | 1780.1268 |  | 115.3028
|  | 67 | 3662.0028 |  | 295.7159 |  |  |  | 2277.9972 |  | 147.551
|  | 68 | 3669.0002 |  | 296.2809 |  |  |  | 2270.9998 |  | 147.0978
|  | 69 | 3675.9651 |  | 296.8434 |  |  |  | 2561.0349 |  | 165.884
|  | 70 | 3682.8976 |  | 297.4032 |  |  |  | 1781.9024 |  | 115.4179
|  | 71 | 3681.7798 |  | 297.3129 |  |  |  | 1010.8202 |  | 65.4731
|  | 72 | 3674.8423 |  | 296.7527 |  |  |  | 245.5577 |  | 15.9053
|  | 73 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 74 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 75 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 76 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 77 | 2970 |  | 239.8349 |  |  |  | 0 |  | 0
|  | 78 | 3168 |  | 255.8239 |  |  |  | 0 |  | 0
|  | 79 | 3366 |  | 271.8129 |  |  |  | 0 |  | 0
|  | 80 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 81 | 3660.4576 |  | 295.5911 |  |  |  | 101.5424 |  | 6.5771
|  | 82 | 3667.5166 |  | 296.1611 |  |  |  | 292.4834 |  | 18.9448
|  | 83 | 3674.5505 |  | 296.7291 |  |  |  | 483.4495 |  | 31.3141
|  | 84 | 3681.5587 |  | 297.2951 |  |  |  | 674.4413 |  | 43.6851
|  | 85 | 3688.8938 |  | 297.8874 |  |  |  | 865.1062 |  | 56.0349
|  | 86 | 3696.7305 |  | 298.5202 |  |  |  | 1055.2695 |  | 68.3522
|  | 87 | 3704.5388 |  | 299.1508 |  |  |  | 898.9612 |  | 58.2278
|  | 88 | 3712.3191 |  | 299.779 |  |  |  | 1237.6809 |  | 80.1674
|  | 89 | 3720.0706 |  | 300.405 |  |  |  | 1576.4294 |  | 102.1089
|  | 90 | 3727.7926 |  | 301.0286 |  |  |  | 1915.2074 |  | 124.0523
|  | 91 | 3735.4846 |  | 301.6497 |  |  |  | 1499.1404 |  | 97.1027
|  | 92 | 3743.1476 |  | 302.2685 |  |  |  | 1083.1024 |  | 70.155
|  | 93 | 3750.7831 |  | 302.8851 |  |  |  | 667.0919 |  | 43.2091
|  | 94 | 3758.3924 |  | 303.4996 |  |  |  | 251.1076 |  | 16.2648
|  | 95 | 3601.125 |  | 290.7998 |  |  |  | 0 |  | 0
|  | 96 | 2970 |  | 239.8349 |  |  |  | 0 |  | 0
|  | 97 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 98 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 99 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 100 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 101 | 2943 |  | 237.6546 |  |  |  | 0 |  | 0
|  | 102 | 3132 |  | 252.9168 |  |  |  | 0 |  | 0
|  | 103 | 3321 |  | 268.179 |  |  |  | 0 |  | 0
|  | 104 | 3510 |  | 283.4413 |  |  |  | 0 |  | 0
|  | 105 | 3699 |  | 298.7035 |  |  |  | 0 |  | 0
|  | 106 | 3754.8469 |  | 303.2133 |  |  |  | 133.1531 |  | 8.6246
|  | 107 | 3762.5496 |  | 303.8353 |  |  |  | 314.4504 |  | 20.3677
|  | 108 | 3770.226 |  | 304.4552 |  |  |  | 495.774 |  | 32.1124
|  | 109 | 3777.8758 |  | 305.0729 |  |  |  | 677.1242 |  | 43.8589
|  | 110 | 3785.4984 |  | 305.6885 |  |  |  | 584.6445 |  | 37.8687
|  | 111 | 3793.094 |  | 306.3018 |  |  |  | 492.1917 |  | 31.8804
|  | 112 | 3800.3983 |  | 306.8917 |  |  |  | 400.0302 |  | 25.9109
|  | 113 | 3805.2969 |  | 307.2872 |  |  |  | 310.2745 |  | 20.0972
|  | 114 | 3810.1744 |  | 307.6811 |  |  |  | 220.5398 |  | 14.2849
|  | 115 | 3815.0311 |  | 308.0733 |  |  |  | 130.826 |  | 8.4739
|  | 116 | 3819.8673 |  | 308.4638 |  |  |  | 41.1327 |  | 2.6643
|  | 117 | 3824.6831 |  | 308.8527 |  |  |  | 333.3169 |  | 21.5897
|  | 118 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 119 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 120 | 2821.5 |  | 227.8432 |  |  |  | 0 |  | 0
|  | 121 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 122 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 123 | 2545.7143 |  | 205.5728 |  |  |  | 0 |  | 0
|  | 124 | 2715.4286 |  | 219.2776 |  |  |  | 0 |  | 0
|  | 125 | 2885.1429 |  | 232.9825 |  |  |  | 0 |  | 0
|  | 126 | 3054.8571 |  | 246.6873 |  |  |  | 0 |  | 0
|  | 127 | 3224.5714 |  | 260.3922 |  |  |  | 0 |  | 0
|  | 128 | 3394.2857 |  | 274.0971 |  |  |  | 0 |  | 0
|  | 129 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 130 | 3733.7143 |  | 301.5068 |  |  |  | 0 |  | 0
|  | 131 | 3764.8271 |  | 304.0192 |  |  |  | 138.6014 |  | 8.9775
|  | 132 | 3755.2519 |  | 303.246 |  |  |  | 317.8909 |  | 20.5905
|  | 133 | 3745.4524 |  | 302.4546 |  |  |  | 412.5476 |  | 26.7216
|  | 134 | 3735.6931 |  | 301.6666 |  |  |  | 422.3069 |  | 27.3538
|  | 135 | 3725.974 |  | 300.8817 |  |  |  | 856.3117 |  | 55.4652
|  | 136 | 3725.0993 |  | 300.8111 |  |  |  | 1026.9007 |  | 66.5147
|  | 137 | 3732.9701 |  | 301.4467 |  |  |  | 781.4299 |  | 50.615
|  | 138 | 3740.811 |  | 302.0798 |  |  |  | 535.989 |  | 34.7172
|  | 139 | 3748.6226 |  | 302.7106 |  |  |  | 409.3774 |  | 26.5163
|  | 140 | 3756.4056 |  | 303.3391 |  |  |  | 45.1944 |  | 2.9273
|  | 141 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 142 | 3326.4 |  | 268.6151 |  |  |  | 0 |  | 0
|  | 143 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 144 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 145 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 146 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 147 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 148 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 149 | 2821.5 |  | 227.8432 |  |  |  | 0 |  | 0
|  | 150 | 2970 |  | 239.8349 |  |  |  | 0 |  | 0
|  | 151 | 3118.5 |  | 251.8267 |  |  |  | 0 |  | 0
|  | 152 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 153 | 3415.5 |  | 275.8102 |  |  |  | 0 |  | 0
|  | 154 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 155 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 156 | 3742.1908 |  | 302.1913 |  |  |  | 118.8092 |  | 7.6955
|  | 157 | 3736.0623 |  | 301.6964 |  |  |  | 273.4377 |  | 17.7112
|  | 158 | 3729.9669 |  | 301.2041 |  |  |  | 428.0331 |  | 27.7247
|  | 159 | 3723.9043 |  | 300.7146 |  |  |  | 285.5957 |  | 18.4987
|  | 160 | 3723.8709 |  | 300.7119 |  |  |  | 434.1291 |  | 28.1195
|  | 161 | 3731.8788 |  | 301.3585 |  |  |  | 1020.1212 |  | 66.0756
|  | 162 | 3739.8544 |  | 302.0026 |  |  |  | 863.6456 |  | 55.9403
|  | 163 | 3747.7975 |  | 302.644 |  |  |  | 1152.7025 |  | 74.6632
|  | 164 | 3755.7079 |  | 303.2828 |  |  |  | 818.0921 |  | 52.9897
|  | 165 | 3763.0571 |  | 303.8763 |  |  |  | 484.0429 |  | 31.3526
|  | 166 | 3768.2611 |  | 304.2965 |  |  |  | 152.1389 |  | 9.8544
|  | 167 | 3593.7 |  | 290.2003 |  |  |  | 0 |  | 0
|  | 168 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 169 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 170 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 171 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 172 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 173 | 3044.25 |  | 245.8308 |  |  |  | 0 |  | 0
|  | 174 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 175 | 3489.75 |  | 281.806 |  |  |  | 0 |  | 0
|  | 176 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 177 | 3726.0637 |  | 300.8889 |  |  |  | 209.1863 |  | 13.5495
|  | 178 | 3719.161 |  | 300.3315 |  |  |  | 438.839 |  | 28.4246
|  | 179 | 3712.2927 |  | 299.7769 |  |  |  | 668.4573 |  | 43.2975
|  | 180 | 3705.4586 |  | 299.225 |  |  |  | 898.0414 |  | 58.1682
|  | 181 | 3698.6585 |  | 298.6759 |  |  |  | 1127.5915 |  | 73.0367
|  | 182 | 3691.8924 |  | 298.1295 |  |  |  | 1357.1076 |  | 87.9029
|  | 183 | 3685.1601 |  | 297.5859 |  |  |  | 1215.3399 |  | 78.7203
|  | 184 | 3684.425 |  | 297.5265 |  |  |  | 1414.075 |  | 91.5928
|  | 185 | 3691.7222 |  | 298.1158 |  |  |  | 2099.7778 |  | 136.0074
|  | 186 | 3698.9837 |  | 298.7022 |  |  |  | 1944.0163 |  | 125.9183
|  | 187 | 3706.2094 |  | 299.2857 |  |  |  | 2233.7906 |  | 144.6877
|  | 188 | 3713.399 |  | 299.8662 |  |  |  | 1929.601 |  | 124.9846
|  | 189 | 3720.5528 |  | 300.4439 |  |  |  | 2367.9472 |  | 153.3773
|  | 190 | 3728.1115 |  | 301.0543 |  |  |  | 1617.8885 |  | 104.7943
|  | 191 | 3728.0397 |  | 301.0485 |  |  |  | 875.4603 |  | 56.7055
|  | 192 | 3722.0514 |  | 300.5649 |  |  |  | 138.9486 |  | 9
|  | 193 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 194 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 195 | 2554.2 |  | 206.258 |  |  |  | 0 |  | 0
|  | 196 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 197 | 2948.7857 |  | 238.1218 |  |  |  | 0 |  | 0
|  | 198 | 3139.7143 |  | 253.5398 |  |  |  | 0 |  | 0
|  | 199 | 3330.6429 |  | 268.9577 |  |  |  | 0 |  | 0
|  | 200 | 3521.5714 |  | 284.3757 |  |  |  | 0 |  | 0
|  | 201 | 3709.5604 |  | 299.5563 |  |  |  | 2.9396 |  | 0.19041
|  | 202 | 3703.7076 |  | 299.0836 |  |  |  | 199.721 |  | 12.9364
|  | 203 | 3697.8868 |  | 298.6136 |  |  |  | 396.4703 |  | 25.6803
|  | 204 | 3692.0979 |  | 298.1461 |  |  |  | 593.1878 |  | 38.4221
|  | 205 | 3686.3407 |  | 297.6812 |  |  |  | 789.8736 |  | 51.1619
|  | 206 | 3679.7336 |  | 297.1477 |  |  |  | 987.4093 |  | 63.9567
|  | 207 | 3673.1597 |  | 296.6168 |  |  |  | 1184.9118 |  | 76.7494
|  | 208 | 3672.504 |  | 296.5639 |  |  |  | 1376.496 |  | 89.1588
|  | 209 | 3679.8662 |  | 297.1584 |  |  |  | 1220.6338 |  | 79.0632
|  | 210 | 3687.1939 |  | 297.7501 |  |  |  | 1510.3061 |  | 97.8259
|  | 211 | 3694.4867 |  | 298.339 |  |  |  | 1800.0133 |  | 116.5909
|  | 212 | 3701.7441 |  | 298.9251 |  |  |  | 1941.2559 |  | 125.7395
|  | 213 | 3708.9655 |  | 299.5082 |  |  |  | 2379.5345 |  | 154.1278
|  | 214 | 3716.1508 |  | 300.0885 |  |  |  | 1629.8492 |  | 105.569
|  | 215 | 3715.2787 |  | 300.018 |  |  |  | 888.2213 |  | 57.5321
|  | 216 | 3708.5671 |  | 299.4761 |  |  |  | 152.4329 |  | 9.8734
|  | 217 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 218 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 219 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 220 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 221 | 2992.8462 |  | 241.6798 |  |  |  | 0 |  | 0
|  | 222 | 3198.4615 |  | 258.2838 |  |  |  | 0 |  | 0
|  | 223 | 3404.0769 |  | 274.8877 |  |  |  | 0 |  | 0
|  | 224 | 3609.6923 |  | 291.4917 |  |  |  | 0 |  | 0
|  | 225 | 3688.507 |  | 297.8562 |  |  |  | 126.8007 |  | 8.2132
|  | 226 | 3681.9463 |  | 297.3264 |  |  |  | 338.9768 |  | 21.9563
|  | 227 | 3675.4185 |  | 296.7992 |  |  |  | 551.1199 |  | 35.6973
|  | 228 | 3668.9236 |  | 296.2747 |  |  |  | 763.2302 |  | 49.4361
|  | 229 | 3662.4615 |  | 295.7529 |  |  |  | 975.3077 |  | 63.1729
|  | 230 | 3656.032 |  | 295.2337 |  |  |  | 1187.3526 |  | 76.9075
|  | 231 | 3649.635 |  | 294.7171 |  |  |  | 1399.365 |  | 90.64
|  | 232 | 3649.8039 |  | 294.7308 |  |  |  | 1250.6961 |  | 81.0104
|  | 233 | 3658.1569 |  | 295.4053 |  |  |  | 1509.6431 |  | 97.783
|  | 234 | 3666.4753 |  | 296.077 |  |  |  | 1768.6247 |  | 114.5578
|  | 235 | 3674.7582 |  | 296.7459 |  |  |  | 2265.2418 |  | 146.7248
|  | 236 | 3683.0049 |  | 297.4118 |  |  |  | 2256.9951 |  | 146.1907
|  | 237 | 3691.2151 |  | 298.0748 |  |  |  | 2545.7849 |  | 164.8963
|  | 238 | 3699.3889 |  | 298.7349 |  |  |  | 1765.4111 |  | 114.3497
|  | 239 | 3699.5133 |  | 298.7449 |  |  |  | 993.0867 |  | 64.3245
|  | 240 | 3693.8434 |  | 298.2871 |  |  |  | 226.5566 |  | 14.6746
|  | 241 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 242 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 243 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 244 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 245 | 2970 |  | 239.8349 |  |  |  | 0 |  | 0
|  | 246 | 3168 |  | 255.8239 |  |  |  | 0 |  | 0
|  | 247 | 3366 |  | 271.8129 |  |  |  | 0 |  | 0
|  | 248 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 249 | 3691.0515 |  | 298.0616 |  |  |  | 70.9485 |  | 4.5955
|  | 250 | 3699.3004 |  | 298.7277 |  |  |  | 260.6996 |  | 16.8861
|  | 251 | 3707.5203 |  | 299.3915 |  |  |  | 450.4797 |  | 29.1786
|  | 252 | 3715.7108 |  | 300.0529 |  |  |  | 640.2892 |  | 41.473
|  | 253 | 3723.8716 |  | 300.7119 |  |  |  | 830.1284 |  | 53.7693
|  | 254 | 3732.0022 |  | 301.3685 |  |  |  | 1019.9978 |  | 66.0676
|  | 255 | 3740.1024 |  | 302.0226 |  |  |  | 863.3976 |  | 55.9242
|  | 256 | 3748.1725 |  | 302.6743 |  |  |  | 1201.8275 |  | 77.8451
|  | 257 | 3756.2119 |  | 303.3235 |  |  |  | 1540.2881 |  | 99.768
|  | 258 | 3763.6903 |  | 303.9274 |  |  |  | 1879.3097 |  | 121.7271
|  | 259 | 3769.0225 |  | 304.358 |  |  |  | 1465.6025 |  | 94.9304
|  | 260 | 3774.3288 |  | 304.7865 |  |  |  | 1051.9212 |  | 68.1353
|  | 261 | 3779.6105 |  | 305.213 |  |  |  | 638.2645 |  | 41.3418
|  | 262 | 3784.8691 |  | 305.6376 |  |  |  | 224.6309 |  | 14.5499
|  | 263 | 3601.125 |  | 290.7998 |  |  |  | 0 |  | 0
|  | 264 | 2970 |  | 239.8349 |  |  |  | 0 |  | 0
|  | 265 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 266 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 267 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 268 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 269 | 2943 |  | 237.6546 |  |  |  | 0 |  | 0
|  | 270 | 3132 |  | 252.9168 |  |  |  | 0 |  | 0
|  | 271 | 3321 |  | 268.179 |  |  |  | 0 |  | 0
|  | 272 | 3510 |  | 283.4413 |  |  |  | 0 |  | 0
|  | 273 | 3699 |  | 298.7035 |  |  |  | 0 |  | 0
|  | 274 | 3754.0298 |  | 303.1473 |  |  |  | 133.9702 |  | 8.6776
|  | 275 | 3759.4294 |  | 303.5833 |  |  |  | 317.5706 |  | 20.5698
|  | 276 | 3764.8074 |  | 304.0176 |  |  |  | 501.1926 |  | 32.4634
|  | 277 | 3770.1632 |  | 304.4501 |  |  |  | 684.8368 |  | 44.3584
|  | 278 | 3775.4964 |  | 304.8808 |  |  |  | 594.6464 |  | 38.5166
|  | 279 | 3780.8072 |  | 305.3096 |  |  |  | 504.4785 |  | 32.6762
|  | 280 | 3786.0958 |  | 305.7367 |  |  |  | 414.3328 |  | 26.8373
|  | 281 | 3791.3625 |  | 306.162 |  |  |  | 324.2089 |  | 20.9997
|  | 282 | 3796.6077 |  | 306.5856 |  |  |  | 234.1066 |  | 15.1636
|  | 283 | 3801.8316 |  | 307.0074 |  |  |  | 144.0256 |  | 9.3289
|  | 284 | 3807.0344 |  | 307.4275 |  |  |  | 53.9656 |  | 3.4955
|  | 285 | 3812.2163 |  | 307.846 |  |  |  | 345.7837 |  | 22.3972
|  | 286 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 287 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 288 | 2821.5 |  | 227.8432 |  |  |  | 0 |  | 0
|  | 289 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 290 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 291 | 2545.7143 |  | 205.5728 |  |  |  | 0 |  | 0
|  | 292 | 2715.4286 |  | 219.2776 |  |  |  | 0 |  | 0
|  | 293 | 2885.1429 |  | 232.9825 |  |  |  | 0 |  | 0
|  | 294 | 3054.8571 |  | 246.6873 |  |  |  | 0 |  | 0
|  | 295 | 3224.5714 |  | 260.3922 |  |  |  | 0 |  | 0
|  | 296 | 3394.2857 |  | 274.0971 |  |  |  | 0 |  | 0
|  | 297 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 298 | 3733.7143 |  | 301.5068 |  |  |  | 0 |  | 0
|  | 299 | 3756.8349 |  | 303.3738 |  |  |  | 146.5937 |  | 9.4952
|  | 300 | 3747.3692 |  | 302.6094 |  |  |  | 325.7737 |  | 21.1011
|  | 301 | 3737.9422 |  | 301.8482 |  |  |  | 420.0578 |  | 27.2081
|  | 302 | 3728.5538 |  | 301.09 |  |  |  | 429.4462 |  | 27.8162
|  | 303 | 3720.7913 |  | 300.4632 |  |  |  | 861.4944 |  | 55.8009
|  | 304 | 3720.0967 |  | 300.4071 |  |  |  | 1031.9033 |  | 66.8387
|  | 305 | 3727.4413 |  | 301.0002 |  |  |  | 786.9587 |  | 50.9731
|  | 306 | 3734.7572 |  | 301.591 |  |  |  | 542.0428 |  | 35.1093
|  | 307 | 3742.045 |  | 302.1795 |  |  |  | 415.955 |  | 26.9423
|  | 308 | 3749.3054 |  | 302.7658 |  |  |  | 52.2946 |  | 3.3872
|  | 309 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 310 | 3326.4 |  | 268.6151 |  |  |  | 0 |  | 0
|  | 311 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 312 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 313 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 314 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 315 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 316 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 317 | 2821.5 |  | 227.8432 |  |  |  | 0 |  | 0
|  | 318 | 2970 |  | 239.8349 |  |  |  | 0 |  | 0
|  | 319 | 3118.5 |  | 251.8267 |  |  |  | 0 |  | 0
|  | 320 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 321 | 3415.5 |  | 275.8102 |  |  |  | 0 |  | 0
|  | 322 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 323 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 324 | 3712.857 |  | 299.8225 |  |  |  | 148.143 |  | 9.5956
|  | 325 | 3706.24 |  | 299.2881 |  |  |  | 303.26 |  | 19.6428
|  | 326 | 3699.656 |  | 298.7565 |  |  |  | 458.344 |  | 29.688
|  | 327 | 3693.1051 |  | 298.2275 |  |  |  | 316.3949 |  | 20.4936
|  | 328 | 3692.5981 |  | 298.1865 |  |  |  | 465.4019 |  | 30.1451
|  | 329 | 3700.136 |  | 298.7952 |  |  |  | 1051.864 |  | 68.1316
|  | 330 | 3707.6425 |  | 299.4014 |  |  |  | 895.8575 |  | 58.0267
|  | 331 | 3715.1176 |  | 300.005 |  |  |  | 1185.3824 |  | 76.7799
|  | 332 | 3722.5609 |  | 300.6061 |  |  |  | 851.2391 |  | 55.1367
|  | 333 | 3729.9732 |  | 301.2047 |  |  |  | 517.1268 |  | 33.4955
|  | 334 | 3737.3555 |  | 301.8008 |  |  |  | 183.0445 |  | 11.8562
|  | 335 | 3593.7 |  | 290.2003 |  |  |  | 0 |  | 0
|  | 336 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 337 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 338 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 339 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 340 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 341 | 3044.25 |  | 245.8308 |  |  |  | 0 |  | 0
|  | 342 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 343 | 3489.75 |  | 281.806 |  |  |  | 0 |  | 0
|  | 344 | 3712.2687 |  | 299.775 |  |  |  | 0.23128 |  | 0.014981
|  | 345 | 3711.7157 |  | 299.7303 |  |  |  | 223.5343 |  | 14.4788
|  | 346 | 3705.1602 |  | 299.2009 |  |  |  | 452.8398 |  | 29.3315
|  | 347 | 3698.6375 |  | 298.6742 |  |  |  | 682.1125 |  | 44.182
|  | 348 | 3692.1475 |  | 298.1501 |  |  |  | 911.3525 |  | 59.0304
|  | 349 | 3685.6901 |  | 297.6287 |  |  |  | 1140.5599 |  | 73.8766
|  | 350 | 3679.2651 |  | 297.1099 |  |  |  | 1369.7349 |  | 88.7208
|  | 351 | 3672.8725 |  | 296.5936 |  |  |  | 1227.6275 |  | 79.5162
|  | 352 | 3672.5112 |  | 296.5645 |  |  |  | 1425.9888 |  | 92.3645
|  | 353 | 3680.188 |  | 297.1844 |  |  |  | 2111.312 |  | 136.7545
|  | 354 | 3687.8284 |  | 297.8014 |  |  |  | 1955.1716 |  | 126.6409
|  | 355 | 3695.4321 |  | 298.4154 |  |  |  | 2244.5679 |  | 145.3857
|  | 356 | 3702.9991 |  | 299.0264 |  |  |  | 1940.0009 |  | 125.6583
|  | 357 | 3710.5295 |  | 299.6345 |  |  |  | 2377.9705 |  | 154.0265
|  | 358 | 3718.0231 |  | 300.2397 |  |  |  | 1627.9769 |  | 105.4478
|  | 359 | 3717.4387 |  | 300.1925 |  |  |  | 886.0613 |  | 57.3922
|  | 360 | 3710.8963 |  | 299.6641 |  |  |  | 150.1037 |  | 9.7226
|  | 361 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 362 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 363 | 2554.2 |  | 206.258 |  |  |  | 0 |  | 0
|  | 364 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 365 | 2948.7857 |  | 238.1218 |  |  |  | 0 |  | 0
|  | 366 | 3139.7143 |  | 253.5398 |  |  |  | 0 |  | 0
|  | 367 | 3330.6429 |  | 268.9577 |  |  |  | 0 |  | 0
|  | 368 | 3521.5714 |  | 284.3757 |  |  |  | 0 |  | 0
|  | 369 | 3693.3152 |  | 298.2444 |  |  |  | 19.1848 |  | 1.2426
|  | 370 | 3686.9114 |  | 297.7273 |  |  |  | 216.5172 |  | 14.0243
|  | 371 | 3680.5397 |  | 297.2128 |  |  |  | 413.8174 |  | 26.8039
|  | 372 | 3674.2002 |  | 296.7008 |  |  |  | 611.0855 |  | 39.5814
|  | 373 | 3667.8927 |  | 296.1915 |  |  |  | 808.3216 |  | 52.3568
|  | 374 | 3661.617 |  | 295.6847 |  |  |  | 1005.5258 |  | 65.1302
|  | 375 | 3655.3732 |  | 295.1805 |  |  |  | 1202.6983 |  | 77.9015
|  | 376 | 3655.1005 |  | 295.1585 |  |  |  | 1393.8995 |  | 90.286
|  | 377 | 3662.8542 |  | 295.7846 |  |  |  | 1237.6458 |  | 80.1651
|  | 378 | 3670.572 |  | 296.4079 |  |  |  | 1526.928 |  | 98.9026
|  | 379 | 3678.2533 |  | 297.0281 |  |  |  | 1816.2467 |  | 117.6424
|  | 380 | 3685.8975 |  | 297.6454 |  |  |  | 1957.1025 |  | 126.766
|  | 381 | 3693.5038 |  | 298.2597 |  |  |  | 2394.9962 |  | 155.1293
|  | 382 | 3701.0719 |  | 298.8708 |  |  |  | 1644.9281 |  | 106.5457
|  | 383 | 3700.5712 |  | 298.8304 |  |  |  | 902.9288 |  | 58.4847
|  | 384 | 3694.1749 |  | 298.3139 |  |  |  | 166.8251 |  | 10.8056
|  | 385 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 386 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 387 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 388 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 389 | 2992.8462 |  | 241.6798 |  |  |  | 0 |  | 0
|  | 390 | 3198.4615 |  | 258.2838 |  |  |  | 0 |  | 0
|  | 391 | 3404.0769 |  | 274.8877 |  |  |  | 0 |  | 0
|  | 392 | 3609.6923 |  | 291.4917 |  |  |  | 0 |  | 0
|  | 393 | 3676.7973 |  | 296.9106 |  |  |  | 138.5103 |  | 8.9716
|  | 394 | 3670.5391 |  | 296.4052 |  |  |  | 350.384 |  | 22.6952
|  | 395 | 3664.3124 |  | 295.9024 |  |  |  | 562.226 |  | 36.4167
|  | 396 | 3658.1173 |  | 295.4021 |  |  |  | 774.0365 |  | 50.1361
|  | 397 | 3651.9537 |  | 294.9044 |  |  |  | 985.8156 |  | 63.8535
|  | 398 | 3645.8213 |  | 294.4092 |  |  |  | 1197.5633 |  | 77.5689
|  | 399 | 3639.7202 |  | 293.9165 |  |  |  | 1409.2798 |  | 91.2822
|  | 400 | 3639.5078 |  | 293.8993 |  |  |  | 1260.9922 |  | 81.6773
|  | 401 | 3647.3058 |  | 294.5291 |  |  |  | 1520.4942 |  | 98.4859
|  | 402 | 3655.0661 |  | 295.1557 |  |  |  | 1780.0339 |  | 115.2968
|  | 403 | 3662.7881 |  | 295.7793 |  |  |  | 2277.2119 |  | 147.5002
|  | 404 | 3670.4709 |  | 296.3997 |  |  |  | 2269.5291 |  | 147.0025
|  | 405 | 3678.1144 |  | 297.0169 |  |  |  | 2558.8856 |  | 165.7448
|  | 406 | 3685.7187 |  | 297.631 |  |  |  | 1779.0813 |  | 115.2351
|  | 407 | 3685.9745 |  | 297.6516 |  |  |  | 1006.6255 |  | 65.2014
|  | 408 | 3680.5997 |  | 297.2176 |  |  |  | 239.8003 |  | 15.5324
|  | 409 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 410 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 411 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 412 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 413 | 2970 |  | 239.8349 |  |  |  | 0 |  | 0
|  | 414 | 3168 |  | 255.8239 |  |  |  | 0 |  | 0
|  | 415 | 3366 |  | 271.8129 |  |  |  | 0 |  | 0
|  | 416 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 417 | 3680.1414 |  | 297.1806 |  |  |  | 81.8586 |  | 5.3022
|  | 418 | 3688.6536 |  | 297.868 |  |  |  | 271.3464 |  | 17.5757
|  | 419 | 3697.1326 |  | 298.5527 |  |  |  | 460.8674 |  | 29.8514
|  | 420 | 3705.5781 |  | 299.2347 |  |  |  | 650.4219 |  | 42.1293
|  | 421 | 3713.9897 |  | 299.9139 |  |  |  | 840.0103 |  | 54.4094
|  | 422 | 3722.3671 |  | 300.5904 |  |  |  | 1029.6329 |  | 66.6917
|  | 423 | 3730.7099 |  | 301.2641 |  |  |  | 872.7901 |  | 56.5326
|  | 424 | 3739.0186 |  | 301.9351 |  |  |  | 1210.9814 |  | 78.438
|  | 425 | 3747.2925 |  | 302.6032 |  |  |  | 1549.2075 |  | 100.3457
|  | 426 | 3755.5308 |  | 303.2685 |  |  |  | 1887.4692 |  | 122.2557
|  | 427 | 3763.4684 |  | 303.9095 |  |  |  | 1471.1566 |  | 95.2901
|  | 428 | 3768.9918 |  | 304.3555 |  |  |  | 1057.2582 |  | 68.481
|  | 429 | 3774.4867 |  | 304.7992 |  |  |  | 643.3883 |  | 41.6737
|  | 430 | 3779.9546 |  | 305.2408 |  |  |  | 229.5454 |  | 14.8682
|  | 431 | 3601.125 |  | 290.7998 |  |  |  | 0 |  | 0
|  | 432 | 2970 |  | 239.8349 |  |  |  | 0 |  | 0
|  | 433 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 434 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 435 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 436 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 437 | 2943 |  | 237.6546 |  |  |  | 0 |  | 0
|  | 438 | 3132 |  | 252.9168 |  |  |  | 0 |  | 0
|  | 439 | 3321 |  | 268.179 |  |  |  | 0 |  | 0
|  | 440 | 3510 |  | 283.4413 |  |  |  | 0 |  | 0
|  | 441 | 3699 |  | 298.7035 |  |  |  | 0 |  | 0
|  | 442 | 3751.7524 |  | 302.9634 |  |  |  | 136.2476 |  | 8.8251
|  | 443 | 3757.3109 |  | 303.4122 |  |  |  | 319.6891 |  | 20.707
|  | 444 | 3762.8446 |  | 303.8591 |  |  |  | 503.1554 |  | 32.5905
|  | 445 | 3768.3532 |  | 304.3039 |  |  |  | 686.6468 |  | 44.4757
|  | 446 | 3773.8363 |  | 304.7467 |  |  |  | 596.3065 |  | 38.6241
|  | 447 | 3779.2944 |  | 305.1875 |  |  |  | 505.9913 |  | 32.7742
|  | 448 | 3784.7278 |  | 305.6262 |  |  |  | 415.7008 |  | 26.9259
|  | 449 | 3790.1371 |  | 306.063 |  |  |  | 325.4344 |  | 21.0791
|  | 450 | 3795.5226 |  | 306.4979 |  |  |  | 235.1917 |  | 15.2339
|  | 451 | 3800.8848 |  | 306.9309 |  |  |  | 144.9724 |  | 9.3902
|  | 452 | 3806.2241 |  | 307.3621 |  |  |  | 54.7759 |  | 3.548
|  | 453 | 3811.5409 |  | 307.7914 |  |  |  | 346.4591 |  | 22.4409
|  | 454 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 455 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 456 | 2821.5 |  | 227.8432 |  |  |  | 0 |  | 0
|  | 457 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 458 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 459 | 2545.7143 |  | 205.5728 |  |  |  | 0 |  | 0
|  | 460 | 2715.4286 |  | 219.2776 |  |  |  | 0 |  | 0
|  | 461 | 2885.1429 |  | 232.9825 |  |  |  | 0 |  | 0
|  | 462 | 3054.8571 |  | 246.6873 |  |  |  | 0 |  | 0
|  | 463 | 3224.5714 |  | 260.3922 |  |  |  | 0 |  | 0
|  | 464 | 3394.2857 |  | 274.0971 |  |  |  | 0 |  | 0
|  | 465 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 466 | 3733.7143 |  | 301.5068 |  |  |  | 0 |  | 0
|  | 467 | 3759.1954 |  | 303.5644 |  |  |  | 144.2331 |  | 9.3423
|  | 468 | 3749.962 |  | 302.8188 |  |  |  | 323.1808 |  | 20.9332
|  | 469 | 3740.7663 |  | 302.0762 |  |  |  | 417.2337 |  | 27.0252
|  | 470 | 3731.6081 |  | 301.3367 |  |  |  | 426.3919 |  | 27.6184
|  | 471 | 3723.2812 |  | 300.6643 |  |  |  | 859.0045 |  | 55.6397
|  | 472 | 3722.7273 |  | 300.6195 |  |  |  | 1029.2727 |  | 66.6683
|  | 473 | 3730.1976 |  | 301.2228 |  |  |  | 784.2024 |  | 50.7946
|  | 474 | 3737.6402 |  | 301.8238 |  |  |  | 539.1598 |  | 34.9226
|  | 475 | 3745.056 |  | 302.4226 |  |  |  | 412.944 |  | 26.7473
|  | 476 | 3752.4455 |  | 303.0193 |  |  |  | 49.1545 |  | 3.1838
|  | 477 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 478 | 3326.4 |  | 268.6151 |  |  |  | 0 |  | 0
|  | 479 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 480 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 481 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 482 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 483 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 484 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 485 | 2821.5 |  | 227.8432 |  |  |  | 0 |  | 0
|  | 486 | 2970 |  | 239.8349 |  |  |  | 0 |  | 0
|  | 487 | 3118.5 |  | 251.8267 |  |  |  | 0 |  | 0
|  | 488 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 489 | 3415.5 |  | 275.8102 |  |  |  | 0 |  | 0
|  | 490 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 491 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 492 | 3722.3563 |  | 300.5896 |  |  |  | 138.6437 |  | 8.9803
|  | 493 | 3716.8262 |  | 300.143 |  |  |  | 292.6738 |  | 18.9571
|  | 494 | 3711.3265 |  | 299.6989 |  |  |  | 446.6735 |  | 28.9321
|  | 495 | 3705.857 |  | 299.2572 |  |  |  | 303.643 |  | 19.6676
|  | 496 | 3706.3757 |  | 299.2991 |  |  |  | 451.6243 |  | 29.2527
|  | 497 | 3714.9289 |  | 299.9898 |  |  |  | 1037.0711 |  | 67.1734
|  | 498 | 3723.4502 |  | 300.6779 |  |  |  | 880.0498 |  | 57.0028
|  | 499 | 3731.9396 |  | 301.3634 |  |  |  | 1168.5604 |  | 75.6903
|  | 500 | 3740.3968 |  | 302.0464 |  |  |  | 833.4032 |  | 53.9814
|  | 501 | 3748.8225 |  | 302.7268 |  |  |  | 498.2775 |  | 32.2746
|  | 502 | 3757.2178 |  | 303.4047 |  |  |  | 163.1822 |  | 10.5697
|  | 503 | 3593.7 |  | 290.2003 |  |  |  | 0 |  | 0
|  | 504 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 505 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 506 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 507 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 508 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 509 | 3044.25 |  | 245.8308 |  |  |  | 0 |  | 0
|  | 510 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 511 | 3489.75 |  | 281.806 |  |  |  | 0 |  | 0
|  | 512 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 513 | 3743.526 |  | 302.2991 |  |  |  | 191.724 |  | 12.4184
|  | 514 | 3738.0022 |  | 301.853 |  |  |  | 419.9978 |  | 27.2042
|  | 515 | 3732.5087 |  | 301.4094 |  |  |  | 648.2413 |  | 41.9881
|  | 516 | 3727.0453 |  | 300.9682 |  |  |  | 876.4547 |  | 56.77
|  | 517 | 3721.612 |  | 300.5295 |  |  |  | 1104.638 |  | 71.5499
|  | 518 | 3716.2085 |  | 300.0931 |  |  |  | 1332.7915 |  | 86.3279
|  | 519 | 3710.8349 |  | 299.6592 |  |  |  | 1189.6651 |  | 77.0573
|  | 520 | 3711.4752 |  | 299.7109 |  |  |  | 1387.0248 |  | 89.8407
|  | 521 | 3720.1502 |  | 300.4114 |  |  |  | 2071.3498 |  | 134.166
|  | 522 | 3728.7884 |  | 301.109 |  |  |  | 1914.2116 |  | 123.9878
|  | 523 | 3737.3895 |  | 301.8035 |  |  |  | 2202.6105 |  | 142.6681
|  | 524 | 3745.9533 |  | 302.4951 |  |  |  | 1897.0467 |  | 122.876
|  | 525 | 3754.4801 |  | 303.1836 |  |  |  | 2334.0199 |  | 151.1798
|  | 526 | 3762.9697 |  | 303.8692 |  |  |  | 1583.0303 |  | 102.5365
|  | 527 | 3760.7366 |  | 303.6889 |  |  |  | 842.7634 |  | 54.5877
|  | 528 | 3752.5513 |  | 303.0279 |  |  |  | 108.4487 |  | 7.0245
|  | 529 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 530 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 531 | 2554.2 |  | 206.258 |  |  |  | 0 |  | 0
|  | 532 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 533 | 2948.7857 |  | 238.1218 |  |  |  | 0 |  | 0
|  | 534 | 3139.7143 |  | 253.5398 |  |  |  | 0 |  | 0
|  | 535 | 3330.6429 |  | 268.9577 |  |  |  | 0 |  | 0
|  | 536 | 3521.5714 |  | 284.3757 |  |  |  | 0 |  | 0
|  | 537 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 538 | 3722.1511 |  | 300.573 |  |  |  | 181.2775 |  | 11.7418
|  | 539 | 3715.9065 |  | 300.0687 |  |  |  | 378.4507 |  | 24.5131
|  | 540 | 3709.6932 |  | 299.567 |  |  |  | 575.5925 |  | 37.2824
|  | 541 | 3703.5111 |  | 299.0678 |  |  |  | 772.7032 |  | 50.0497
|  | 542 | 3697.3601 |  | 298.5711 |  |  |  | 969.7828 |  | 62.815
|  | 543 | 3691.2401 |  | 298.0769 |  |  |  | 1166.8313 |  | 75.5783
|  | 544 | 3691.1147 |  | 298.0667 |  |  |  | 1357.8853 |  | 87.9533
|  | 545 | 3699.0209 |  | 298.7052 |  |  |  | 1201.4791 |  | 77.8225
|  | 546 | 3706.8921 |  | 299.3408 |  |  |  | 1490.6079 |  | 96.5501
|  | 547 | 3714.7278 |  | 299.9736 |  |  |  | 1779.7722 |  | 115.2799
|  | 548 | 3722.5273 |  | 300.6034 |  |  |  | 1920.4727 |  | 124.3934
|  | 549 | 3730.2899 |  | 301.2302 |  |  |  | 2358.2101 |  | 152.7466
|  | 550 | 3738.0151 |  | 301.8541 |  |  |  | 1607.9849 |  | 104.1528
|  | 551 | 3737.6664 |  | 301.8259 |  |  |  | 865.8336 |  | 56.082
|  | 552 | 3731.3857 |  | 301.3187 |  |  |  | 129.6143 |  | 8.3954
|  | 553 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 554 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 555 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 556 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 557 | 2992.8462 |  | 241.6798 |  |  |  | 0 |  | 0
|  | 558 | 3198.4615 |  | 258.2838 |  |  |  | 0 |  | 0
|  | 559 | 3404.0769 |  | 274.8877 |  |  |  | 0 |  | 0
|  | 560 | 3609.6923 |  | 291.4917 |  |  |  | 0 |  | 0
|  | 561 | 3715.8668 |  | 300.0655 |  |  |  | 99.4409 |  | 6.441
|  | 562 | 3709.7126 |  | 299.5686 |  |  |  | 311.2104 |  | 20.1578
|  | 563 | 3703.5894 |  | 299.0741 |  |  |  | 522.9491 |  | 33.8726
|  | 564 | 3697.497 |  | 298.5821 |  |  |  | 734.6569 |  | 47.5854
|  | 565 | 3691.4353 |  | 298.0926 |  |  |  | 946.334 |  | 61.2962
|  | 566 | 3685.4042 |  | 297.6056 |  |  |  | 1157.9805 |  | 75.005
|  | 567 | 3679.4036 |  | 297.121 |  |  |  | 1369.5964 |  | 88.7119
|  | 568 | 3679.3522 |  | 297.1169 |  |  |  | 1221.1478 |  | 79.0965
|  | 569 | 3687.323 |  | 297.7605 |  |  |  | 1480.477 |  | 95.8938
|  | 570 | 3695.2569 |  | 298.4012 |  |  |  | 1739.8431 |  | 112.6936
|  | 571 | 3703.1529 |  | 299.0388 |  |  |  | 2236.8471 |  | 144.8857
|  | 572 | 3711.0102 |  | 299.6733 |  |  |  | 2228.9898 |  | 144.3767
|  | 573 | 3718.8283 |  | 300.3047 |  |  |  | 2518.1717 |  | 163.1077
|  | 574 | 3726.7836 |  | 300.9471 |  |  |  | 1738.0164 |  | 112.5753
|  | 575 | 3727.3777 |  | 300.9951 |  |  |  | 965.2223 |  | 62.5196
|  | 576 | 3722.0938 |  | 300.5684 |  |  |  | 198.3062 |  | 12.8447
|  | 577 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 578 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 579 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 580 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 581 | 2970 |  | 239.8349 |  |  |  | 0 |  | 0
|  | 582 | 3168 |  | 255.8239 |  |  |  | 0 |  | 0
|  | 583 | 3366 |  | 271.8129 |  |  |  | 0 |  | 0
|  | 584 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 585 | 3723.4546 |  | 300.6783 |  |  |  | 38.5454 |  | 2.4967
|  | 586 | 3732.1285 |  | 301.3787 |  |  |  | 227.8715 |  | 14.7598
|  | 587 | 3740.7674 |  | 302.0763 |  |  |  | 417.2326 |  | 27.0251
|  | 588 | 3749.3708 |  | 302.7711 |  |  |  | 606.6292 |  | 39.2927
|  | 589 | 3757.9382 |  | 303.4629 |  |  |  | 796.0618 |  | 51.5627
|  | 590 | 3765.4106 |  | 304.0663 |  |  |  | 986.5894 |  | 63.9036
|  | 591 | 3771.2621 |  | 304.5388 |  |  |  | 832.2379 |  | 53.9059
|  | 592 | 3777.0819 |  | 305.0088 |  |  |  | 1172.9181 |  | 75.9726
|  | 593 | 3782.8692 |  | 305.4761 |  |  |  | 1513.6308 |  | 98.0413
|  | 594 | 3788.6231 |  | 305.9408 |  |  |  | 1854.3769 |  | 120.1122
|  | 595 | 3794.343 |  | 306.4027 |  |  |  | 1440.282 |  | 93.2903
|  | 596 | 3800.03 |  | 306.8619 |  |  |  | 1026.22 |  | 66.4706
|  | 597 | 3805.6852 |  | 307.3186 |  |  |  | 612.1898 |  | 39.6529
|  | 598 | 3811.3101 |  | 307.7728 |  |  |  | 198.1899 |  | 12.8372
|  | 599 | 3601.125 |  | 290.7998 |  |  |  | 0 |  | 0
|  | 600 | 2970 |  | 239.8349 |  |  |  | 0 |  | 0
|  | 601 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 602 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 603 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 604 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 605 | 2943 |  | 237.6546 |  |  |  | 0 |  | 0
|  | 606 | 3132 |  | 252.9168 |  |  |  | 0 |  | 0
|  | 607 | 3321 |  | 268.179 |  |  |  | 0 |  | 0
|  | 608 | 3510 |  | 283.4413 |  |  |  | 0 |  | 0
|  | 609 | 3699 |  | 298.7035 |  |  |  | 0 |  | 0
|  | 610 | 3785.1332 |  | 305.659 |  |  |  | 102.8668 |  | 6.6629
|  | 611 | 3790.8012 |  | 306.1167 |  |  |  | 286.1988 |  | 18.5377
|  | 612 | 3796.4411 |  | 306.5721 |  |  |  | 469.5589 |  | 30.4144
|  | 613 | 3802.0525 |  | 307.0252 |  |  |  | 652.9475 |  | 42.2929
|  | 614 | 3807.6352 |  | 307.4761 |  |  |  | 562.5077 |  | 36.4349
|  | 615 | 3813.1895 |  | 307.9246 |  |  |  | 472.0962 |  | 30.5787
|  | 616 | 3818.7159 |  | 308.3709 |  |  |  | 381.7126 |  | 24.7244
|  | 617 | 3824.215 |  | 308.8149 |  |  |  | 291.3565 |  | 18.8718
|  | 618 | 3829.687 |  | 309.2568 |  |  |  | 201.0273 |  | 13.021
|  | 619 | 3835.1326 |  | 309.6965 |  |  |  | 110.7246 |  | 7.1719
|  | 620 | 3840.5521 |  | 310.1342 |  |  |  | 20.4479 |  | 1.3245
|  | 621 | 3845.9458 |  | 310.5697 |  |  |  | 312.0542 |  | 20.2125
|  | 622 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 623 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 624 | 2821.5 |  | 227.8432 |  |  |  | 0 |  | 0
|  | 625 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 626 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 627 | 2545.7143 |  | 205.5728 |  |  |  | 0 |  | 0
|  | 628 | 2715.4286 |  | 219.2776 |  |  |  | 0 |  | 0
|  | 629 | 2885.1429 |  | 232.9825 |  |  |  | 0 |  | 0
|  | 630 | 3054.8571 |  | 246.6873 |  |  |  | 0 |  | 0
|  | 631 | 3224.5714 |  | 260.3922 |  |  |  | 0 |  | 0
|  | 632 | 3394.2857 |  | 274.0971 |  |  |  | 0 |  | 0
|  | 633 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 634 | 3733.7143 |  | 301.5068 |  |  |  | 0 |  | 0
|  | 635 | 3795.3094 |  | 306.4807 |  |  |  | 108.1191 |  | 7.0031
|  | 636 | 3786.1391 |  | 305.7402 |  |  |  | 287.0038 |  | 18.5899
|  | 637 | 3777.0059 |  | 305.0027 |  |  |  | 380.9941 |  | 24.6779
|  | 638 | 3767.9097 |  | 304.2681 |  |  |  | 390.0903 |  | 25.267
|  | 639 | 3758.8505 |  | 303.5366 |  |  |  | 823.4352 |  | 53.3358
|  | 640 | 3755.6738 |  | 303.28 |  |  |  | 996.3262 |  | 64.5343
|  | 641 | 3760.5163 |  | 303.6711 |  |  |  | 753.8837 |  | 48.8308
|  | 642 | 3765.3338 |  | 304.0601 |  |  |  | 511.4662 |  | 33.1288
|  | 643 | 3770.1271 |  | 304.4472 |  |  |  | 387.8729 |  | 25.1234
|  | 644 | 3774.897 |  | 304.8324 |  |  |  | 26.703 |  | 1.7296
|  | 645 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 646 | 3326.4 |  | 268.6151 |  |  |  | 0 |  | 0
|  | 647 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 648 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 649 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 650 | 2376 |  | 191.8679 |  |  |  | 0 |  | 0
|  | 651 | 2524.5 |  | 203.8597 |  |  |  | 0 |  | 0
|  | 652 | 2673 |  | 215.8514 |  |  |  | 0 |  | 0
|  | 653 | 2821.5 |  | 227.8432 |  |  |  | 0 |  | 0
|  | 654 | 2970 |  | 239.8349 |  |  |  | 0 |  | 0
|  | 655 | 3118.5 |  | 251.8267 |  |  |  | 0 |  | 0
|  | 656 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
|  | 657 | 3415.5 |  | 275.8102 |  |  |  | 0 |  | 0
|  | 658 | 3564 |  | 287.8019 |  |  |  | 0 |  | 0
|  | 659 | 3712.5 |  | 299.7936 |  |  |  | 0 |  | 0
|  | 660 | 3717.5011 |  | 300.1975 |  |  |  | 143.4989 |  | 9.2947
|  | 661 | 3711.2215 |  | 299.6904 |  |  |  | 298.2785 |  | 19.3202
|  | 662 | 3704.9734 |  | 299.1859 |  |  |  | 453.0266 |  | 29.3436
|  | 663 | 3698.7567 |  | 298.6838 |  |  |  | 310.7433 |  | 20.1275
|  | 664 | 3698.4697 |  | 298.6607 |  |  |  | 459.5303 |  | 29.7648
|  | 665 | 3706.2076 |  | 299.2855 |  |  |  | 1045.7924 |  | 67.7383
|  | 666 | 3713.915 |  | 299.9079 |  |  |  | 889.585 |  | 57.6204
|  | 667 | 3721.5917 |  | 300.5278 |  |  |  | 1178.9083 |  | 76.3606
|  | 668 | 3729.2375 |  | 301.1452 |  |  |  | 844.5625 |  | 54.7042
|  | 669 | 3736.8531 |  | 301.7602 |  |  |  | 510.2469 |  | 33.0498
|  | 670 | 3744.4395 |  | 302.3728 |  |  |  | 175.9605 |  | 11.3974
|  | 671 | 3593.7 |  | 290.2003 |  |  |  | 0 |  | 0
|  | 672 | 3267 |  | 263.8184 |  |  |  | 0 |  | 0
Note on C8: Peter North: (Sat-Toutlet = 2 to 5K) Condenser refrig sat temp (30ºC) minus 2ºC approach temp. Needs to be written-up and justified. Sat temp - outlet temp btw 2 to 5K. 2K taken to max deltaT and min mass flowrate.
Note on C9: Peter North: (Toutlet - sat = 5K) Evaporator refrig sat temp (5ºC) plus 5K or 2K approach temp. Needs to be written-up and justified.

## Spring_Autumn
T0 | K | 273
cp water | kJ/kg.K | 4.18
Tcond.sat | ºC | 30
T evap.sat | ºC | 5
Thot sink | ºC | 20 | 293 | K
Tcold sink | ºC | 10 | 283 | K | Approach Temp
Tcond.hot, out | ºC | 28 | 301 | K | 2 | K
Thp.hot, out | ºC | 10 | 283 | K | 5 | K
Tcond.cold, out | ºC | 28 | 301 | K | 5 | K
Thp.cold, out | ºC | 7 | 280 | K | 2 | K
Spring/Autumn
|  |  | Hot Sink | [5 empty] | Cold Sink
|  |  | Condenser |  |  | HP Evaporator |  |  | Condenser |  |  | HP Evaporator
|  |  | Qcond, hot | ṁcond, hot | Edest cond, hot | Qhp, hot | ṁhp, hot | Edest hp, hot | Qcond, cold | ṁcond, cold | Edest cond, cold | Qhp, cold | ṁhp, cold | Edest hp, cold
|  |  | kW | kg/s | kW | kW | kg/s | kW | kW | kg/s | kW | kW | kg/s | kW
|  | Total | 2182261.1703 | 0 | 176223.0411 | 0 | 0 | 0 | 640290.5163 | 0 | 41473.0674 | 0 | 0 | 0 | 217696.1085
|  | Hours |  |  |  | 8.075% | [5 empty] | 6.477%
|  | 1 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 2 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 3 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 4 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 5 | 3272.7044 |  | 264.2791 |  |  |  | 0 |  | 0
|  | 6 | 3512.1706 |  | 283.6165 |  |  |  | 0 |  | 0
|  | 7 | 3718.4927 |  | 300.2776 |  |  |  | 33.144 |  | 2.1468
|  | 8 | 3717.5067 |  | 300.198 |  |  |  | 273.5962 |  | 17.7214
|  | 9 | 3712.4356 |  | 299.7884 |  |  |  | 518.1335 |  | 33.5607
|  | 10 | 3705.1105 |  | 299.1969 |  |  |  | 764.9247 |  | 49.5459
|  | 11 | 3697.8219 |  | 298.6084 |  |  |  | 1011.6796 |  | 65.5288
|  | 12 | 3690.5694 |  | 298.0227 |  |  |  | 1258.3982 |  | 81.5093
|  | 13 | 3683.353 |  | 297.44 |  |  |  | 1505.0808 |  | 97.4875
|  | 14 | 3676.1725 |  | 296.8601 |  |  |  | 1751.7274 |  | 113.4634
|  | 15 | 3669.0279 |  | 296.2832 |  |  |  | 1599.2279 |  | 103.5856
|  | 16 | 3664.1878 |  | 295.8923 |  |  |  | 1816.9269 |  | 117.6865
|  | 17 | 3663.4534 |  | 295.833 |  |  |  | 2562.6671 |  | 165.9898
|  | 18 | 3662.7215 |  | 295.7739 |  |  |  | 2403.7549 |  | 155.6967
|  | 19 | 3661.9919 |  | 295.715 |  |  |  | 2723.7728 |  | 176.4249
|  | 20 | 3661.2642 |  | 295.6562 |  |  |  | 2405.2123 |  | 155.791
|  | 21 | 3660.5386 |  | 295.5976 |  |  |  | 2884.8702 |  | 186.8596
|  | 22 | 3659.8147 |  | 295.5392 |  |  |  | 2087.3735 |  | 135.2039
|  | 23 | 3655.0143 |  | 295.1515 |  |  |  | 1293.9533 |  | 83.8123
|  | 24 | 3647.9938 |  | 294.5846 |  |  |  | 502.7532 |  | 32.5645
|  | 25 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 26 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 27 | 2745.8788 |  | 221.7366 |  |  |  | 0 |  | 0
|  | 28 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 29 | 3170.076 |  | 255.9916 |  |  |  | 0 |  | 0
|  | 30 | 3375.3327 |  | 272.5666 |  |  |  | 0 |  | 0
|  | 31 | 3580.5895 |  | 289.1415 |  |  |  | 0 |  | 0
|  | 32 | 3610.8818 |  | 291.5877 |  |  |  | 174.9644 |  | 11.3328
|  | 33 | 3606.9574 |  | 291.2708 |  |  |  | 384.1455 |  | 24.882
|  | 34 | 3601.0728 |  | 290.7956 |  |  |  | 595.2868 |  | 38.5581
|  | 35 | 3595.221 |  | 290.3231 |  |  |  | 806.3953 |  | 52.2321
|  | 36 | 3589.4018 |  | 289.8532 |  |  |  | 1017.4712 |  | 65.9039
|  | 37 | 3583.6152 |  | 289.3859 |  |  |  | 1228.5146 |  | 79.5737
|  | 38 | 3577.8609 |  | 288.9212 |  |  |  | 1439.5256 |  | 93.2413
|  | 39 | 3572.0508 |  | 288.452 |  |  |  | 1650.5925 |  | 106.9126
|  | 40 | 3567.7202 |  | 288.1023 |  |  |  | 1860.1798 |  | 120.4881
|  | 41 | 3567.482 |  | 288.0831 |  |  |  | 1700.7738 |  | 110.163
|  | 42 | 3567.2472 |  | 288.0641 |  |  |  | 2020.2969 |  | 130.8592
|  | 43 | 3567.0151 |  | 288.0454 |  |  |  | 2339.8172 |  | 151.5553
|  | 44 | 3566.7849 |  | 288.0268 |  |  |  | 2499.6915 |  | 161.9107
|  | 45 | 3566.556 |  | 288.0083 |  |  |  | 2978.8528 |  | 192.947
|  | 46 | 3566.3279 |  | 287.9899 |  |  |  | 2180.8603 |  | 141.2593
|  | 47 | 3562.0313 |  | 287.6429 |  |  |  | 1386.9363 |  | 89.835
|  | 48 | 3555.535 |  | 287.1183 |  |  |  | 595.212 |  | 38.5532
|  | 49 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 50 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 51 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 52 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 53 | 3217.443 |  | 259.8166 |  |  |  | 0 |  | 0
|  | 54 | 3438.4887 |  | 277.6665 |  |  |  | 0 |  | 0
|  | 55 | 3520.985 |  | 284.3283 |  |  |  | 138.5494 |  | 8.9742
|  | 56 | 3521.0149 |  | 284.3307 |  |  |  | 359.5652 |  | 23.2899
|  | 57 | 3516.9762 |  | 284.0046 |  |  |  | 584.6496 |  | 37.8691
|  | 58 | 3510.7247 |  | 283.4998 |  |  |  | 811.9467 |  | 52.5916
|  | 59 | 3504.5058 |  | 282.9976 |  |  |  | 1039.2113 |  | 67.3121
|  | 60 | 3498.3195 |  | 282.498 |  |  |  | 1266.4434 |  | 82.0304
|  | 61 | 3492.1655 |  | 282.0011 |  |  |  | 1493.643 |  | 96.7466
|  | 62 | 3486.0439 |  | 281.5068 |  |  |  | 1720.8104 |  | 111.4608
|  | 63 | 3479.9544 |  | 281.015 |  |  |  | 1947.9455 |  | 126.1728
|  | 64 | 3476.1335 |  | 280.7065 |  |  |  | 1792.1224 |  | 116.0798
|  | 65 | 3476.4034 |  | 280.7283 |  |  |  | 2079.2119 |  | 134.6753
|  | 66 | 3476.6763 |  | 280.7503 |  |  |  | 2366.2983 |  | 153.2705
|  | 67 | 3476.9515 |  | 280.7725 |  |  |  | 2908.8132 |  | 188.4104
|  | 68 | 3477.2276 |  | 280.7948 |  |  |  | 2908.537 |  | 188.3925
|  | 69 | 3477.5044 |  | 280.8172 |  |  |  | 3227.5485 |  | 209.0556
|  | 70 | 3477.7818 |  | 280.8396 |  |  |  | 2397.1217 |  | 155.267
|  | 71 | 3473.9893 |  | 280.5333 |  |  |  | 1570.7648 |  | 101.742
|  | 72 | 3467.9927 |  | 280.0491 |  |  |  | 746.612 |  | 48.3598
|  | 73 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 74 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 75 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 76 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 77 | 3192.8823 |  | 257.8332 |  |  |  | 0 |  | 0
|  | 78 | 3405.7411 |  | 275.0221 |  |  |  | 0 |  | 0
|  | 79 | 3435.8879 |  | 277.4565 |  |  |  | 182.7121 |  | 11.8347
|  | 80 | 3436.4325 |  | 277.5005 |  |  |  | 395.0263 |  | 25.5868
|  | 81 | 3436.9856 |  | 277.5452 |  |  |  | 607.332 |  | 39.3383
|  | 82 | 3437.5468 |  | 277.5905 |  |  |  | 819.6296 |  | 53.0893
|  | 83 | 3438.1154 |  | 277.6364 |  |  |  | 1031.9199 |  | 66.8398
|  | 84 | 3438.6907 |  | 277.6829 |  |  |  | 1244.2033 |  | 80.5899
|  | 85 | 3439.2723 |  | 277.7298 |  |  |  | 1456.4806 |  | 94.3395
|  | 86 | 3439.8596 |  | 277.7773 |  |  |  | 1668.7522 |  | 108.0889
|  | 87 | 3440.452 |  | 277.8251 |  |  |  | 1508.5156 |  | 97.71
|  | 88 | 3441.0496 |  | 277.8734 |  |  |  | 1880.4209 |  | 121.7991
|  | 89 | 3441.6513 |  | 277.9219 |  |  |  | 2252.3222 |  | 145.888
|  | 90 | 3442.2559 |  | 277.9708 |  |  |  | 2624.2205 |  | 169.9767
|  | 91 | 3442.8626 |  | 278.0198 |  |  |  | 2184.5925 |  | 141.501
|  | 92 | 3443.4723 |  | 278.069 |  |  |  | 1744.9614 |  | 113.0251
|  | 93 | 3444.0863 |  | 278.1186 |  |  |  | 1305.3261 |  | 84.5489
|  | 94 | 3444.7058 |  | 278.1686 |  |  |  | 865.6853 |  | 56.0724
|  | 95 | 3441.2331 |  | 277.8882 |  |  |  | 430.1368 |  | 27.8609
|  | 96 | 3192.8823 |  | 257.8332 |  |  |  | 0 |  | 0
|  | 97 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 98 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 99 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 100 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 101 | 3163.8561 |  | 255.4893 |  |  |  | 0 |  | 0
|  | 102 | 3367.0395 |  | 271.8969 |  |  |  | 0 |  | 0
|  | 103 | 3405.718 |  | 275.0202 |  |  |  | 164.505 |  | 10.6554
|  | 104 | 3406.6054 |  | 275.0919 |  |  |  | 366.801 |  | 23.7585
|  | 105 | 3407.4995 |  | 275.1641 |  |  |  | 569.0903 |  | 36.8613
|  | 106 | 3408.3996 |  | 275.2368 |  |  |  | 771.3736 |  | 49.9636
|  | 107 | 3409.305 |  | 275.3099 |  |  |  | 973.6516 |  | 63.0656
|  | 108 | 3410.215 |  | 275.3834 |  |  |  | 1175.925 |  | 76.1673
|  | 109 | 3411.1289 |  | 275.4572 |  |  |  | 1378.1946 |  | 89.2688
|  | 110 | 3412.0462 |  | 275.5313 |  |  |  | 1286.0521 |  | 83.3005
|  | 111 | 3412.9668 |  | 275.6056 |  |  |  | 1193.9062 |  | 77.332
|  | 112 | 3413.8911 |  | 275.6802 |  |  |  | 1101.7568 |  | 71.3633
|  | 113 | 3414.8191 |  | 275.7552 |  |  |  | 1009.6035 |  | 65.3943
|  | 114 | 3415.7511 |  | 275.8304 |  |  |  | 917.4463 |  | 59.4251
|  | 115 | 3416.6873 |  | 275.906 |  |  |  | 825.2849 |  | 53.4556
|  | 116 | 3417.6279 |  | 275.982 |  |  |  | 733.1191 |  | 47.4858
|  | 117 | 3418.5728 |  | 276.0583 |  |  |  | 1051.4624 |  | 68.1056
|  | 118 | 3419.5217 |  | 276.1349 |  |  |  | 571.5812 |  | 37.0226
|  | 119 | 3416.3466 |  | 275.8785 |  |  |  | 95.824 |  | 6.2067
|  | 120 | 3033.2382 |  | 244.9416 |  |  |  | 0 |  | 0
|  | 121 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 122 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 123 | 2736.7563 |  | 220.9999 |  |  |  | 0 |  | 0
|  | 124 | 2919.2067 |  | 235.7332 |  |  |  | 0 |  | 0
|  | 125 | 3101.6571 |  | 250.4666 |  |  |  | 0 |  | 0
|  | 126 | 3284.1075 |  | 265.1999 |  |  |  | 0 |  | 0
|  | 127 | 3383.5081 |  | 273.2267 |  |  |  | 83.0498 |  | 5.3793
|  | 128 | 3385.5819 |  | 273.3942 |  |  |  | 263.4265 |  | 17.0627
|  | 129 | 3383.5204 |  | 273.2277 |  |  |  | 447.9384 |  | 29.014
|  | 130 | 3379.0875 |  | 272.8698 |  |  |  | 634.8218 |  | 41.1188
|  | 131 | 3374.682 |  | 272.514 |  |  |  | 821.6776 |  | 53.2219
|  | 132 | 3370.304 |  | 272.1605 |  |  |  | 1008.5061 |  | 65.3232
|  | 133 | 3365.9532 |  | 271.8091 |  |  |  | 1104.082 |  | 71.5139
|  | 134 | 3361.6297 |  | 271.46 |  |  |  | 1108.4056 |  | 71.7939
|  | 135 | 3357.3333 |  | 271.113 |  |  |  | 1568.828 |  | 101.6165
|  | 136 | 3355.4579 |  | 270.9616 |  |  |  | 1753.1538 |  | 113.5557
|  | 137 | 3357.7288 |  | 271.145 |  |  |  | 1495.4523 |  | 96.8638
|  | 138 | 3359.9973 |  | 271.3282 |  |  |  | 1237.7532 |  | 80.1721
|  | 139 | 3362.2641 |  | 271.5112 |  |  |  | 1107.7712 |  | 71.7529
|  | 140 | 3364.5295 |  | 271.6942 |  |  |  | 722.3598 |  | 46.7889
|  | 141 | 3366.7947 |  | 271.8771 |  |  |  | 464.6641 |  | 30.0973
|  | 142 | 3369.0603 |  | 272.06 |  |  |  | 206.9679 |  | 13.4058
|  | 143 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 144 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 145 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 146 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 147 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 148 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 149 | 3033.2382 |  | 244.9416 |  |  |  | 0 |  | 0
|  | 150 | 3192.8823 |  | 257.8332 |  |  |  | 0 |  | 0
|  | 151 | 3345.6978 |  | 270.1735 |  |  |  | 6.8287 |  | 0.44231
|  | 152 | 3348.1555 |  | 270.3719 |  |  |  | 164.0151 |  | 10.6236
|  | 153 | 3346.4667 |  | 270.2355 |  |  |  | 325.348 |  | 21.0735
|  | 154 | 3342.3787 |  | 269.9054 |  |  |  | 489.0801 |  | 31.6788
|  | 155 | 3338.3169 |  | 269.5774 |  |  |  | 652.7861 |  | 42.2824
|  | 156 | 3334.2811 |  | 269.2515 |  |  |  | 816.466 |  | 52.8844
|  | 157 | 3330.2712 |  | 268.9277 |  |  |  | 980.1199 |  | 63.4846
|  | 158 | 3326.2873 |  | 268.606 |  |  |  | 1143.748 |  | 74.0831
|  | 159 | 3322.3291 |  | 268.2864 |  |  |  | 988.062 |  | 63.999
|  | 160 | 3320.8117 |  | 268.1638 |  |  |  | 1149.2235 |  | 74.4378
|  | 161 | 3323.4461 |  | 268.3766 |  |  |  | 1785.1656 |  | 115.6292
|  | 162 | 3326.0746 |  | 268.5888 |  |  |  | 1622.893 |  | 105.1185
|  | 163 | 3328.6969 |  | 268.8006 |  |  |  | 1939.5589 |  | 125.6296
|  | 164 | 3331.3128 |  | 269.0118 |  |  |  | 1585.726 |  | 102.7111
|  | 165 | 3333.9229 |  | 269.2226 |  |  |  | 1231.8989 |  | 79.7929
|  | 166 | 3336.5281 |  | 269.433 |  |  |  | 878.0766 |  | 56.875
|  | 167 | 3334.9869 |  | 269.3085 |  |  |  | 528.4007 |  | 34.2257
|  | 168 | 3331.0563 |  | 268.9911 |  |  |  | 181.1143 |  | 11.7312
|  | 169 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 170 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 171 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 172 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 173 | 3272.7044 |  | 264.2791 |  |  |  | 0 |  | 0
|  | 174 | 3313.3102 |  | 267.5581 |  |  |  | 198.8603 |  | 12.8806
|  | 175 | 3311.9417 |  | 267.4476 |  |  |  | 439.695 |  | 28.48
|  | 176 | 3314.7239 |  | 267.6722 |  |  |  | 676.379 |  | 43.8106
|  | 177 | 3313.3589 |  | 267.562 |  |  |  | 917.2102 |  | 59.4098
|  | 178 | 3309.6029 |  | 267.2587 |  |  |  | 1160.4323 |  | 75.1638
|  | 179 | 3305.4308 |  | 266.9218 |  |  |  | 1404.0706 |  | 90.9448
|  | 180 | 3300.8438 |  | 266.5514 |  |  |  | 1648.1238 |  | 106.7527
|  | 181 | 3296.2831 |  | 266.1831 |  |  |  | 1892.1507 |  | 122.5589
|  | 182 | 3291.7486 |  | 265.8169 |  |  |  | 2136.1514 |  | 138.3634
|  | 183 | 3287.2402 |  | 265.4529 |  |  |  | 1981.0156 |  | 128.3149
|  | 184 | 3285.142 |  | 265.2834 |  |  |  | 2195.9727 |  | 142.2381
|  | 185 | 3287.1813 |  | 265.4481 |  |  |  | 2938.9392 |  | 190.3618
|  | 186 | 3289.2105 |  | 265.612 |  |  |  | 2777.2659 |  | 179.8898
|  | 187 | 3291.2294 |  | 265.775 |  |  |  | 3094.5353 |  | 200.4401
|  | 188 | 3293.2374 |  | 265.9371 |  |  |  | 2773.2391 |  | 179.629
|  | 189 | 3295.2348 |  | 266.0984 |  |  |  | 3250.174 |  | 210.5211
|  | 190 | 3297.2213 |  | 266.2589 |  |  |  | 2449.9669 |  | 158.6899
|  | 191 | 3295.0772 |  | 266.0857 |  |  |  | 1653.8904 |  | 107.1262
|  | 192 | 3290.6017 |  | 265.7243 |  |  |  | 860.1453 |  | 55.7136
|  | 193 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 194 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 195 | 2745.8788 |  | 221.7366 |  |  |  | 0 |  | 0
|  | 196 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 197 | 3170.076 |  | 255.9916 |  |  |  | 0 |  | 0
|  | 198 | 3269.0402 |  | 263.9832 |  |  |  | 106.2926 |  | 6.8848
|  | 199 | 3267.0611 |  | 263.8233 |  |  |  | 313.5284 |  | 20.3079
|  | 200 | 3269.2085 |  | 263.9967 |  |  |  | 516.6377 |  | 33.4638
|  | 201 | 3267.2347 |  | 263.8374 |  |  |  | 723.8682 |  | 46.8866
|  | 202 | 3262.9414 |  | 263.4907 |  |  |  | 933.4183 |  | 60.4596
|  | 203 | 3258.6733 |  | 263.146 |  |  |  | 1142.9431 |  | 74.031
|  | 204 | 3254.4303 |  | 262.8034 |  |  |  | 1352.4428 |  | 87.6008
|  | 205 | 3250.2124 |  | 262.4628 |  |  |  | 1561.9174 |  | 101.1689
|  | 206 | 3246.0194 |  | 262.1242 |  |  |  | 1771.3671 |  | 114.7355
|  | 207 | 3241.8513 |  | 261.7876 |  |  |  | 1980.7919 |  | 128.3004
|  | 208 | 3240.0166 |  | 261.6394 |  |  |  | 2187.8834 |  | 141.7142
|  | 209 | 3242.2925 |  | 261.8232 |  |  |  | 2025.9634 |  | 131.2262
|  | 210 | 3244.5583 |  | 262.0062 |  |  |  | 2342.9858 |  | 151.7605
|  | 211 | 3246.8133 |  | 262.1883 |  |  |  | 2660.019 |  | 172.2955
|  | 212 | 3249.0566 |  | 262.3694 |  |  |  | 2817.4198 |  | 182.4907
|  | 213 | 3251.2876 |  | 262.5496 |  |  |  | 3294.1212 |  | 213.3677
|  | 214 | 3253.5056 |  | 262.7287 |  |  |  | 2493.6826 |  | 161.5215
|  | 215 | 3251.6213 |  | 262.5765 |  |  |  | 1697.3463 |  | 109.941
|  | 216 | 3247.4782 |  | 262.242 |  |  |  | 903.2688 |  | 58.5068
|  | 217 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 218 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 219 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 220 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 221 | 3217.443 |  | 259.8166 |  |  |  | 0 |  | 0
|  | 222 | 3227.434 |  | 260.6234 |  |  |  | 211.0547 |  | 13.6705
|  | 223 | 3225.7001 |  | 260.4833 |  |  |  | 433.8342 |  | 28.1004
|  | 224 | 3228.0571 |  | 260.6737 |  |  |  | 652.523 |  | 42.2654
|  | 225 | 3226.3249 |  | 260.5338 |  |  |  | 875.3008 |  | 56.6952
|  | 226 | 3222.355 |  | 260.2132 |  |  |  | 1100.3165 |  | 71.27
|  | 227 | 3218.409 |  | 259.8946 |  |  |  | 1325.3082 |  | 85.8432
|  | 228 | 3214.4869 |  | 259.5778 |  |  |  | 1550.276 |  | 100.4149
|  | 229 | 3210.5886 |  | 259.2631 |  |  |  | 1775.2199 |  | 114.985
|  | 230 | 3206.7141 |  | 258.9502 |  |  |  | 2000.1402 |  | 129.5536
|  | 231 | 3202.8632 |  | 258.6392 |  |  |  | 2225.0367 |  | 144.1207
|  | 232 | 3201.2569 |  | 258.5095 |  |  |  | 2066.9989 |  | 133.8842
|  | 233 | 3203.7218 |  | 258.7085 |  |  |  | 2351.8935 |  | 152.3375
|  | 234 | 3206.1753 |  | 258.9067 |  |  |  | 2636.7993 |  | 170.7915
|  | 235 | 3208.6168 |  | 259.1038 |  |  |  | 3177.1479 |  | 205.7911
|  | 236 | 3211.045 |  | 259.2999 |  |  |  | 3174.7196 |  | 205.6338
|  | 237 | 3213.4598 |  | 259.4949 |  |  |  | 3491.5931 |  | 226.1584
|  | 238 | 3215.861 |  | 259.6888 |  |  |  | 2659.0424 |  | 172.2322
|  | 239 | 3214.1972 |  | 259.5545 |  |  |  | 1830.5568 |  | 118.5693
|  | 240 | 3210.3649 |  | 259.245 |  |  |  | 1004.2397 |  | 65.0469
|  | 241 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 242 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 243 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 244 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 245 | 3192.8823 |  | 257.8332 |  |  |  | 0 |  | 0
|  | 246 | 3191.8276 |  | 257.7481 |  |  |  | 213.9136 |  | 13.8557
|  | 247 | 3190.3144 |  | 257.6259 |  |  |  | 428.2856 |  | 27.741
|  | 248 | 3192.859 |  | 257.8313 |  |  |  | 638.5998 |  | 41.3636
|  | 249 | 3195.3989 |  | 258.0364 |  |  |  | 848.9187 |  | 54.9864
|  | 250 | 3197.9335 |  | 258.2411 |  |  |  | 1059.2429 |  | 68.6096
|  | 251 | 3200.4624 |  | 258.4453 |  |  |  | 1269.5729 |  | 82.2331
|  | 252 | 3202.9849 |  | 258.649 |  |  |  | 1479.9091 |  | 95.8571
|  | 253 | 3205.5007 |  | 258.8522 |  |  |  | 1690.2522 |  | 109.4815
|  | 254 | 3208.0091 |  | 259.0548 |  |  |  | 1900.6026 |  | 123.1063
|  | 255 | 3210.5099 |  | 259.2567 |  |  |  | 1738.4577 |  | 112.6038
|  | 256 | 3213.0032 |  | 259.458 |  |  |  | 2108.4673 |  | 136.5702
|  | 257 | 3215.4883 |  | 259.6587 |  |  |  | 2478.4852 |  | 160.5371
|  | 258 | 3217.9642 |  | 259.8586 |  |  |  | 2848.5122 |  | 184.5046
|  | 259 | 3220.4304 |  | 260.0578 |  |  |  | 2407.0247 |  | 155.9084
|  | 260 | 3222.8878 |  | 260.2562 |  |  |  | 1965.546 |  | 127.3129
|  | 261 | 3225.3381 |  | 260.4541 |  |  |  | 1524.0744 |  | 98.7178
|  | 262 | 3227.7825 |  | 260.6515 |  |  |  | 1082.6086 |  | 70.123
|  | 263 | 3226.1797 |  | 260.5221 |  |  |  | 645.1902 |  | 41.7904
|  | 264 | 3192.8823 |  | 257.8332 |  |  |  | 0 |  | 0
|  | 265 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 266 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 267 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 268 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 269 | 3163.8561 |  | 255.4893 |  |  |  | 0 |  | 0
|  | 270 | 3204.971 |  | 258.8094 |  |  |  | 162.0685 |  | 10.4975
|  | 271 | 3203.5322 |  | 258.6932 |  |  |  | 366.6907 |  | 23.7514
|  | 272 | 3206.1505 |  | 258.9047 |  |  |  | 567.2559 |  | 36.7424
|  | 273 | 3208.7664 |  | 259.1159 |  |  |  | 767.8234 |  | 49.7337
|  | 274 | 3211.3795 |  | 259.3269 |  |  |  | 968.3937 |  | 62.7251
|  | 275 | 3213.9892 |  | 259.5377 |  |  |  | 1168.9675 |  | 75.7167
|  | 276 | 3216.595 |  | 259.7481 |  |  |  | 1369.545 |  | 88.7085
|  | 277 | 3219.1965 |  | 259.9582 |  |  |  | 1570.127 |  | 101.7007
|  | 278 | 3221.7932 |  | 260.1679 |  |  |  | 1476.3051 |  | 95.6236
|  | 279 | 3224.3855 |  | 260.3772 |  |  |  | 1382.4876 |  | 89.5469
|  | 280 | 3226.9736 |  | 260.5862 |  |  |  | 1288.6742 |  | 83.4703
|  | 281 | 3229.5581 |  | 260.7949 |  |  |  | 1194.8646 |  | 77.3941
|  | 282 | 3232.1392 |  | 261.0033 |  |  |  | 1101.0582 |  | 71.318
|  | 283 | 3235.599 |  | 261.2827 |  |  |  | 1006.3733 |  | 65.1851
|  | 284 | 3239.0545 |  | 261.5617 |  |  |  | 911.6926 |  | 59.0524
|  | 285 | 3242.5059 |  | 261.8405 |  |  |  | 1227.5293 |  | 79.5099
|  | 286 | 3245.9531 |  | 262.1188 |  |  |  | 745.1498 |  | 48.265
|  | 287 | 3245.3364 |  | 262.069 |  |  |  | 266.8342 |  | 17.2835
|  | 288 | 3033.2382 |  | 244.9416 |  |  |  | 0 |  | 0
|  | 289 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 290 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 291 | 2736.7563 |  | 220.9999 |  |  |  | 0 |  | 0
|  | 292 | 2919.2067 |  | 235.7332 |  |  |  | 0 |  | 0
|  | 293 | 3101.6571 |  | 250.4666 |  |  |  | 0 |  | 0
|  | 294 | 3231.59 |  | 260.959 |  |  |  | 52.5175 |  | 3.4017
|  | 295 | 3231.1331 |  | 260.9221 |  |  |  | 235.4248 |  | 15.249
|  | 296 | 3234.7565 |  | 261.2147 |  |  |  | 414.2518 |  | 26.832
|  | 297 | 3234.304 |  | 261.1781 |  |  |  | 597.1548 |  | 38.6791
|  | 298 | 3231.6338 |  | 260.9625 |  |  |  | 782.2754 |  | 50.6697
|  | 299 | 3228.9841 |  | 260.7485 |  |  |  | 967.3756 |  | 62.6591
|  | 300 | 3226.3545 |  | 260.5362 |  |  |  | 1152.4555 |  | 74.6472
|  | 301 | 3223.7452 |  | 260.3255 |  |  |  | 1246.29 |  | 80.725
|  | 302 | 3221.1561 |  | 260.1164 |  |  |  | 1248.8792 |  | 80.8927
|  | 303 | 3218.5869 |  | 259.9089 |  |  |  | 1707.5744 |  | 110.6035
|  | 304 | 3218.2809 |  | 259.8842 |  |  |  | 1890.3308 |  | 122.441
|  | 305 | 3222.0584 |  | 260.1893 |  |  |  | 1631.1227 |  | 105.6515
|  | 306 | 3225.8306 |  | 260.4939 |  |  |  | 1371.92 |  | 88.8624
|  | 307 | 3229.5982 |  | 260.7981 |  |  |  | 1240.4371 |  | 80.3459
|  | 308 | 3233.3618 |  | 261.102 |  |  |  | 853.5275 |  | 55.2849
|  | 309 | 3237.1227 |  | 261.4057 |  |  |  | 594.3361 |  | 38.4965
|  | 310 | 3240.8816 |  | 261.7093 |  |  |  | 335.1466 |  | 21.7082
|  | 311 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 312 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 313 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 314 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 315 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 316 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 317 | 3033.2382 |  | 244.9416 |  |  |  | 0 |  | 0
|  | 318 | 3192.8823 |  | 257.8332 |  |  |  | 0 |  | 0
|  | 319 | 3229.9261 |  | 260.8246 |  |  |  | 122.6003 |  | 7.9411
|  | 320 | 3233.8679 |  | 261.1429 |  |  |  | 278.3026 |  | 18.0263
|  | 321 | 3233.6993 |  | 261.1293 |  |  |  | 438.1153 |  | 28.3777
|  | 322 | 3231.2267 |  | 260.9296 |  |  |  | 600.2321 |  | 38.8784
|  | 323 | 3228.7734 |  | 260.7315 |  |  |  | 762.3295 |  | 49.3778
|  | 324 | 3226.3396 |  | 260.535 |  |  |  | 924.4074 |  | 59.876
|  | 325 | 3223.9251 |  | 260.34 |  |  |  | 1086.4661 |  | 70.3729
|  | 326 | 3221.5297 |  | 260.1466 |  |  |  | 1248.5055 |  | 80.8685
|  | 327 | 3219.1536 |  | 259.9547 |  |  |  | 1091.2376 |  | 70.6819
|  | 328 | 3219.135 |  | 259.9532 |  |  |  | 1250.9002 |  | 81.0236
|  | 329 | 3223.2405 |  | 260.2847 |  |  |  | 1885.3712 |  | 122.1198
|  | 330 | 3227.3392 |  | 260.6157 |  |  |  | 1721.6284 |  | 111.5138
|  | 331 | 3231.431 |  | 260.9461 |  |  |  | 2036.8249 |  | 131.9298
|  | 332 | 3235.5152 |  | 261.2759 |  |  |  | 1681.5235 |  | 108.9161
|  | 333 | 3239.5928 |  | 261.6052 |  |  |  | 1326.229 |  | 85.9029
|  | 334 | 3243.6646 |  | 261.934 |  |  |  | 970.9401 |  | 62.89
|  | 335 | 3243.6058 |  | 261.9293 |  |  |  | 619.7818 |  | 40.1447
|  | 336 | 3241.2014 |  | 261.7351 |  |  |  | 270.9692 |  | 17.5513
|  | 337 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 338 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 339 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 340 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 341 | 3233.8835 |  | 261.1442 |  |  |  | 38.8209 |  | 2.5145
|  | 342 | 3231.5721 |  | 260.9575 |  |  |  | 280.5984 |  | 18.175
|  | 343 | 3231.6719 |  | 260.9656 |  |  |  | 519.9648 |  | 33.6793
|  | 344 | 3235.9147 |  | 261.3082 |  |  |  | 755.1882 |  | 48.9152
|  | 345 | 3236.0123 |  | 261.3161 |  |  |  | 994.5568 |  | 64.4197
|  | 346 | 3233.7235 |  | 261.1312 |  |  |  | 1236.3118 |  | 80.0787
|  | 347 | 3231.4533 |  | 260.9479 |  |  |  | 1478.0482 |  | 95.7365
|  | 348 | 3229.2016 |  | 260.7661 |  |  |  | 1719.766 |  | 111.3931
|  | 349 | 3226.9684 |  | 260.5858 |  |  |  | 1961.4654 |  | 127.0486
|  | 350 | 3224.7535 |  | 260.4069 |  |  |  | 2203.1465 |  | 142.7028
|  | 351 | 3222.5569 |  | 260.2295 |  |  |  | 2045.6989 |  | 132.5046
|  | 352 | 3222.7802 |  | 260.2476 |  |  |  | 2258.3344 |  | 146.2774
|  | 353 | 3227.1438 |  | 260.5999 |  |  |  | 2998.9768 |  | 194.2505
|  | 354 | 3231.4944 |  | 260.9512 |  |  |  | 2834.982 |  | 183.6282
|  | 355 | 3235.832 |  | 261.3015 |  |  |  | 3149.9326 |  | 204.0283
|  | 356 | 3240.1561 |  | 261.6507 |  |  |  | 2826.3203 |  | 183.0672
|  | 357 | 3244.4669 |  | 261.9988 |  |  |  | 3300.9419 |  | 213.8095
|  | 358 | 3248.764 |  | 262.3458 |  |  |  | 2498.4242 |  | 161.8286
|  | 359 | 3248.9114 |  | 262.3577 |  |  |  | 1700.0562 |  | 110.1165
|  | 360 | 3246.6768 |  | 262.1773 |  |  |  | 904.0702 |  | 58.5587
|  | 361 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 362 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 363 | 2745.8788 |  | 221.7366 |  |  |  | 0 |  | 0
|  | 364 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 365 | 3170.076 |  | 255.9916 |  |  |  | 0 |  | 0
|  | 366 | 3238.0019 |  | 261.4767 |  |  |  | 137.3308 |  | 8.8952
|  | 367 | 3238.289 |  | 261.4999 |  |  |  | 342.3004 |  | 22.1716
|  | 368 | 3242.7252 |  | 261.8582 |  |  |  | 543.121 |  | 35.1792
|  | 369 | 3243.0072 |  | 261.8809 |  |  |  | 748.0957 |  | 48.4559
|  | 370 | 3240.8801 |  | 261.7092 |  |  |  | 955.4795 |  | 61.8886
|  | 371 | 3238.7708 |  | 261.5388 |  |  |  | 1162.8455 |  | 75.3201
|  | 372 | 3236.6793 |  | 261.3699 |  |  |  | 1370.1938 |  | 88.7506
|  | 373 | 3234.6054 |  | 261.2025 |  |  |  | 1577.5244 |  | 102.1798
|  | 374 | 3232.5491 |  | 261.0364 |  |  |  | 1784.8375 |  | 115.608
|  | 375 | 3230.5103 |  | 260.8718 |  |  |  | 1992.133 |  | 129.035
|  | 376 | 3230.9088 |  | 260.904 |  |  |  | 2196.9911 |  | 142.3041
|  | 377 | 3235.4523 |  | 261.2709 |  |  |  | 2032.8036 |  | 131.6693
|  | 378 | 3239.9826 |  | 261.6367 |  |  |  | 2347.5614 |  | 152.0569
|  | 379 | 3244.4992 |  | 262.0014 |  |  |  | 2662.3331 |  | 172.4453
|  | 380 | 3249.0011 |  | 262.365 |  |  |  | 2817.4753 |  | 182.4943
|  | 381 | 3253.4875 |  | 262.7272 |  |  |  | 3291.9212 |  | 213.2252
|  | 382 | 3257.9579 |  | 263.0882 |  |  |  | 2489.2303 |  | 161.2331
|  | 383 | 3258.2714 |  | 263.1136 |  |  |  | 1690.6962 |  | 109.5102
|  | 384 | 3256.1869 |  | 262.9452 |  |  |  | 894.5601 |  | 57.9427
|  | 385 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 386 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 387 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 388 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 389 | 3217.443 |  | 259.8166 |  |  |  | 0 |  | 0
|  | 390 | 3248.4914 |  | 262.3238 |  |  |  | 189.9973 |  | 12.3066
|  | 391 | 3248.9285 |  | 262.3591 |  |  |  | 410.6059 |  | 26.5959
|  | 392 | 3253.5143 |  | 262.7294 |  |  |  | 627.0658 |  | 40.6165
|  | 393 | 3253.9425 |  | 262.764 |  |  |  | 847.6833 |  | 54.9064
|  | 394 | 3251.9576 |  | 262.6037 |  |  |  | 1070.7139 |  | 69.3526
|  | 395 | 3249.9898 |  | 262.4448 |  |  |  | 1293.7273 |  | 83.7977
|  | 396 | 3248.0391 |  | 262.2873 |  |  |  | 1516.7238 |  | 98.2416
|  | 397 | 3246.1052 |  | 262.1311 |  |  |  | 1739.7033 |  | 112.6845
|  | 398 | 3244.1883 |  | 261.9763 |  |  |  | 1962.6659 |  | 127.1263
|  | 399 | 3242.2882 |  | 261.8229 |  |  |  | 2185.6118 |  | 141.567
|  | 400 | 3242.8174 |  | 261.8656 |  |  |  | 2025.4385 |  | 131.1922
|  | 401 | 3247.4871 |  | 262.2427 |  |  |  | 2308.1281 |  | 149.5027
|  | 402 | 3252.141 |  | 262.6185 |  |  |  | 2590.8336 |  | 167.8142
|  | 403 | 3256.7781 |  | 262.993 |  |  |  | 3128.9865 |  | 202.6715
|  | 404 | 3261.3972 |  | 263.366 |  |  |  | 3124.3675 |  | 202.3724
|  | 405 | 3265.9978 |  | 263.7375 |  |  |  | 3439.0551 |  | 222.7554
|  | 406 | 3270.5797 |  | 264.1075 |  |  |  | 2604.3238 |  | 168.688
|  | 407 | 3271.0084 |  | 264.1421 |  |  |  | 1773.7456 |  | 114.8895
|  | 408 | 3269.0569 |  | 263.9845 |  |  |  | 945.5478 |  | 61.2453
|  | 409 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 410 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 411 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 412 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 413 | 3192.8823 |  | 257.8332 |  |  |  | 0 |  | 0
|  | 414 | 3262.3117 |  | 263.4398 |  |  |  | 143.4294 |  | 9.2902
|  | 415 | 3262.8487 |  | 263.4832 |  |  |  | 355.7512 |  | 23.0428
|  | 416 | 3267.5234 |  | 263.8607 |  |  |  | 563.9354 |  | 36.5274
|  | 417 | 3272.1865 |  | 264.2372 |  |  |  | 772.1311 |  | 50.0127
|  | 418 | 3276.8374 |  | 264.6128 |  |  |  | 980.339 |  | 63.4988
|  | 419 | 3281.4754 |  | 264.9873 |  |  |  | 1188.5599 |  | 76.9857
|  | 420 | 3286.0998 |  | 265.3608 |  |  |  | 1396.7943 |  | 90.4735
|  | 421 | 3290.71 |  | 265.7331 |  |  |  | 1605.0429 |  | 103.9623
|  | 422 | 3295.3053 |  | 266.1041 |  |  |  | 1813.3064 |  | 117.452
|  | 423 | 3299.8853 |  | 266.474 |  |  |  | 1649.0823 |  | 106.8148
|  | 424 | 3304.45 |  | 266.8426 |  |  |  | 2017.0205 |  | 130.647
|  | 425 | 3308.9985 |  | 267.2099 |  |  |  | 2384.975 |  | 154.4802
|  | 426 | 3313.5297 |  | 267.5758 |  |  |  | 2752.9467 |  | 178.3146
|  | 427 | 3318.0429 |  | 267.9403 |  |  |  | 2309.4122 |  | 149.5859
|  | 428 | 3322.539 |  | 268.3033 |  |  |  | 1865.8948 |  | 120.8582
|  | 429 | 3327.0194 |  | 268.6651 |  |  |  | 1422.3931 |  | 92.1316
|  | 430 | 3331.4853 |  | 269.0258 |  |  |  | 978.9058 |  | 63.4059
|  | 431 | 3331.8063 |  | 269.0517 |  |  |  | 539.5635 |  | 34.9488
|  | 432 | 3192.8823 |  | 257.8332 |  |  |  | 0 |  | 0
|  | 433 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 434 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 435 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 436 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 437 | 3163.8561 |  | 255.4893 |  |  |  | 0 |  | 0
|  | 438 | 3323.7844 |  | 268.4039 |  |  |  | 43.2551 |  | 2.8017
|  | 439 | 3324.2047 |  | 268.4378 |  |  |  | 246.0183 |  | 15.9352
|  | 440 | 3328.7557 |  | 268.8053 |  |  |  | 444.6507 |  | 28.801
|  | 441 | 3333.2943 |  | 269.1718 |  |  |  | 643.2955 |  | 41.6677
|  | 442 | 3337.8198 |  | 269.5373 |  |  |  | 841.9534 |  | 54.5352
|  | 443 | 3342.3317 |  | 269.9016 |  |  |  | 1040.6249 |  | 67.4036
|  | 444 | 3346.8293 |  | 270.2648 |  |  |  | 1239.3108 |  | 80.273
|  | 445 | 3351.3119 |  | 270.6268 |  |  |  | 1438.0116 |  | 93.1433
|  | 446 | 3355.7792 |  | 270.9876 |  |  |  | 1342.3191 |  | 86.945
|  | 447 | 3360.2312 |  | 271.3471 |  |  |  | 1246.6419 |  | 80.7478
|  | 448 | 3364.6682 |  | 271.7054 |  |  |  | 1150.9797 |  | 74.5516
|  | 449 | 3369.0905 |  | 272.0625 |  |  |  | 1055.3322 |  | 68.3563
|  | 450 | 3373.4983 |  | 272.4184 |  |  |  | 959.6991 |  | 62.1619
|  | 451 | 3377.892 |  | 272.7732 |  |  |  | 864.0803 |  | 55.9684
|  | 452 | 3382.2718 |  | 273.1269 |  |  |  | 768.4753 |  | 49.7759
|  | 453 | 3386.6377 |  | 273.4795 |  |  |  | 1083.3975 |  | 70.1741
|  | 454 | 3390.9895 |  | 273.8309 |  |  |  | 600.1134 |  | 38.8707
|  | 455 | 3391.2013 |  | 273.848 |  |  |  | 120.9693 |  | 7.8355
|  | 456 | 3033.2382 |  | 244.9416 |  |  |  | 0 |  | 0
|  | 457 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 458 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 459 | 2736.7563 |  | 220.9999 |  |  |  | 0 |  | 0
|  | 460 | 2919.2067 |  | 235.7332 |  |  |  | 0 |  | 0
|  | 461 | 3101.6571 |  | 250.4666 |  |  |  | 0 |  | 0
|  | 462 | 3284.1075 |  | 265.1999 |  |  |  | 0 |  | 0
|  | 463 | 3384.5242 |  | 273.3088 |  |  |  | 82.0337 |  | 5.3135
|  | 464 | 3388.9432 |  | 273.6656 |  |  |  | 260.0651 |  | 16.845
|  | 465 | 3389.2264 |  | 273.6885 |  |  |  | 442.2324 |  | 28.6444
|  | 466 | 3387.1664 |  | 273.5222 |  |  |  | 626.7428 |  | 40.5955
|  | 467 | 3385.123 |  | 273.3571 |  |  |  | 811.2366 |  | 52.5456
|  | 468 | 3383.0962 |  | 273.1935 |  |  |  | 995.7139 |  | 64.4946
|  | 469 | 3381.0857 |  | 273.0311 |  |  |  | 1088.9495 |  | 70.5337
|  | 470 | 3379.0917 |  | 272.8701 |  |  |  | 1090.9436 |  | 70.6629
|  | 471 | 3377.1139 |  | 272.7104 |  |  |  | 1549.0474 |  | 100.3353
|  | 472 | 3377.4806 |  | 272.74 |  |  |  | 1731.1311 |  | 112.1293
|  | 473 | 3381.9567 |  | 273.1015 |  |  |  | 1471.2244 |  | 95.2945
|  | 474 | 3386.4156 |  | 273.4615 |  |  |  | 1211.335 |  | 78.4609
|  | 475 | 3390.8579 |  | 273.8202 |  |  |  | 1079.1774 |  | 69.9008
|  | 476 | 3395.2842 |  | 274.1777 |  |  |  | 691.6052 |  | 44.7968
|  | 477 | 3399.6956 |  | 274.5339 |  |  |  | 431.7632 |  | 27.9663
|  | 478 | 3404.0928 |  | 274.889 |  |  |  | 171.9354 |  | 11.1366
|  | 479 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 480 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 481 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 482 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 483 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 484 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 485 | 3033.2382 |  | 244.9416 |  |  |  | 0 |  | 0
|  | 486 | 3192.8823 |  | 257.8332 |  |  |  | 0 |  | 0
|  | 487 | 3352.5264 |  | 270.7249 |  |  |  | 0 |  | 0
|  | 488 | 3405.6189 |  | 275.0122 |  |  |  | 106.5516 |  | 6.9016
|  | 489 | 3405.9413 |  | 275.0383 |  |  |  | 265.8734 |  | 17.2212
|  | 490 | 3403.9746 |  | 274.8794 |  |  |  | 427.4842 |  | 27.6891
|  | 491 | 3402.0239 |  | 274.7219 |  |  |  | 589.079 |  | 38.156
|  | 492 | 3400.0892 |  | 274.5657 |  |  |  | 750.6578 |  | 48.6218
|  | 493 | 3398.1704 |  | 274.4108 |  |  |  | 912.2207 |  | 59.0866
|  | 494 | 3396.2675 |  | 274.2571 |  |  |  | 1073.7678 |  | 69.5504
|  | 495 | 3394.3804 |  | 274.1047 |  |  |  | 916.0108 |  | 59.3321
|  | 496 | 3394.7812 |  | 274.1371 |  |  |  | 1075.254 |  | 69.6466
|  | 497 | 3399.2687 |  | 274.4994 |  |  |  | 1709.3431 |  | 110.718
|  | 498 | 3403.7379 |  | 274.8603 |  |  |  | 1545.2297 |  | 100.088
|  | 499 | 3408.1891 |  | 275.2198 |  |  |  | 1860.0668 |  | 120.4807
|  | 500 | 3412.6219 |  | 275.5777 |  |  |  | 1504.4169 |  | 97.4445
|  | 501 | 3417.0373 |  | 275.9343 |  |  |  | 1148.7845 |  | 74.4094
|  | 502 | 3421.4364 |  | 276.2895 |  |  |  | 793.1682 |  | 51.3753
|  | 503 | 3421.7389 |  | 276.314 |  |  |  | 441.6487 |  | 28.6066
|  | 504 | 3419.7979 |  | 276.1572 |  |  |  | 92.3726 |  | 5.9832
|  | 505 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 506 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 507 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 508 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 509 | 3272.7044 |  | 264.2791 |  |  |  | 0 |  | 0
|  | 510 | 3414.884 |  | 275.7604 |  |  |  | 97.2866 |  | 6.3015
|  | 511 | 3415.2647 |  | 275.7912 |  |  |  | 336.3721 |  | 21.7876
|  | 512 | 3419.7217 |  | 276.1511 |  |  |  | 571.3812 |  | 37.0097
|  | 513 | 3420.0886 |  | 276.1807 |  |  |  | 810.4805 |  | 52.4967
|  | 514 | 3418.2245 |  | 276.0302 |  |  |  | 1051.8108 |  | 68.1282
|  | 515 | 3416.3759 |  | 275.8809 |  |  |  | 1293.1256 |  | 83.7587
|  | 516 | 3414.5426 |  | 275.7328 |  |  |  | 1534.425 |  | 99.3882
|  | 517 | 3412.7247 |  | 275.586 |  |  |  | 1775.709 |  | 115.0167
|  | 518 | 3410.9222 |  | 275.4405 |  |  |  | 2016.9778 |  | 130.6442
|  | 519 | 3409.1348 |  | 275.2962 |  |  |  | 1859.121 |  | 120.4195
|  | 520 | 3409.5766 |  | 275.3318 |  |  |  | 2071.538 |  | 134.1782
|  | 521 | 3414.0795 |  | 275.6954 |  |  |  | 2812.041 |  | 182.1423
|  | 522 | 3418.5632 |  | 276.0575 |  |  |  | 2647.9132 |  | 171.5113
|  | 523 | 3423.0278 |  | 276.418 |  |  |  | 2962.7368 |  | 191.9032
|  | 524 | 3427.4731 |  | 276.777 |  |  |  | 2639.0034 |  | 170.9342
|  | 525 | 3431.8994 |  | 277.1344 |  |  |  | 3113.5094 |  | 201.6691
|  | 526 | 3436.3065 |  | 277.4903 |  |  |  | 2310.8817 |  | 149.681
|  | 527 | 3436.6418 |  | 277.5174 |  |  |  | 1512.3258 |  | 97.9568
|  | 528 | 3434.7986 |  | 277.3686 |  |  |  | 715.9484 |  | 46.3736
|  | 529 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 530 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 531 | 2745.8788 |  | 221.7366 |  |  |  | 0 |  | 0
|  | 532 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 533 | 3170.076 |  | 255.9916 |  |  |  | 0 |  | 0
|  | 534 | 3375.3327 |  | 272.5666 |  |  |  | 0 |  | 0
|  | 535 | 3431.0453 |  | 277.0655 |  |  |  | 149.5441 |  | 9.6863
|  | 536 | 3435.5212 |  | 277.4269 |  |  |  | 350.325 |  | 22.6913
|  | 537 | 3435.9303 |  | 277.46 |  |  |  | 555.1726 |  | 35.9598
|  | 538 | 3434.1587 |  | 277.3169 |  |  |  | 762.2009 |  | 49.3695
|  | 539 | 3432.4021 |  | 277.175 |  |  |  | 969.2143 |  | 62.7782
|  | 540 | 3430.6603 |  | 277.0344 |  |  |  | 1176.2127 |  | 76.186
|  | 541 | 3428.9334 |  | 276.8949 |  |  |  | 1383.1964 |  | 89.5928
|  | 542 | 3427.2213 |  | 276.7567 |  |  |  | 1590.1652 |  | 102.9986
|  | 543 | 3425.5239 |  | 276.6196 |  |  |  | 1797.1193 |  | 116.4035
|  | 544 | 3426.0219 |  | 276.6598 |  |  |  | 2001.8781 |  | 129.6662
|  | 545 | 3430.57 |  | 277.0271 |  |  |  | 1837.6859 |  | 119.0311
|  | 546 | 3435.1034 |  | 277.3932 |  |  |  | 2152.4406 |  | 139.4185
|  | 547 | 3439.6218 |  | 277.758 |  |  |  | 2467.2105 |  | 159.8068
|  | 548 | 3444.1242 |  | 278.1216 |  |  |  | 2622.3522 |  | 169.8557
|  | 549 | 3448.6102 |  | 278.4839 |  |  |  | 3096.7986 |  | 200.5867
|  | 550 | 3453.0793 |  | 278.8448 |  |  |  | 2294.1089 |  | 148.5946
|  | 551 | 3453.4854 |  | 278.8776 |  |  |  | 1495.4822 |  | 96.8658
|  | 552 | 3451.7287 |  | 278.7357 |  |  |  | 699.0183 |  | 45.277
|  | 553 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 554 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 555 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 556 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 557 | 3217.443 |  | 259.8166 |  |  |  | 0 |  | 0
|  | 558 | 3438.4887 |  | 277.6665 |  |  |  | 0 |  | 0
|  | 559 | 3448.6547 |  | 278.4875 |  |  |  | 210.8796 |  | 13.6592
|  | 560 | 3453.2126 |  | 278.8555 |  |  |  | 427.3674 |  | 27.6816
|  | 561 | 3453.7047 |  | 278.8953 |  |  |  | 647.9211 |  | 41.9673
|  | 562 | 3452.0142 |  | 278.7588 |  |  |  | 870.6572 |  | 56.3944
|  | 563 | 3450.3383 |  | 278.6234 |  |  |  | 1093.3789 |  | 70.8206
|  | 564 | 3448.6767 |  | 278.4893 |  |  |  | 1316.0862 |  | 85.2459
|  | 565 | 3447.0295 |  | 278.3562 |  |  |  | 1538.7791 |  | 99.6702
|  | 566 | 3445.3965 |  | 278.2244 |  |  |  | 1761.4577 |  | 114.0936
|  | 567 | 3443.7778 |  | 278.0937 |  |  |  | 1984.1221 |  | 128.5161
|  | 568 | 3444.3665 |  | 278.1412 |  |  |  | 1823.8893 |  | 118.1374
|  | 569 | 3449.0121 |  | 278.5163 |  |  |  | 2106.6031 |  | 136.4495
|  | 570 | 3453.6445 |  | 278.8904 |  |  |  | 2389.3302 |  | 154.7623
|  | 571 | 3458.2628 |  | 279.2634 |  |  |  | 2927.5019 |  | 189.6209
|  | 572 | 3462.8659 |  | 279.6351 |  |  |  | 2922.8988 |  | 189.3228
|  | 573 | 3467.4535 |  | 280.0055 |  |  |  | 3237.5994 |  | 209.7066
|  | 574 | 3472.0257 |  | 280.3747 |  |  |  | 2402.8778 |  | 155.6398
|  | 575 | 3472.527 |  | 280.4152 |  |  |  | 1572.227 |  | 101.8367
|  | 576 | 3470.844 |  | 280.2793 |  |  |  | 743.7606 |  | 48.1751
|  | 577 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 578 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 579 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 580 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 581 | 3192.8823 |  | 257.8332 |  |  |  | 0 |  | 0
|  | 582 | 3405.7411 |  | 275.0221 |  |  |  | 0 |  | 0
|  | 583 | 3468.6394 |  | 280.1013 |  |  |  | 149.9606 |  | 9.7133
|  | 584 | 3473.3183 |  | 280.4791 |  |  |  | 358.1405 |  | 23.1976
|  | 585 | 3477.9904 |  | 280.8564 |  |  |  | 566.3272 |  | 36.6823
|  | 586 | 3482.6551 |  | 281.2331 |  |  |  | 774.5213 |  | 50.1675
|  | 587 | 3487.3121 |  | 281.6092 |  |  |  | 982.7232 |  | 63.6532
|  | 588 | 3491.9606 |  | 281.9845 |  |  |  | 1190.9335 |  | 77.1395
|  | 589 | 3496.6003 |  | 282.3592 |  |  |  | 1399.1526 |  | 90.6263
|  | 590 | 3501.2304 |  | 282.7331 |  |  |  | 1607.3813 |  | 104.1137
|  | 591 | 3505.8508 |  | 283.1062 |  |  |  | 1443.1168 |  | 93.4739
|  | 592 | 3510.4615 |  | 283.4785 |  |  |  | 1811.009 |  | 117.3032
|  | 593 | 3515.0619 |  | 283.85 |  |  |  | 2178.9116 |  | 141.133
|  | 594 | 3519.6508 |  | 284.2206 |  |  |  | 2546.8256 |  | 164.9637
|  | 595 | 3524.2278 |  | 284.5902 |  |  |  | 2103.2273 |  | 136.2308
|  | 596 | 3528.7938 |  | 284.9589 |  |  |  | 1659.64 |  | 107.4986
|  | 597 | 3533.3503 |  | 285.3269 |  |  |  | 1216.0622 |  | 78.7671
|  | 598 | 3537.8988 |  | 285.6942 |  |  |  | 772.4924 |  | 50.0361
|  | 599 | 3538.3447 |  | 285.7302 |  |  |  | 333.0251 |  | 21.5708
|  | 600 | 3192.8823 |  | 257.8332 |  |  |  | 0 |  | 0
|  | 601 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 602 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 603 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 604 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 605 | 3163.8561 |  | 255.4893 |  |  |  | 0 |  | 0
|  | 606 | 3367.0395 |  | 271.8969 |  |  |  | 0 |  | 0
|  | 607 | 3535.4216 |  | 285.4941 |  |  |  | 34.8014 |  | 2.2542
|  | 608 | 3540.1005 |  | 285.872 |  |  |  | 233.3059 |  | 15.1117
|  | 609 | 3544.7738 |  | 286.2493 |  |  |  | 431.816 |  | 27.9697
|  | 610 | 3549.4409 |  | 286.6262 |  |  |  | 630.3323 |  | 40.8281
|  | 611 | 3554.101 |  | 287.0025 |  |  |  | 828.8556 |  | 53.6869
|  | 612 | 3558.7536 |  | 287.3782 |  |  |  | 1027.3865 |  | 66.5462
|  | 613 | 3563.3978 |  | 287.7533 |  |  |  | 1225.9257 |  | 79.406
|  | 614 | 3568.0333 |  | 288.1276 |  |  |  | 1130.065 |  | 73.1969
|  | 615 | 3572.6601 |  | 288.5012 |  |  |  | 1034.213 |  | 66.9883
|  | 616 | 3577.2785 |  | 288.8742 |  |  |  | 938.3694 |  | 60.7803
|  | 617 | 3581.8886 |  | 289.2464 |  |  |  | 842.5341 |  | 54.5728
|  | 618 | 3586.4907 |  | 289.6181 |  |  |  | 746.7068 |  | 48.3659
|  | 619 | 3591.085 |  | 289.9891 |  |  |  | 650.8872 |  | 42.1594
|  | 620 | 3595.6718 |  | 290.3595 |  |  |  | 555.0752 |  | 35.9535
|  | 621 | 3600.251 |  | 290.7293 |  |  |  | 869.7842 |  | 56.3379
|  | 622 | 3604.8223 |  | 291.0984 |  |  |  | 386.2806 |  | 25.0203
|  | 623 | 3512.1706 |  | 283.6165 |  |  |  | 0 |  | 0
|  | 624 | 3033.2382 |  | 244.9416 |  |  |  | 0 |  | 0
|  | 625 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 626 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 627 | 2736.7563 |  | 220.9999 |  |  |  | 0 |  | 0
|  | 628 | 2919.2067 |  | 235.7332 |  |  |  | 0 |  | 0
|  | 629 | 3101.6571 |  | 250.4666 |  |  |  | 0 |  | 0
|  | 630 | 3284.1075 |  | 265.1999 |  |  |  | 0 |  | 0
|  | 631 | 3466.558 |  | 279.9332 |  |  |  | 0 |  | 0
|  | 632 | 3608.3644 |  | 291.3844 |  |  |  | 40.644 |  | 2.6326
|  | 633 | 3608.8739 |  | 291.4256 |  |  |  | 222.5849 |  | 14.4173
|  | 634 | 3606.9224 |  | 291.268 |  |  |  | 406.9868 |  | 26.3615
|  | 635 | 3604.9856 |  | 291.1116 |  |  |  | 591.374 |  | 38.3046
|  | 636 | 3603.0634 |  | 290.9564 |  |  |  | 775.7466 |  | 50.2469
|  | 637 | 3601.1558 |  | 290.8023 |  |  |  | 868.8794 |  | 56.2793
|  | 638 | 3599.2627 |  | 290.6495 |  |  |  | 870.7725 |  | 56.4019
|  | 639 | 3597.3841 |  | 290.4978 |  |  |  | 1328.7772 |  | 86.0679
|  | 640 | 3598.0094 |  | 290.5482 |  |  |  | 1510.6023 |  | 97.8451
|  | 641 | 3602.8035 |  | 290.9354 |  |  |  | 1250.3777 |  | 80.9898
|  | 642 | 3607.5854 |  | 291.3215 |  |  |  | 990.1651 |  | 64.1352
|  | 643 | 3612.3561 |  | 291.7068 |  |  |  | 857.6792 |  | 55.5538
|  | 644 | 3617.1158 |  | 292.0911 |  |  |  | 469.7735 |  | 30.4283
|  | 645 | 3621.8657 |  | 292.4747 |  |  |  | 209.5931 |  | 13.5758
|  | 646 | 3576.0282 |  | 288.7732 |  |  |  | 0 |  | 0
|  | 647 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 648 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 649 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 650 | 2554.3059 |  | 206.2666 |  |  |  | 0 |  | 0
|  | 651 | 2713.95 |  | 219.1582 |  |  |  | 0 |  | 0
|  | 652 | 2873.5941 |  | 232.0499 |  |  |  | 0 |  | 0
|  | 653 | 3033.2382 |  | 244.9416 |  |  |  | 0 |  | 0
|  | 654 | 3192.8823 |  | 257.8332 |  |  |  | 0 |  | 0
|  | 655 | 3352.5264 |  | 270.7249 |  |  |  | 0 |  | 0
|  | 656 | 3512.1706 |  | 283.6165 |  |  |  | 0 |  | 0
|  | 657 | 3635.162 |  | 293.5484 |  |  |  | 36.6527 |  | 2.3741
|  | 658 | 3633.226 |  | 293.3921 |  |  |  | 198.2328 |  | 12.84
|  | 659 | 3631.3044 |  | 293.2369 |  |  |  | 359.7985 |  | 23.305
|  | 660 | 3629.3973 |  | 293.0829 |  |  |  | 521.3498 |  | 33.769
|  | 661 | 3627.5044 |  | 292.93 |  |  |  | 682.8867 |  | 44.2321
|  | 662 | 3625.6259 |  | 292.7783 |  |  |  | 844.4094 |  | 54.6943
|  | 663 | 3623.7616 |  | 292.6278 |  |  |  | 686.6296 |  | 44.4746
|  | 664 | 3624.4788 |  | 292.6857 |  |  |  | 845.5564 |  | 54.7686
|  | 665 | 3629.3901 |  | 293.0823 |  |  |  | 1479.2216 |  | 95.8125
|  | 666 | 3634.2864 |  | 293.4777 |  |  |  | 1314.6812 |  | 85.1549
|  | 667 | 3639.1674 |  | 293.8719 |  |  |  | 1629.0885 |  | 105.5198
|  | 668 | 3644.0326 |  | 294.2647 |  |  |  | 1273.0061 |  | 82.4555
|  | 669 | 3648.8829 |  | 294.6564 |  |  |  | 916.9388 |  | 59.3922
|  | 670 | 3653.7193 |  | 295.047 |  |  |  | 560.8854 |  | 36.3298
|  | 671 | 3654.3441 |  | 295.0974 |  |  |  | 209.0435 |  | 13.5402
|  | 672 | 3512.1706 |  | 283.6165 |  |  |  | 0 |  | 0
Note on C8: Peter North: (Sat-Toutlet = 2 to 5K) Condenser refrig sat temp (30ºC) minus 2ºC approach temp. Needs to be written-up and justified. Sat temp - outlet temp btw 2 to 5K. 2K taken to max deltaT and min mass flowrate.
Note on C9: Peter North: (Toutlet - sat = 5K) Evaporator refrig sat temp (5ºC) plus 5K or 2K approach temp. Needs to be written-up and justified.

## Summer
T0 | K | 273
cp water | kJ/kg.K | 4.18
Tcond.sat | ºC | 30
T evap.sat | ºC | 5
Thot sink | ºC | 20 | 293 | K
Tcold sink | ºC | 10 | 283 | K | Approach Temp
Tcond.hot, out | ºC | 28 | 301 | K | 2 | K
Thp.hot, out | ºC | 10 | 283 | K | 5 | K
Tcond.cold, out | ºC | 28 | 301 | K | 5 | K
Thp.cold, out | ºC | 7 | 280 | K | 2 | K
Summer
|  |  | Hot Sink | [5 empty] | Cold Sink
|  |  | Condenser |  |  | HP Evaporator |  |  | Condenser |  |  | HP Evaporator
|  |  | Qcond, hot | ṁcond, hot | Edest cond, hot | Qhp, hot | ṁhp, hot | Edest hp, hot | Qcond, cold | ṁcond, cold | Edest cond, cold | Qhp, cold | ṁhp, cold | Edest hp, hot
|  |  | kW | kg/s | kW | kW | kg/s | kW | kW | kg/s | kW | kW | kg/s | kW
|  | Total | 1999013.7215 | 0 | 161425.3519 | 16 | 0 | 0 | 1028260.9548 | 0 | 66602.7916 | 36 | 0 | 0 | 228028.1435
[5 empty] | 70.79% | [5 empty] | 29.21%
Hours
|  | 1 | 2910.796 |  | 235.054 | 0.026938 |  |  | 0 |  | 0 | 1.0296
|  | 2 | 2739.5727 |  | 221.2273 | 8 |  |  | 0 |  | 0 | 18
|  | 3 | 2910.796 |  | 235.054 | 7.9731 |  |  | 0 |  | 0 | 16.9704
|  | 4 | 3082.0192 |  | 248.8808 |  |  |  | 0 |  | 0
|  | 5 | 3510.0775 |  | 283.4475 |  |  |  | 0 |  | 0
|  | 6 | 3720.8569 |  | 300.4685 |  |  |  | 46.0556 |  | 2.9831
|  | 7 | 3713.486 |  | 299.8733 |  |  |  | 310.2613 |  | 20.0963
|  | 8 | 3706.1516 |  | 299.281 |  |  |  | 574.4306 |  | 37.2072
|  | 9 | 3698.8536 |  | 298.6917 |  |  |  | 838.5636 |  | 54.3157
|  | 10 | 3691.5919 |  | 298.1053 |  |  |  | 1102.6603 |  | 71.4218
|  | 11 | 3684.3662 |  | 297.5218 |  |  |  | 1366.7209 |  | 88.5256
|  | 12 | 3677.1765 |  | 296.9412 |  |  |  | 1630.7455 |  | 105.6271
|  | 13 | 3670.0228 |  | 296.3635 |  |  |  | 1894.7342 |  | 122.7262
|  | 14 | 3662.9047 |  | 295.7887 |  |  |  | 2158.6872 |  | 139.8231
|  | 15 | 3655.8223 |  | 295.2168 |  |  |  | 1994.5463 |  | 129.1913
|  | 16 | 3648.7755 |  | 294.6477 |  |  |  | 2229.8909 |  | 144.4351
|  | 17 | 3642.5575 |  | 294.1456 |  |  |  | 3035.1509 |  | 196.5936
|  | 18 | 3636.4613 |  | 293.6533 |  |  |  | 2870.0238 |  | 185.8979
|  | 19 | 3630.3986 |  | 293.1638 |  |  |  | 3218.5331 |  | 208.4717
|  | 20 | 3624.3693 |  | 292.6769 |  |  |  | 2882.1158 |  | 186.6812
|  | 21 | 3618.3733 |  | 292.1927 |  |  |  | 3401.7817 |  | 220.3411
|  | 22 | 3612.4104 |  | 291.7112 |  |  |  | 2551.6281 |  | 165.2747
|  | 23 | 3605.9515 |  | 291.1896 |  |  |  | 1701.9705 |  | 110.2405
|  | 24 | 3599.1741 |  | 290.6423 |  |  |  | 852.6315 |  | 55.2269
|  | 25 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 26 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 27 | 2945.0406 |  | 237.8194 |  |  |  | 0 |  | 0
|  | 28 | 3082.0192 |  | 248.8808 |  |  |  | 0 |  | 0
|  | 29 | 3400.0054 |  | 274.5589 |  |  |  | 0 |  | 0
|  | 30 | 3565.0445 |  | 287.8863 |  |  |  | 55.1051 |  | 3.5693
|  | 31 | 3558.4792 |  | 287.3561 |  |  |  | 281.8146 |  | 18.2538
|  | 32 | 3551.9478 |  | 286.8287 |  |  |  | 508.4903 |  | 32.9361
|  | 33 | 3545.4499 |  | 286.3039 |  |  |  | 735.1324 |  | 47.6162
|  | 34 | 3538.9856 |  | 285.7819 |  |  |  | 961.7409 |  | 62.2941
|  | 35 | 3532.5547 |  | 285.2626 |  |  |  | 1188.316 |  | 76.9699
|  | 36 | 3526.1572 |  | 284.746 |  |  |  | 1414.8578 |  | 91.6435
|  | 37 | 3519.7928 |  | 284.2321 |  |  |  | 1641.3664 |  | 106.315
|  | 38 | 3513.4615 |  | 283.7208 |  |  |  | 1867.8419 |  | 120.9844
|  | 39 | 3507.1632 |  | 283.2122 |  |  |  | 2094.2845 |  | 135.6516
|  | 40 | 3500.8978 |  | 282.7062 |  |  |  | 2320.6941 |  | 150.3166
|  | 41 | 3494.9297 |  | 282.2243 |  |  |  | 2155.4389 |  | 139.6127
|  | 42 | 3489.6107 |  | 281.7948 |  |  |  | 2503.2045 |  | 162.1382
|  | 43 | 3484.3225 |  | 281.3677 |  |  |  | 2850.9393 |  | 184.6618
|  | 44 | 3479.0651 |  | 280.9432 |  |  |  | 3027.42 |  | 196.0929
|  | 45 | 3473.8383 |  | 280.5211 |  |  |  | 3546.3166 |  | 229.703
|  | 46 | 3468.6421 |  | 280.1015 |  |  |  | 2695.3964 |  | 174.5869
|  | 47 | 3463.4763 |  | 279.6844 |  |  |  | 1844.4457 |  | 119.4689
|  | 48 | 3458.2526 |  | 279.2625 |  |  |  | 993.5529 |  | 64.3547
|  | 49 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 50 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 51 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 52 | 3082.0192 |  | 248.8808 |  |  |  | 0 |  | 0
|  | 53 | 3432.9858 |  | 277.2222 |  |  |  | 17.8221 |  | 1.1544
|  | 54 | 3427.137 |  | 276.7499 |  |  |  | 260.7493 |  | 16.8893
|  | 55 | 3421.3195 |  | 276.2801 |  |  |  | 503.6451 |  | 32.6222
|  | 56 | 3416.3267 |  | 275.8769 |  |  |  | 745.7164 |  | 48.3017
|  | 57 | 3411.4516 |  | 275.4832 |  |  |  | 987.6699 |  | 63.9736
|  | 58 | 3406.6057 |  | 275.0919 |  |  |  | 1229.5942 |  | 79.6436
|  | 59 | 3401.7891 |  | 274.703 |  |  |  | 1471.4892 |  | 95.3117
|  | 60 | 3397.0016 |  | 274.3164 |  |  |  | 1713.3551 |  | 110.9779
|  | 61 | 3392.2431 |  | 273.9321 |  |  |  | 1955.192 |  | 126.6422
|  | 62 | 3387.5136 |  | 273.5502 |  |  |  | 2196.9999 |  | 142.3047
|  | 63 | 3382.8128 |  | 273.1706 |  |  |  | 2438.7791 |  | 157.9652
|  | 64 | 3377.2592 |  | 272.7221 |  |  |  | 2273.1094 |  | 147.2344
|  | 65 | 3371.7359 |  | 272.2761 |  |  |  | 2586.8346 |  | 167.5551
|  | 66 | 3366.2428 |  | 271.8325 |  |  |  | 2900.5297 |  | 187.8739
|  | 67 | 3360.7797 |  | 271.3914 |  |  |  | 3488.1519 |  | 225.9355
|  | 68 | 3355.3466 |  | 270.9526 |  |  |  | 3493.585 |  | 226.2874
|  | 69 | 3349.9434 |  | 270.5163 |  |  |  | 3841.4349 |  | 248.8184
|  | 70 | 3344.6581 |  | 270.0895 |  |  |  | 2956.359 |  | 191.4901
|  | 71 | 3340.1956 |  | 269.7291 |  |  |  | 2070.4604 |  | 134.1084
|  | 72 | 3335.761 |  | 269.371 |  |  |  | 1184.5339 |  | 76.7249
|  | 73 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 74 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 75 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 76 | 3082.0192 |  | 248.8808 |  |  |  | 0 |  | 0
|  | 77 | 3317.2726 |  | 267.878 |  |  |  | 107.1932 |  | 6.9431
|  | 78 | 3312.9881 |  | 267.5321 |  |  |  | 339.7754 |  | 22.008
|  | 79 | 3308.7309 |  | 267.1883 |  |  |  | 572.3304 |  | 37.0711
|  | 80 | 3304.5008 |  | 266.8467 |  |  |  | 804.8582 |  | 52.1325
|  | 81 | 3300.2977 |  | 266.5073 |  |  |  | 1037.359 |  | 67.1921
|  | 82 | 3296.1216 |  | 266.1701 |  |  |  | 1269.8328 |  | 82.2499
|  | 83 | 3291.9724 |  | 265.835 |  |  |  | 1502.2798 |  | 97.3061
|  | 84 | 3287.8499 |  | 265.5021 |  |  |  | 1734.7 |  | 112.3605
|  | 85 | 3283.754 |  | 265.1713 |  |  |  | 1967.0936 |  | 127.4131
|  | 86 | 3279.6847 |  | 264.8427 |  |  |  | 2199.4606 |  | 142.464
|  | 87 | 3275.6419 |  | 264.5163 |  |  |  | 2032.2802 |  | 131.6354
|  | 88 | 3271.6254 |  | 264.1919 |  |  |  | 2435.8176 |  | 157.7734
|  | 89 | 3267.6352 |  | 263.8697 |  |  |  | 2839.3289 |  | 183.9098
|  | 90 | 3263.6712 |  | 263.5496 |  |  |  | 3242.8139 |  | 210.0444
|  | 91 | 3259.7332 |  | 263.2316 |  |  |  | 2775.8878 |  | 179.8005
|  | 92 | 3255.8213 |  | 262.9157 |  |  |  | 2308.9357 |  | 149.555
|  | 93 | 3251.9352 |  | 262.6019 |  |  |  | 1841.9577 |  | 119.3078
|  | 94 | 3248.0749 |  | 262.2902 |  |  |  | 1374.954 |  | 89.0589
|  | 95 | 3244.2404 |  | 261.9805 |  |  |  | 907.9245 |  | 58.8083
|  | 96 | 3240.4314 |  | 261.6729 |  |  |  | 184.0344 |  | 11.9203
|  | 97 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 98 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 99 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 100 | 3082.0192 |  | 248.8808 |  |  |  | 0 |  | 0
|  | 101 | 3222.4692 |  | 260.2224 |  |  |  | 170.8651 |  | 11.0673
|  | 102 | 3217.922 |  | 259.8552 |  |  |  | 393.3329 |  | 25.4771
|  | 103 | 3213.4014 |  | 259.4902 |  |  |  | 615.7741 |  | 39.8851
|  | 104 | 3208.9074 |  | 259.1273 |  |  |  | 838.1886 |  | 54.2914
|  | 105 | 3204.4398 |  | 258.7665 |  |  |  | 1060.5767 |  | 68.696
|  | 106 | 3199.9987 |  | 258.4079 |  |  |  | 1282.9384 |  | 83.0988
|  | 107 | 3195.5838 |  | 258.0514 |  |  |  | 1505.2738 |  | 97.5
|  | 108 | 3191.7243 |  | 257.7397 |  |  |  | 1727.0539 |  | 111.8652
|  | 109 | 3188.2422 |  | 257.4585 |  |  |  | 1948.4565 |  | 126.2059
|  | 110 | 3184.7845 |  | 257.1793 |  |  |  | 1854.0724 |  | 120.0925
|  | 111 | 3181.3511 |  | 256.902 |  |  |  | 1759.6639 |  | 113.9774
|  | 112 | 3177.9418 |  | 256.6267 |  |  |  | 1665.2313 |  | 107.8608
|  | 113 | 3174.5566 |  | 256.3534 |  |  |  | 1570.7746 |  | 101.7426
|  | 114 | 3171.1954 |  | 256.0819 |  |  |  | 1476.294 |  | 95.6229
|  | 115 | 3167.8581 |  | 255.8125 |  |  |  | 1381.7894 |  | 89.5016
|  | 116 | 3164.5446 |  | 255.5449 |  |  |  | 1287.261 |  | 83.3788
|  | 117 | 3161.2548 |  | 255.2792 |  |  |  | 1632.9974 |  | 105.7729
|  | 118 | 3157.9887 |  | 255.0155 |  |  |  | 1122.5936 |  | 72.7129
|  | 119 | 3154.3933 |  | 254.7251 |  |  |  | 612.5191 |  | 39.6743
|  | 120 | 3150.2933 |  | 254.3941 |  |  |  | 102.9492 |  | 6.6683
|  | 121 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 122 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 123 | 2935.2564 |  | 237.0293 |  |  |  | 0 |  | 0
|  | 124 | 3130.9402 |  | 252.8312 |  |  |  | 0 |  | 0
|  | 125 | 3132.3349 |  | 252.9439 |  |  |  | 194.2891 |  | 12.5845
|  | 126 | 3128.3739 |  | 252.624 |  |  |  | 393.9339 |  | 25.516
|  | 127 | 3124.4374 |  | 252.3061 |  |  |  | 593.5541 |  | 38.4458
|  | 128 | 3120.5253 |  | 251.9902 |  |  |  | 793.1499 |  | 51.3741
|  | 129 | 3116.6377 |  | 251.6763 |  |  |  | 992.7213 |  | 64.3008
|  | 130 | 3112.7743 |  | 251.3643 |  |  |  | 1192.2685 |  | 77.2259
|  | 131 | 3108.9351 |  | 251.0543 |  |  |  | 1391.7914 |  | 90.1495
|  | 132 | 3105.12 |  | 250.7462 |  |  |  | 1591.2903 |  | 103.0715
|  | 133 | 3101.3289 |  | 250.4401 |  |  |  | 1692.9232 |  | 109.6545
|  | 134 | 3097.5618 |  | 250.1359 |  |  |  | 1696.6904 |  | 109.8985
|  | 135 | 3093.8185 |  | 249.8336 |  |  |  | 2189.6431 |  | 141.8281
|  | 136 | 3090.099 |  | 249.5332 |  |  |  | 2389.0463 |  | 154.7439
|  | 137 | 3086.4032 |  | 249.2348 |  |  |  | 2118.7849 |  | 137.2385
|  | 138 | 3082.7309 |  | 248.9382 |  |  |  | 1848.4999 |  | 119.7315
|  | 139 | 3079.435 |  | 248.6721 |  |  |  | 1714.8172 |  | 111.0726
|  | 140 | 3076.6905 |  | 248.4504 |  |  |  | 1306.6258 |  | 84.6331
|  | 141 | 3073.9677 |  | 248.2306 |  |  |  | 1035.3913 |  | 67.0646
|  | 142 | 3071.2665 |  | 248.0124 |  |  |  | 764.1353 |  | 49.4948
|  | 143 | 3068.5868 |  | 247.796 |  |  |  | 13.4325 |  | 0.87005
|  | 144 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 145 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 146 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 147 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 148 | 3057.5869 |  | 246.9078 |  |  |  | 24.4323 |  | 1.5825
|  | 149 | 3055.025 |  | 246.7009 |  |  |  | 198.2176 |  | 12.839
|  | 150 | 3052.484 |  | 246.4957 |  |  |  | 371.9818 |  | 24.0941
|  | 151 | 3049.9639 |  | 246.2922 |  |  |  | 545.7252 |  | 35.3479
|  | 152 | 3047.4646 |  | 246.0904 |  |  |  | 719.4478 |  | 46.6003
|  | 153 | 3044.9861 |  | 245.8902 |  |  |  | 893.1496 |  | 57.8513
|  | 154 | 3042.4399 |  | 245.6846 |  |  |  | 1066.9191 |  | 69.1068
|  | 155 | 3039.1213 |  | 245.4166 |  |  |  | 1241.461 |  | 80.4122
|  | 156 | 3035.8248 |  | 245.1504 |  |  |  | 1415.9808 |  | 91.7163
|  | 157 | 3032.5503 |  | 244.886 |  |  |  | 1590.4785 |  | 103.0189
|  | 158 | 3029.2979 |  | 244.6234 |  |  |  | 1764.9543 |  | 114.3201
|  | 159 | 3026.0674 |  | 244.3625 |  |  |  | 1596.9615 |  | 103.4388
|  | 160 | 3022.8587 |  | 244.1034 |  |  |  | 1771.3934 |  | 114.7372
|  | 161 | 3019.6718 |  | 243.846 |  |  |  | 2459.4735 |  | 159.3057
|  | 162 | 3016.5066 |  | 243.5904 |  |  |  | 2291.4154 |  | 148.4202
|  | 163 | 3013.363 |  | 243.3366 |  |  |  | 2637.0056 |  | 170.8048
|  | 164 | 3010.2409 |  | 243.0845 |  |  |  | 2263.4365 |  | 146.6079
|  | 165 | 3007.1403 |  | 242.8341 |  |  |  | 1889.8459 |  | 122.4096
|  | 166 | 3004.3256 |  | 242.6068 |  |  |  | 1515.9693 |  | 98.1928
|  | 167 | 3002.1486 |  | 242.431 |  |  |  | 1141.4551 |  | 73.9346
|  | 168 | 2999.9911 |  | 242.2568 |  |  |  | 766.9213 |  | 49.6752
|  | 169 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 170 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 171 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 172 | 2992.3725 |  | 241.6416 |  |  |  | 89.6468 |  | 5.8066
|  | 173 | 2990.3078 |  | 241.4748 |  |  |  | 519.7696 |  | 33.6667
|  | 174 | 2988.2623 |  | 241.3096 |  |  |  | 778.6501 |  | 50.4349
|  | 175 | 2986.2358 |  | 241.146 |  |  |  | 1037.5116 |  | 67.202
|  | 176 | 2984.2282 |  | 240.9839 |  |  |  | 1296.3541 |  | 83.9678
|  | 177 | 2982.2395 |  | 240.8233 |  |  |  | 1555.1777 |  | 100.7324
|  | 178 | 2980.2696 |  | 240.6642 |  |  |  | 1813.9826 |  | 117.4958
|  | 179 | 2978.3184 |  | 240.5067 |  |  |  | 2072.7687 |  | 134.2579
|  | 180 | 2976.3859 |  | 240.3506 |  |  |  | 2331.5362 |  | 151.0189
|  | 181 | 2974.472 |  | 240.196 |  |  |  | 2590.285 |  | 167.7786
|  | 182 | 2972.5765 |  | 240.043 |  |  |  | 2849.0154 |  | 184.5372
|  | 183 | 2970.6995 |  | 239.8914 |  |  |  | 2679.6691 |  | 173.5682
|  | 184 | 2968.8409 |  | 239.7413 |  |  |  | 2909.8254 |  | 188.476
|  | 185 | 2967.0006 |  | 239.5927 |  |  |  | 3710.7078 |  | 240.351
|  | 186 | 2965.1784 |  | 239.4456 |  |  |  | 3541.3066 |  | 229.3785
|  | 187 | 2963.3745 |  | 239.2999 |  |  |  | 3885.5572 |  | 251.6763
|  | 188 | 2961.5886 |  | 239.1557 |  |  |  | 3544.8965 |  | 229.611
|  | 189 | 2959.8207 |  | 239.0129 |  |  |  | 4060.3343 |  | 262.9971
|  | 190 | 2958.0707 |  | 238.8716 |  |  |  | 3205.9678 |  | 207.6578
|  | 191 | 2956.3386 |  | 238.7317 |  |  |  | 2351.5835 |  | 152.3174
|  | 192 | 2954.6243 |  | 238.5933 |  |  |  | 1497.1813 |  | 96.9758
|  | 193 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 194 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 195 | 2945.0406 |  | 237.8194 |  |  |  | 0 |  | 0
|  | 196 | 2948.4698 |  | 238.0963 |  |  |  | 133.5494 |  | 8.6503
|  | 197 | 2946.8409 |  | 237.9648 |  |  |  | 453.1644 |  | 29.3525
|  | 198 | 2945.2295 |  | 237.8346 |  |  |  | 674.9201 |  | 43.7161
|  | 199 | 2943.6353 |  | 237.7059 |  |  |  | 896.6585 |  | 58.0786
|  | 200 | 2942.0584 |  | 237.5786 |  |  |  | 1118.3797 |  | 72.44
|  | 201 | 2940.4986 |  | 237.4526 |  |  |  | 1340.0837 |  | 86.8003
|  | 202 | 2938.9559 |  | 237.328 |  |  |  | 1561.7706 |  | 101.1594
|  | 203 | 2937.4303 |  | 237.2048 |  |  |  | 1783.4404 |  | 115.5175
|  | 204 | 2935.9216 |  | 237.083 |  |  |  | 2005.0933 |  | 129.8744
|  | 205 | 2934.4299 |  | 236.9625 |  |  |  | 2226.7294 |  | 144.2303
|  | 206 | 2932.9549 |  | 236.8434 |  |  |  | 2448.3485 |  | 158.5851
|  | 207 | 2931.4967 |  | 236.7257 |  |  |  | 2669.951 |  | 172.9388
|  | 208 | 2930.0552 |  | 236.6093 |  |  |  | 2891.5367 |  | 187.2914
|  | 209 | 2928.6303 |  | 236.4942 |  |  |  | 2721.7383 |  | 176.2932
|  | 210 | 2927.222 |  | 236.3805 |  |  |  | 3065.5932 |  | 198.5654
|  | 211 | 2925.8302 |  | 236.2681 |  |  |  | 3409.4316 |  | 220.8366
|  | 212 | 2924.4548 |  | 236.157 |  |  |  | 3582.0303 |  | 232.0162
|  | 213 | 2923.0957 |  | 236.0473 |  |  |  | 4097.0593 |  | 265.3758
|  | 214 | 2921.7529 |  | 235.9388 |  |  |  | 3242.2856 |  | 210.0102
|  | 215 | 2920.4264 |  | 235.8317 |  |  |  | 2387.4957 |  | 154.6435
|  | 216 | 2919.116 |  | 235.7259 |  |  |  | 1532.6896 |  | 99.2758
|  | 217 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 218 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 219 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 220 | 2914.4433 |  | 235.3486 |  |  |  | 167.576 |  | 10.8543
|  | 221 | 2913.2108 |  | 235.249 |  |  |  | 537.5971 |  | 34.8214
|  | 222 | 2911.9941 |  | 235.1508 |  |  |  | 775.8922 |  | 50.2563
|  | 223 | 2910.7931 |  | 235.0538 |  |  |  | 1014.1716 |  | 65.6902
|  | 224 | 2909.6078 |  | 234.9581 |  |  |  | 1252.4353 |  | 81.1231
|  | 225 | 2908.438 |  | 234.8636 |  |  |  | 1490.6835 |  | 96.5549
|  | 226 | 2907.2837 |  | 234.7704 |  |  |  | 1728.9162 |  | 111.9858
|  | 227 | 2906.1449 |  | 234.6785 |  |  |  | 1967.1334 |  | 127.4157
|  | 228 | 2905.0215 |  | 234.5877 |  |  |  | 2205.3352 |  | 142.8446
|  | 229 | 2903.9134 |  | 234.4983 |  |  |  | 2443.5217 |  | 158.2724
|  | 230 | 2902.8206 |  | 234.41 |  |  |  | 2681.693 |  | 173.6993
|  | 231 | 2901.7429 |  | 234.323 |  |  |  | 2919.849 |  | 189.1252
|  | 232 | 2900.6804 |  | 234.2372 |  |  |  | 2749.6882 |  | 178.1035
|  | 233 | 2899.633 |  | 234.1526 |  |  |  | 3058.9376 |  | 198.1343
|  | 234 | 2898.6005 |  | 234.0692 |  |  |  | 3368.1719 |  | 218.1641
|  | 235 | 2897.5831 |  | 233.9871 |  |  |  | 3951.3486 |  | 255.9378
|  | 236 | 2896.5805 |  | 233.9061 |  |  |  | 3952.3512 |  | 256.0027
|  | 237 | 2895.5927 |  | 233.8263 |  |  |  | 4295.7856 |  | 278.2478
|  | 238 | 2894.6197 |  | 233.7478 |  |  |  | 3406.3975 |  | 220.6401
|  | 239 | 2893.6613 |  | 233.6704 |  |  |  | 2516.9947 |  | 163.0314
|  | 240 | 2892.7177 |  | 233.5942 |  |  |  | 1627.5772 |  | 105.4219
|  | 241 | 2891.7886 |  | 233.5192 |  |  |  | 19.0074 |  | 1.2312
|  | 242 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 243 | 2888.5091 |  | 233.2543 |  |  |  | 22.2869 |  | 1.4436
|  | 244 | 2886.7438 |  | 233.1118 |  |  |  | 195.2755 |  | 12.6484
|  | 245 | 2884.9945 |  | 232.9705 |  |  |  | 539.4713 |  | 34.9428
|  | 246 | 2883.2612 |  | 232.8305 |  |  |  | 769.5024 |  | 49.8424
|  | 247 | 2881.5437 |  | 232.6919 |  |  |  | 999.5175 |  | 64.741
|  | 248 | 2879.8421 |  | 232.5544 |  |  |  | 1229.5169 |  | 79.6386
|  | 249 | 2878.1562 |  | 232.4183 |  |  |  | 1459.5005 |  | 94.5352
|  | 250 | 2876.486 |  | 232.2834 |  |  |  | 1689.4684 |  | 109.4307
|  | 251 | 2874.8315 |  | 232.1498 |  |  |  | 1919.4207 |  | 124.3252
|  | 252 | 2873.1925 |  | 232.0175 |  |  |  | 2149.3574 |  | 139.2187
|  | 253 | 2871.569 |  | 231.8864 |  |  |  | 2379.2786 |  | 154.1113
|  | 254 | 2869.961 |  | 231.7565 |  |  |  | 2609.1843 |  | 169.0028
|  | 255 | 2868.3684 |  | 231.6279 |  |  |  | 2439.5537 |  | 158.0154
|  | 256 | 2866.7911 |  | 231.5005 |  |  |  | 2840.652 |  | 183.9955
|  | 257 | 2865.229 |  | 231.3744 |  |  |  | 3241.735 |  | 209.9745
|  | 258 | 2863.6822 |  | 231.2495 |  |  |  | 3642.8029 |  | 235.9526
|  | 259 | 2862.1505 |  | 231.1258 |  |  |  | 3173.4705 |  | 205.5529
|  | 260 | 2860.6339 |  | 231.0033 |  |  |  | 2704.123 |  | 175.1522
|  | 261 | 2859.1324 |  | 230.8821 |  |  |  | 2234.7606 |  | 144.7505
|  | 262 | 2857.6458 |  | 230.762 |  |  |  | 1765.3831 |  | 114.3479
|  | 263 | 2856.1741 |  | 230.6432 |  |  |  | 1295.9907 |  | 83.9443
|  | 264 | 2854.7172 |  | 230.5255 |  |  |  | 569.7486 |  | 36.9039
|  | 265 | 2853.2752 |  | 230.4091 |  |  |  | 57.5208 |  | 3.7257
|  | 266 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 267 | 2850.6004 |  | 230.1931 |  |  |  | 60.1955 |  | 3.899
|  | 268 | 2849.2017 |  | 230.0802 |  |  |  | 232.8176 |  | 15.0801
|  | 269 | 2847.8174 |  | 229.9684 |  |  |  | 545.5169 |  | 35.3344
|  | 270 | 2846.4477 |  | 229.8578 |  |  |  | 764.8072 |  | 49.5383
|  | 271 | 2845.0924 |  | 229.7483 |  |  |  | 984.083 |  | 63.7413
|  | 272 | 2843.7516 |  | 229.64 |  |  |  | 1203.3444 |  | 77.9433
|  | 273 | 2842.425 |  | 229.5329 |  |  |  | 1422.5915 |  | 92.1445
|  | 274 | 2841.1127 |  | 229.4269 |  |  |  | 1641.8244 |  | 106.3447
|  | 275 | 2839.8146 |  | 229.3221 |  |  |  | 1861.043 |  | 120.544
|  | 276 | 2838.5307 |  | 229.2184 |  |  |  | 2080.2475 |  | 134.7423
|  | 277 | 2837.2609 |  | 229.1159 |  |  |  | 2299.4378 |  | 148.9398
|  | 278 | 2836.0051 |  | 229.0145 |  |  |  | 2202.8517 |  | 142.6837
|  | 279 | 2834.7634 |  | 228.9142 |  |  |  | 2106.2516 |  | 136.4267
|  | 280 | 2833.5355 |  | 228.8151 |  |  |  | 2009.6376 |  | 130.1688
|  | 281 | 2832.3215 |  | 228.717 |  |  |  | 1913.0097 |  | 123.91
|  | 282 | 2831.1214 |  | 228.6201 |  |  |  | 1816.368 |  | 117.6503
|  | 283 | 2829.935 |  | 228.5243 |  |  |  | 1719.7125 |  | 111.3897
|  | 284 | 2828.7623 |  | 228.4296 |  |  |  | 1623.0433 |  | 105.1282
|  | 285 | 2827.6033 |  | 228.336 |  |  |  | 1966.6489 |  | 127.3843
|  | 286 | 2826.4579 |  | 228.2435 |  |  |  | 1454.1244 |  | 94.1869
|  | 287 | 2825.326 |  | 228.1521 |  |  |  | 941.5864 |  | 60.9887
|  | 288 | 2824.2076 |  | 228.0618 |  |  |  | 429.035 |  | 27.7896
|  | 289 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 290 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 291 | 2821.1725 |  | 227.8167 |  |  |  | 114.084 |  | 7.3895
|  | 292 | 2820.1064 |  | 227.7306 |  |  |  | 310.8338 |  | 20.1334
|  | 293 | 2819.0535 |  | 227.6456 |  |  |  | 507.5705 |  | 32.8765
|  | 294 | 2818.0138 |  | 227.5617 |  |  |  | 704.2939 |  | 45.6187
|  | 295 | 2816.9872 |  | 227.4788 |  |  |  | 901.0043 |  | 58.3601
|  | 296 | 2816.4146 |  | 227.4325 |  |  |  | 1097.2606 |  | 71.0721
|  | 297 | 2816.2947 |  | 227.4228 |  |  |  | 1293.0643 |  | 83.7547
|  | 298 | 2816.1861 |  | 227.4141 |  |  |  | 1488.8566 |  | 96.4366
|  | 299 | 2816.0888 |  | 227.4062 |  |  |  | 1684.6377 |  | 109.1178
|  | 300 | 2816.0026 |  | 227.3992 |  |  |  | 1880.4077 |  | 121.7983
|  | 301 | 2815.9276 |  | 227.3932 |  |  |  | 1978.3246 |  | 128.1406
|  | 302 | 2815.8636 |  | 227.388 |  |  |  | 1978.3886 |  | 128.1447
|  | 303 | 2815.8107 |  | 227.3837 |  |  |  | 2467.6509 |  | 159.8353
|  | 304 | 2815.7687 |  | 227.3804 |  |  |  | 2663.3766 |  | 172.5129
|  | 305 | 2815.7377 |  | 227.3779 |  |  |  | 2389.4504 |  | 154.7701
|  | 306 | 2815.7175 |  | 227.3762 |  |  |  | 2115.5133 |  | 137.0266
|  | 307 | 2815.7082 |  | 227.3755 |  |  |  | 1978.5439 |  | 128.1548
|  | 308 | 2815.7097 |  | 227.3756 |  |  |  | 1567.6066 |  | 101.5374
|  | 309 | 2815.7219 |  | 227.3766 |  |  |  | 1293.6371 |  | 83.7918
|  | 310 | 2815.7447 |  | 227.3784 |  |  |  | 1019.657 |  | 66.0455
|  | 311 | 2815.7782 |  | 227.3811 |  |  |  | 266.241 |  | 17.245
|  | 312 | 2815.8223 |  | 227.3847 |  |  |  | 94.9736 |  | 6.1517
|  | 313 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 314 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 315 | 2816.2648 |  | 227.4204 |  |  |  | 94.5311 |  | 6.123
|  | 316 | 2816.3496 |  | 227.4273 |  |  |  | 265.6696 |  | 17.208
|  | 317 | 2816.4447 |  | 227.4349 |  |  |  | 436.7978 |  | 28.2924
|  | 318 | 2816.5502 |  | 227.4435 |  |  |  | 607.9157 |  | 39.3761
|  | 319 | 2816.6658 |  | 227.4528 |  |  |  | 779.0233 |  | 50.4591
|  | 320 | 2816.7917 |  | 227.463 |  |  |  | 950.1207 |  | 61.5415
|  | 321 | 2816.9278 |  | 227.474 |  |  |  | 1121.208 |  | 72.6232
|  | 322 | 2817.0739 |  | 227.4858 |  |  |  | 1292.2851 |  | 83.7042
|  | 323 | 2817.2301 |  | 227.4984 |  |  |  | 1463.3522 |  | 94.7846
|  | 324 | 2817.3963 |  | 227.5118 |  |  |  | 1634.4093 |  | 105.8644
|  | 325 | 2817.5725 |  | 227.526 |  |  |  | 1805.4564 |  | 116.9435
|  | 326 | 2817.7585 |  | 227.541 |  |  |  | 1976.4936 |  | 128.022
|  | 327 | 2817.9545 |  | 227.5569 |  |  |  | 1805.0744 |  | 116.9188
|  | 328 | 2818.1603 |  | 227.5735 |  |  |  | 1976.0919 |  | 127.9959
|  | 329 | 2818.3758 |  | 227.5909 |  |  |  | 2660.7695 |  | 172.3441
|  | 330 | 2818.6011 |  | 227.6091 |  |  |  | 2489.3209 |  | 161.239
|  | 331 | 2818.8361 |  | 227.6281 |  |  |  | 2831.5325 |  | 183.4048
|  | 332 | 2819.0807 |  | 227.6478 |  |  |  | 2454.5967 |  | 158.9898
|  | 333 | 2819.3349 |  | 227.6683 |  |  |  | 2077.6512 |  | 134.5742
|  | 334 | 2819.5987 |  | 227.6896 |  |  |  | 1700.6962 |  | 110.1579
|  | 335 | 2819.8719 |  | 227.7117 |  |  |  | 1323.7317 |  | 85.7411
|  | 336 | 2820.1547 |  | 227.7345 |  |  |  | 946.7578 |  | 61.3236
|  | 337 | 2820.4468 |  | 227.7581 |  |  |  | 90.3492 |  | 5.8521
|  | 338 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 339 | 2821.1453 |  | 227.8145 |  |  |  | 89.6507 |  | 5.8069
|  | 340 | 2821.465 |  | 227.8403 |  |  |  | 260.5543 |  | 16.8767
|  | 341 | 2821.7939 |  | 227.8669 |  |  |  | 688.2836 |  | 44.5817
|  | 342 | 2822.1321 |  | 227.8942 |  |  |  | 944.7804 |  | 61.1956
|  | 343 | 2822.4793 |  | 227.9223 |  |  |  | 1201.268 |  | 77.8089
|  | 344 | 2822.8357 |  | 227.951 |  |  |  | 1457.7466 |  | 94.4215
|  | 345 | 2823.2011 |  | 227.9805 |  |  |  | 1714.2161 |  | 111.0337
|  | 346 | 2823.5756 |  | 228.0108 |  |  |  | 1970.6766 |  | 127.6452
|  | 347 | 2823.959 |  | 228.0417 |  |  |  | 2227.1281 |  | 144.2561
|  | 348 | 2824.3513 |  | 228.0734 |  |  |  | 2483.5707 |  | 160.8665
|  | 349 | 2824.7525 |  | 228.1058 |  |  |  | 2740.0044 |  | 177.4763
|  | 350 | 2825.1626 |  | 228.1389 |  |  |  | 2996.4293 |  | 194.0855
|  | 351 | 2825.5815 |  | 228.1728 |  |  |  | 2824.7872 |  | 182.9679
|  | 352 | 2826.0091 |  | 228.2073 |  |  |  | 3052.6573 |  | 197.7275
|  | 353 | 2826.4454 |  | 228.2425 |  |  |  | 3851.263 |  | 249.455
|  | 354 | 2826.8904 |  | 228.2785 |  |  |  | 3679.5947 |  | 238.3357
|  | 355 | 2827.344 |  | 228.3151 |  |  |  | 4021.5877 |  | 260.4873
|  | 356 | 2827.8062 |  | 228.3524 |  |  |  | 3678.6789 |  | 238.2764
|  | 357 | 2828.2769 |  | 228.3904 |  |  |  | 4191.878 |  | 271.5174
|  | 358 | 2828.7562 |  | 228.4291 |  |  |  | 3335.2823 |  | 216.0338
|  | 359 | 2829.2439 |  | 228.4685 |  |  |  | 2478.6782 |  | 160.5496
|  | 360 | 2829.74 |  | 228.5086 |  |  |  | 1622.0656 |  | 105.0649
|  | 361 | 2830.2445 |  | 228.5493 |  |  |  | 80.5515 |  | 5.2175
|  | 362 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 363 | 2831.3782 |  | 228.6409 |  |  |  | 113.6624 |  | 7.3622
|  | 364 | 2831.9071 |  | 228.6836 |  |  |  | 250.1122 |  | 16.2003
|  | 365 | 2832.4442 |  | 228.7269 |  |  |  | 567.5612 |  | 36.7622
|  | 366 | 2832.9895 |  | 228.771 |  |  |  | 787.1601 |  | 50.9861
|  | 367 | 2833.5429 |  | 228.8157 |  |  |  | 1006.751 |  | 65.2095
|  | 368 | 2834.1044 |  | 228.861 |  |  |  | 1226.3337 |  | 79.4324
|  | 369 | 2834.6739 |  | 228.907 |  |  |  | 1445.9084 |  | 93.6548
|  | 370 | 2835.2514 |  | 228.9536 |  |  |  | 1665.4751 |  | 107.8766
|  | 371 | 2835.8369 |  | 229.0009 |  |  |  | 1885.0338 |  | 122.0979
|  | 372 | 2836.4304 |  | 229.0488 |  |  |  | 2104.5846 |  | 136.3187
|  | 373 | 2837.0317 |  | 229.0974 |  |  |  | 2324.1275 |  | 150.539
|  | 374 | 2837.6408 |  | 229.1466 |  |  |  | 2543.6626 |  | 164.7588
|  | 375 | 2838.2578 |  | 229.1964 |  |  |  | 2763.1899 |  | 178.9781
|  | 376 | 2838.8825 |  | 229.2469 |  |  |  | 2982.7094 |  | 193.1968
|  | 377 | 2839.515 |  | 229.2979 |  |  |  | 2810.8536 |  | 182.0654
|  | 378 | 2840.1551 |  | 229.3496 |  |  |  | 3152.6601 |  | 204.2049
|  | 379 | 2840.8029 |  | 229.4019 |  |  |  | 3494.4589 |  | 226.344
|  | 380 | 2841.4583 |  | 229.4549 |  |  |  | 3665.0267 |  | 237.3921
|  | 381 | 2842.1213 |  | 229.5084 |  |  |  | 4178.0337 |  | 270.6207
|  | 382 | 2842.7918 |  | 229.5625 |  |  |  | 3321.2467 |  | 215.1247
|  | 383 | 2843.4698 |  | 229.6173 |  |  |  | 2464.4523 |  | 159.6282
|  | 384 | 2844.1552 |  | 229.6726 |  |  |  | 1607.6504 |  | 104.1312
|  | 385 | 2844.8481 |  | 229.7286 |  |  |  | 65.9479 |  | 4.2716
|  | 386 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 387 | 2846.4029 |  | 229.8541 |  |  |  | 64.393 |  | 4.1709
|  | 388 | 2847.1171 |  | 229.9118 |  |  |  | 234.9021 |  | 15.2151
|  | 389 | 2847.8386 |  | 229.9701 |  |  |  | 602.9693 |  | 39.0557
|  | 390 | 2848.5673 |  | 230.0289 |  |  |  | 839.319 |  | 54.3646
|  | 391 | 2849.3031 |  | 230.0883 |  |  |  | 1075.6615 |  | 69.673
|  | 392 | 2850.0462 |  | 230.1483 |  |  |  | 1311.9969 |  | 84.981
|  | 393 | 2850.7963 |  | 230.2089 |  |  |  | 1548.3252 |  | 100.2885
|  | 394 | 2851.5535 |  | 230.2701 |  |  |  | 1784.6464 |  | 115.5956
|  | 395 | 2852.3178 |  | 230.3318 |  |  |  | 2020.9605 |  | 130.9022
|  | 396 | 2853.089 |  | 230.3941 |  |  |  | 2257.2677 |  | 146.2083
|  | 397 | 2853.8672 |  | 230.4569 |  |  |  | 2493.5679 |  | 161.514
|  | 398 | 2854.0351 |  | 230.4705 |  |  |  | 2730.4784 |  | 176.8593
|  | 399 | 2853.9468 |  | 230.4633 |  |  |  | 2967.6451 |  | 192.2211
|  | 400 | 2853.867 |  | 230.4569 |  |  |  | 2796.5016 |  | 181.1357
|  | 401 | 2853.7957 |  | 230.4511 |  |  |  | 3104.7748 |  | 201.1033
|  | 402 | 2853.7329 |  | 230.4461 |  |  |  | 3413.0396 |  | 221.0703
|  | 403 | 2853.6784 |  | 230.4417 |  |  |  | 3995.2533 |  | 258.7816
|  | 404 | 2853.6323 |  | 230.4379 |  |  |  | 3995.2993 |  | 258.7846
|  | 405 | 2853.5946 |  | 230.4349 |  |  |  | 4337.7837 |  | 280.9681
|  | 406 | 2853.5651 |  | 230.4325 |  |  |  | 3447.452 |  | 223.2993
|  | 407 | 2853.5439 |  | 230.4308 |  |  |  | 2557.1121 |  | 165.6299
|  | 408 | 2853.5309 |  | 230.4298 |  |  |  | 1666.764 |  | 107.9601
|  | 409 | 2853.5261 |  | 230.4294 |  |  |  | 57.2698 |  | 3.7095
|  | 410 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 411 | 2853.711 |  | 230.4443 |  |  |  | 57.085 |  | 3.6975
|  | 412 | 2853.7297 |  | 230.4458 |  |  |  | 228.2895 |  | 14.7868
|  | 413 | 2853.7565 |  | 230.448 |  |  |  | 570.7094 |  | 36.9661
|  | 414 | 2853.7912 |  | 230.4508 |  |  |  | 798.9723 |  | 51.7512
|  | 415 | 2853.8339 |  | 230.4542 |  |  |  | 1027.2274 |  | 66.5358
|  | 416 | 2853.8846 |  | 230.4583 |  |  |  | 1255.4744 |  | 81.3199
|  | 417 | 2853.9431 |  | 230.463 |  |  |  | 1483.7137 |  | 96.1035
|  | 418 | 2854.0094 |  | 230.4684 |  |  |  | 1711.945 |  | 110.8866
|  | 419 | 2854.0836 |  | 230.4744 |  |  |  | 1940.1686 |  | 125.6691
|  | 420 | 2854.1656 |  | 230.481 |  |  |  | 2168.3843 |  | 140.4512
|  | 421 | 2854.2553 |  | 230.4882 |  |  |  | 2396.5924 |  | 155.2327
|  | 422 | 2854.3527 |  | 230.4961 |  |  |  | 2624.7927 |  | 170.0138
|  | 423 | 2854.4577 |  | 230.5046 |  |  |  | 2453.4643 |  | 158.9164
|  | 424 | 2854.5704 |  | 230.5137 |  |  |  | 2852.8726 |  | 184.787
|  | 425 | 2854.6907 |  | 230.5234 |  |  |  | 3252.2734 |  | 210.6571
|  | 426 | 2854.8186 |  | 230.5337 |  |  |  | 3651.6665 |  | 236.5267
|  | 427 | 2854.954 |  | 230.5447 |  |  |  | 3180.6671 |  | 206.019
|  | 428 | 2855.0968 |  | 230.5562 |  |  |  | 2709.6602 |  | 175.5108
|  | 429 | 2855.2472 |  | 230.5683 |  |  |  | 2238.6458 |  | 145.0022
|  | 430 | 2855.4049 |  | 230.5811 |  |  |  | 1767.624 |  | 114.493
|  | 431 | 2855.57 |  | 230.5944 |  |  |  | 1296.5948 |  | 83.9834
|  | 432 | 2855.7425 |  | 230.6083 |  |  |  | 568.7233 |  | 36.8375
|  | 433 | 2855.9223 |  | 230.6229 |  |  |  | 54.8737 |  | 3.5543
|  | 434 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 435 | 2856.4816 |  | 230.668 |  |  |  | 54.3144 |  | 3.5181
|  | 436 | 2856.6823 |  | 230.6842 |  |  |  | 225.337 |  | 14.5956
|  | 437 | 2856.8902 |  | 230.701 |  |  |  | 536.4442 |  | 34.7467
|  | 438 | 2857.1052 |  | 230.7184 |  |  |  | 754.1497 |  | 48.848
|  | 439 | 2857.3274 |  | 230.7363 |  |  |  | 971.8481 |  | 62.9488
|  | 440 | 2857.5566 |  | 230.7548 |  |  |  | 1189.5394 |  | 77.0492
|  | 441 | 2857.7929 |  | 230.7739 |  |  |  | 1407.2237 |  | 91.1491
|  | 442 | 2858.0361 |  | 230.7936 |  |  |  | 1624.901 |  | 105.2485
|  | 443 | 2858.2864 |  | 230.8138 |  |  |  | 1842.5712 |  | 119.3475
|  | 444 | 2858.5436 |  | 230.8345 |  |  |  | 2060.2346 |  | 133.4461
|  | 445 | 2858.8077 |  | 230.8559 |  |  |  | 2277.891 |  | 147.5442
|  | 446 | 2859.0787 |  | 230.8777 |  |  |  | 2179.7782 |  | 141.1892
|  | 447 | 2859.3565 |  | 230.9002 |  |  |  | 2081.6585 |  | 134.8337
|  | 448 | 2859.6412 |  | 230.9232 |  |  |  | 1983.532 |  | 128.4779
|  | 449 | 2859.9326 |  | 230.9467 |  |  |  | 1885.3987 |  | 122.1215
|  | 450 | 2860.2307 |  | 230.9708 |  |  |  | 1787.2586 |  | 115.7648
|  | 451 | 2860.5356 |  | 230.9954 |  |  |  | 1689.1119 |  | 109.4076
|  | 452 | 2860.8471 |  | 231.0206 |  |  |  | 1590.9585 |  | 103.05
|  | 453 | 2861.1653 |  | 231.0462 |  |  |  | 1933.0869 |  | 125.2104
|  | 454 | 2861.4901 |  | 231.0725 |  |  |  | 1419.0922 |  | 91.9178
|  | 455 | 2861.8215 |  | 231.0992 |  |  |  | 905.0909 |  | 58.6248
|  | 456 | 2862.1594 |  | 231.1265 |  |  |  | 391.0831 |  | 25.3313
|  | 457 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 458 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 459 | 2863.6082 |  | 231.2435 |  |  |  | 71.6482 |  | 4.6408
|  | 460 | 2863.9702 |  | 231.2727 |  |  |  | 266.97 |  | 17.2923
|  | 461 | 2864.3386 |  | 231.3025 |  |  |  | 462.2854 |  | 29.9433
|  | 462 | 2864.7133 |  | 231.3328 |  |  |  | 657.5944 |  | 42.5939
|  | 463 | 2865.0944 |  | 231.3635 |  |  |  | 852.8971 |  | 55.2441
|  | 464 | 2865.4817 |  | 231.3948 |  |  |  | 1048.1935 |  | 67.8939
|  | 465 | 2865.8754 |  | 231.4266 |  |  |  | 1243.4836 |  | 80.5433
|  | 466 | 2866.2752 |  | 231.4589 |  |  |  | 1438.7675 |  | 93.1922
|  | 467 | 2866.6813 |  | 231.4917 |  |  |  | 1634.0452 |  | 105.8408
|  | 468 | 2867.0936 |  | 231.525 |  |  |  | 1829.3167 |  | 118.489
|  | 469 | 2867.512 |  | 231.5588 |  |  |  | 1926.7402 |  | 124.7993
|  | 470 | 2867.9365 |  | 231.593 |  |  |  | 1926.3157 |  | 124.7718
|  | 471 | 2868.3671 |  | 231.6278 |  |  |  | 2415.0945 |  | 156.4311
|  | 472 | 2868.8037 |  | 231.6631 |  |  |  | 2610.3416 |  | 169.0777
|  | 473 | 2869.2464 |  | 231.6988 |  |  |  | 2335.9417 |  | 151.3042
|  | 474 | 2869.695 |  | 231.735 |  |  |  | 2061.5358 |  | 133.5303
|  | 475 | 2870.1496 |  | 231.7718 |  |  |  | 1924.1025 |  | 124.6285
|  | 476 | 2870.6102 |  | 231.8089 |  |  |  | 1512.7061 |  | 97.9814
|  | 477 | 2871.0766 |  | 231.8466 |  |  |  | 1238.2824 |  | 80.2064
|  | 478 | 2871.549 |  | 231.8848 |  |  |  | 963.8528 |  | 62.4309
|  | 479 | 2872.0271 |  | 231.9234 |  |  |  | 209.9921 |  | 13.6017
|  | 480 | 2872.5111 |  | 231.9624 |  |  |  | 38.2849 |  | 2.4798
|  | 481 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 482 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 483 | 2874.531 |  | 232.1256 |  |  |  | 36.2649 |  | 2.349
|  | 484 | 2875.0355 |  | 232.1663 |  |  |  | 206.9838 |  | 13.4068
|  | 485 | 2875.5456 |  | 232.2075 |  |  |  | 377.6969 |  | 24.4643
|  | 486 | 2876.0614 |  | 232.2491 |  |  |  | 548.4045 |  | 35.5214
|  | 487 | 2876.5828 |  | 232.2912 |  |  |  | 719.1064 |  | 46.5781
|  | 488 | 2877.1097 |  | 232.3338 |  |  |  | 889.8027 |  | 57.6345
|  | 489 | 2877.6423 |  | 232.3768 |  |  |  | 1060.4934 |  | 68.6906
|  | 490 | 2878.1803 |  | 232.4203 |  |  |  | 1231.1787 |  | 79.7462
|  | 491 | 2878.7239 |  | 232.4641 |  |  |  | 1401.8584 |  | 90.8015
|  | 492 | 2879.2729 |  | 232.5085 |  |  |  | 1572.5327 |  | 101.8565
|  | 493 | 2879.8273 |  | 232.5533 |  |  |  | 1743.2015 |  | 112.9111
|  | 494 | 2880.3872 |  | 232.5985 |  |  |  | 1913.865 |  | 123.9654
|  | 495 | 2880.9525 |  | 232.6441 |  |  |  | 1742.0764 |  | 112.8382
|  | 496 | 2881.5231 |  | 232.6902 |  |  |  | 1912.7291 |  | 123.8918
|  | 497 | 2882.099 |  | 232.7367 |  |  |  | 2597.0463 |  | 168.2166
|  | 498 | 2882.6802 |  | 232.7836 |  |  |  | 2425.2418 |  | 157.0884
|  | 499 | 2883.2667 |  | 232.831 |  |  |  | 2767.1019 |  | 179.2315
|  | 500 | 2883.8585 |  | 232.8788 |  |  |  | 2389.8189 |  | 154.794
|  | 501 | 2884.4554 |  | 232.927 |  |  |  | 2012.5307 |  | 130.3562
|  | 502 | 2885.0576 |  | 232.9756 |  |  |  | 1635.2373 |  | 105.918
|  | 503 | 2885.6649 |  | 233.0246 |  |  |  | 1257.9388 |  | 81.4795
|  | 504 | 2886.2773 |  | 233.0741 |  |  |  | 880.6351 |  | 57.0407
|  | 505 | 2886.8949 |  | 233.124 |  |  |  | 23.9011 |  | 1.5481
|  | 506 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 507 | 2888.432 |  | 233.2481 |  |  |  | 22.3639 |  | 1.4486
|  | 508 | 2889.0634 |  | 233.2991 |  |  |  | 192.9558 |  | 12.4982
|  | 509 | 2889.6998 |  | 233.3505 |  |  |  | 620.3777 |  | 40.1833
|  | 510 | 2890.3411 |  | 233.4023 |  |  |  | 876.5713 |  | 56.7775
|  | 511 | 2890.9874 |  | 233.4545 |  |  |  | 1132.7599 |  | 73.3714
|  | 512 | 2891.6386 |  | 233.507 |  |  |  | 1388.9436 |  | 89.965
|  | 513 | 2892.2948 |  | 233.56 |  |  |  | 1645.1225 |  | 106.5583
|  | 514 | 2892.9557 |  | 233.6134 |  |  |  | 1901.2964 |  | 123.1513
|  | 515 | 2893.6216 |  | 233.6672 |  |  |  | 2157.4656 |  | 139.7439
|  | 516 | 2894.2922 |  | 233.7213 |  |  |  | 2413.6299 |  | 156.3363
|  | 517 | 2894.9676 |  | 233.7759 |  |  |  | 2669.7894 |  | 172.9283
|  | 518 | 2895.6478 |  | 233.8308 |  |  |  | 2925.9441 |  | 189.52
|  | 519 | 2896.3327 |  | 233.8861 |  |  |  | 2754.0359 |  | 178.3851
|  | 520 | 2897.0223 |  | 233.9418 |  |  |  | 2981.644 |  | 193.1278
|  | 521 | 2897.7166 |  | 233.9979 |  |  |  | 3779.9918 |  | 244.8386
|  | 522 | 2898.4156 |  | 234.0543 |  |  |  | 3608.0695 |  | 233.7028
|  | 523 | 2899.1192 |  | 234.1111 |  |  |  | 3949.8125 |  | 255.8383
|  | 524 | 2899.8274 |  | 234.1683 |  |  |  | 3606.6577 |  | 233.6114
|  | 525 | 2900.5402 |  | 234.2259 |  |  |  | 4119.6148 |  | 266.8368
|  | 526 | 2901.2575 |  | 234.2838 |  |  |  | 3262.781 |  | 211.3377
|  | 527 | 2901.9794 |  | 234.3421 |  |  |  | 2405.9427 |  | 155.8384
|  | 528 | 2902.7057 |  | 234.4007 |  |  |  | 1549.0999 |  | 100.3387
|  | 529 | 2903.4366 |  | 234.4598 |  |  |  | 7.3594 |  | 0.47668
|  | 530 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 531 | 2905.2368 |  | 234.6051 |  |  |  | 39.8038 |  | 2.5782
|  | 532 | 2905.9795 |  | 234.6651 |  |  |  | 176.0398 |  | 11.4025
|  | 533 | 2906.7265 |  | 234.7254 |  |  |  | 493.2789 |  | 31.9508
|  | 534 | 2907.4779 |  | 234.7861 |  |  |  | 712.6717 |  | 46.1614
|  | 535 | 2908.2336 |  | 234.8471 |  |  |  | 932.0603 |  | 60.3717
|  | 536 | 2908.9936 |  | 234.9085 |  |  |  | 1151.4445 |  | 74.5817
|  | 537 | 2909.7579 |  | 234.9702 |  |  |  | 1370.8244 |  | 88.7914
|  | 538 | 2910.5265 |  | 235.0323 |  |  |  | 1590.2001 |  | 103.0009
|  | 539 | 2911.2993 |  | 235.0947 |  |  |  | 1809.5715 |  | 117.21
|  | 540 | 2912.0763 |  | 235.1574 |  |  |  | 2028.9387 |  | 131.419
|  | 541 | 2912.8575 |  | 235.2205 |  |  |  | 2248.3017 |  | 145.6276
|  | 542 | 2913.6429 |  | 235.2839 |  |  |  | 2467.6606 |  | 159.836
|  | 543 | 2914.4324 |  | 235.3477 |  |  |  | 2687.0153 |  | 174.0441
|  | 544 | 2915.226 |  | 235.4118 |  |  |  | 2906.3659 |  | 188.2519
|  | 545 | 2916.0237 |  | 235.4762 |  |  |  | 2734.3449 |  | 177.1097
|  | 546 | 2916.8255 |  | 235.5409 |  |  |  | 3075.9897 |  | 199.2388
|  | 547 | 2917.6313 |  | 235.606 |  |  |  | 3417.6305 |  | 221.3677
|  | 548 | 2918.4411 |  | 235.6714 |  |  |  | 3588.044 |  | 232.4057
|  | 549 | 2919.255 |  | 235.7371 |  |  |  | 4100.9 |  | 265.6246
|  | 550 | 2920.0728 |  | 235.8032 |  |  |  | 3243.9657 |  | 210.119
|  | 551 | 2920.8945 |  | 235.8695 |  |  |  | 2387.0275 |  | 154.6132
|  | 552 | 2921.7202 |  | 235.9362 |  |  |  | 1530.0854 |  | 99.1071
|  | 553 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 554 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 555 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 556 | 2925.5021 |  | 236.2416 |  |  |  | 156.5171 |  | 10.138
|  | 557 | 2926.3451 |  | 236.3097 |  |  |  | 524.4628 |  | 33.9706
|  | 558 | 2927.1918 |  | 236.3781 |  |  |  | 760.6945 |  | 49.2719
|  | 559 | 2928.0423 |  | 236.4467 |  |  |  | 996.9223 |  | 64.5729
|  | 560 | 2928.8966 |  | 236.5157 |  |  |  | 1233.1465 |  | 79.8737
|  | 561 | 2929.7546 |  | 236.585 |  |  |  | 1469.3669 |  | 95.1742
|  | 562 | 2930.6163 |  | 236.6546 |  |  |  | 1705.5836 |  | 110.4745
|  | 563 | 2931.4817 |  | 236.7245 |  |  |  | 1941.7966 |  | 125.7746
|  | 564 | 2932.3507 |  | 236.7946 |  |  |  | 2178.006 |  | 141.0744
|  | 565 | 2933.2234 |  | 236.8651 |  |  |  | 2414.2117 |  | 156.374
|  | 566 | 2934.0996 |  | 236.9359 |  |  |  | 2650.4139 |  | 171.6733
|  | 567 | 2934.9795 |  | 237.0069 |  |  |  | 2886.6124 |  | 186.9724
|  | 568 | 2935.863 |  | 237.0783 |  |  |  | 2714.5056 |  | 175.8247
|  | 569 | 2936.75 |  | 237.1499 |  |  |  | 3021.8206 |  | 195.7302
|  | 570 | 2937.6405 |  | 237.2218 |  |  |  | 3329.132 |  | 215.6354
|  | 571 | 2938.5345 |  | 237.294 |  |  |  | 3910.3971 |  | 253.2853
|  | 572 | 2939.432 |  | 237.3665 |  |  |  | 3909.4996 |  | 253.2271
|  | 573 | 2940.333 |  | 237.4392 |  |  |  | 4251.0452 |  | 275.3498
|  | 574 | 2941.2374 |  | 237.5123 |  |  |  | 3359.7797 |  | 217.6205
|  | 575 | 2942.1453 |  | 237.5856 |  |  |  | 2468.5107 |  | 159.891
|  | 576 | 2943.0565 |  | 237.6592 |  |  |  | 1577.2384 |  | 102.1613
|  | 577 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 578 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 579 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 580 | 2947.2783 |  | 238.0001 |  |  |  | 134.741 |  | 8.7275
|  | 581 | 2948.2037 |  | 238.0748 |  |  |  | 476.2622 |  | 30.8486
|  | 582 | 2949.1323 |  | 238.1498 |  |  |  | 703.6312 |  | 45.5758
|  | 583 | 2950.0643 |  | 238.2251 |  |  |  | 930.997 |  | 60.3028
|  | 584 | 2950.9995 |  | 238.3006 |  |  |  | 1158.3595 |  | 75.0296
|  | 585 | 2951.9378 |  | 238.3764 |  |  |  | 1385.7189 |  | 89.7562
|  | 586 | 2952.8794 |  | 238.4524 |  |  |  | 1613.075 |  | 104.4825
|  | 587 | 2953.8242 |  | 238.5287 |  |  |  | 1840.428 |  | 119.2087
|  | 588 | 2954.7721 |  | 238.6052 |  |  |  | 2067.7778 |  | 133.9347
|  | 589 | 2955.7232 |  | 238.682 |  |  |  | 2295.1245 |  | 148.6604
|  | 590 | 2956.6773 |  | 238.7591 |  |  |  | 2522.468 |  | 163.386
|  | 591 | 2957.6346 |  | 238.8364 |  |  |  | 2350.2875 |  | 152.2334
|  | 592 | 2958.5949 |  | 238.9139 |  |  |  | 2748.8482 |  | 178.0491
|  | 593 | 2959.5583 |  | 238.9917 |  |  |  | 3147.4058 |  | 203.8646
|  | 594 | 2960.5247 |  | 239.0698 |  |  |  | 3545.9604 |  | 229.6799
|  | 595 | 2961.4941 |  | 239.148 |  |  |  | 3074.1269 |  | 199.1182
|  | 596 | 2962.4665 |  | 239.2266 |  |  |  | 2602.2904 |  | 168.5562
|  | 597 | 2963.4419 |  | 239.3053 |  |  |  | 2130.451 |  | 137.9941
|  | 598 | 2964.4203 |  | 239.3843 |  |  |  | 1658.6086 |  | 107.4318
|  | 599 | 2965.4015 |  | 239.4636 |  |  |  | 1186.7633 |  | 76.8693
|  | 600 | 2966.3857 |  | 239.5431 |  |  |  | 458.0801 |  | 29.6709
|  | 601 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 602 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 603 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 604 | 2971.0212 |  | 239.9174 |  |  |  | 110.998 |  | 7.1896
|  | 605 | 2972.0166 |  | 239.9978 |  |  |  | 421.3177 |  | 27.2897
|  | 606 | 2973.0148 |  | 240.0784 |  |  |  | 638.2401 |  | 41.3403
|  | 607 | 2974.0158 |  | 240.1592 |  |  |  | 855.1596 |  | 55.3906
|  | 608 | 2975.0195 |  | 240.2403 |  |  |  | 1072.0764 |  | 69.4408
|  | 609 | 2976.026 |  | 240.3215 |  |  |  | 1288.9905 |  | 83.4908
|  | 610 | 2977.0353 |  | 240.403 |  |  |  | 1505.9018 |  | 97.5407
|  | 611 | 2978.0472 |  | 240.4848 |  |  |  | 1722.8104 |  | 111.5903
|  | 612 | 2979.0618 |  | 240.5667 |  |  |  | 1939.7163 |  | 125.6398
|  | 613 | 2980.0792 |  | 240.6488 |  |  |  | 2156.6196 |  | 139.6891
|  | 614 | 2981.0991 |  | 240.7312 |  |  |  | 2057.7577 |  | 133.2856
|  | 615 | 2982.1217 |  | 240.8138 |  |  |  | 1958.8933 |  | 126.882
|  | 616 | 2983.1469 |  | 240.8966 |  |  |  | 1860.0262 |  | 120.4781
|  | 617 | 2984.1748 |  | 240.9796 |  |  |  | 1761.1565 |  | 114.0741
|  | 618 | 2985.2052 |  | 241.0628 |  |  |  | 1662.2842 |  | 107.6699
|  | 619 | 2986.2381 |  | 241.1462 |  |  |  | 1563.4093 |  | 101.2656
|  | 620 | 2987.2736 |  | 241.2298 |  |  |  | 1464.5319 |  | 94.8611
|  | 621 | 2988.3117 |  | 241.3136 |  |  |  | 1805.9405 |  | 116.9749
|  | 622 | 2989.3522 |  | 241.3977 |  |  |  | 1291.2301 |  | 83.6359
|  | 623 | 2990.3953 |  | 241.4819 |  |  |  | 776.5172 |  | 50.2968
|  | 624 | 2991.4408 |  | 241.5663 |  |  |  | 261.8018 |  | 16.9575
|  | 625 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 626 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 627 | 2935.2564 |  | 237.0293 |  |  |  | 0 |  | 0
|  | 628 | 2996.7227 |  | 241.9928 |  |  |  | 134.2175 |  | 8.6936
|  | 629 | 2997.7753 |  | 242.0778 |  |  |  | 328.8486 |  | 21.3003
|  | 630 | 2998.8304 |  | 242.163 |  |  |  | 523.4774 |  | 33.9068
|  | 631 | 2999.8878 |  | 242.2484 |  |  |  | 718.1037 |  | 46.5132
|  | 632 | 3000.9475 |  | 242.334 |  |  |  | 912.7277 |  | 59.1194
|  | 633 | 3002.0096 |  | 242.4198 |  |  |  | 1107.3494 |  | 71.7255
|  | 634 | 3003.074 |  | 242.5057 |  |  |  | 1301.9688 |  | 84.3315
|  | 635 | 3004.1406 |  | 242.5919 |  |  |  | 1496.5859 |  | 96.9373
|  | 636 | 3005.2096 |  | 242.6782 |  |  |  | 1691.2007 |  | 109.5429
|  | 637 | 3006.2808 |  | 242.7647 |  |  |  | 1787.9713 |  | 115.811
|  | 638 | 3007.3543 |  | 242.8514 |  |  |  | 1786.8979 |  | 115.7414
|  | 639 | 3008.43 |  | 242.9382 |  |  |  | 2275.0316 |  | 147.359
|  | 640 | 3009.5079 |  | 243.0253 |  |  |  | 2469.6375 |  | 159.964
|  | 641 | 3010.588 |  | 243.1125 |  |  |  | 2194.6001 |  | 142.1492
|  | 642 | 3011.6702 |  | 243.1999 |  |  |  | 1919.5606 |  | 124.3343
|  | 643 | 3012.7546 |  | 243.2875 |  |  |  | 1781.4975 |  | 115.3916
|  | 644 | 3013.8412 |  | 243.3752 |  |  |  | 1369.4751 |  | 88.704
|  | 645 | 3014.9299 |  | 243.4631 |  |  |  | 1094.4291 |  | 70.8887
|  | 646 | 3016.0207 |  | 243.5512 |  |  |  | 819.3811 |  | 53.0732
|  | 647 | 3017.1136 |  | 243.6395 |  |  |  | 64.9057 |  | 4.2041
|  | 648 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 649 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 650 | 2739.5727 |  | 221.2273 |  |  |  | 0 |  | 0
|  | 651 | 2910.796 |  | 235.054 |  |  |  | 0 |  | 0
|  | 652 | 3024.2608 |  | 244.2166 |  |  |  | 57.7584 |  | 3.7411
|  | 653 | 3025.3583 |  | 244.3052 |  |  |  | 227.8842 |  | 14.7606
|  | 654 | 3026.4578 |  | 244.394 |  |  |  | 398.008 |  | 25.7799
|  | 655 | 3027.5593 |  | 244.483 |  |  |  | 568.1299 |  | 36.7991
|  | 656 | 3028.6627 |  | 244.5721 |  |  |  | 738.2497 |  | 47.8181
|  | 657 | 3029.7681 |  | 244.6613 |  |  |  | 908.3676 |  | 58.837
|  | 658 | 3030.8754 |  | 244.7508 |  |  |  | 1078.4836 |  | 69.8558
|  | 659 | 3031.9847 |  | 244.8403 |  |  |  | 1248.5976 |  | 80.8745
|  | 660 | 3033.0959 |  | 244.9301 |  |  |  | 1418.7097 |  | 91.893
|  | 661 | 3034.2089 |  | 245.02 |  |  |  | 1588.82 |  | 102.9115
|  | 662 | 3035.3238 |  | 245.11 |  |  |  | 1758.9283 |  | 113.9298
|  | 663 | 3036.4406 |  | 245.2002 |  |  |  | 1586.5882 |  | 102.7669
|  | 664 | 3037.5593 |  | 245.2905 |  |  |  | 1756.6929 |  | 113.785
|  | 665 | 3038.6797 |  | 245.381 |  |  |  | 2440.4656 |  | 158.0745
|  | 666 | 3039.802 |  | 245.4716 |  |  |  | 2268.12 |  | 146.9113
|  | 667 | 3040.9261 |  | 245.5624 |  |  |  | 2609.4426 |  | 169.0195
|  | 668 | 3042.0519 |  | 245.6533 |  |  |  | 2231.6255 |  | 144.5474
|  | 669 | 3043.7086 |  | 245.7871 |  |  |  | 1853.2775 |  | 120.041
|  | 670 | 3045.7185 |  | 245.9494 |  |  |  | 1474.5764 |  | 95.5117
|  | 671 | 3047.7284 |  | 246.1117 |  |  |  | 1095.8752 |  | 70.9823
|  | 672 | 3049.7384 |  | 246.274 |  |  |  | 717.174 |  | 46.453
Note on C8: Peter North: (Sat-Toutlet = 2 to 5K) Condenser refrig sat temp (30ºC) minus 2ºC approach temp. Needs to be written-up and justified. Sat temp - outlet temp btw 2 to 5K. 2K taken to max deltaT and min mass flowrate.
Note on C9: Peter North: (Toutlet - sat = 5K) Evaporator refrig sat temp (5ºC) plus 5K or 2K approach temp. Needs to be written-up and justified.